## Q95 Flow (Background) 10% EQS
[10 empty] | RFR+EFR | 1.5602
[10 empty] | 10 X EFR | 0.011574
[5 empty] | Discharge Consent |  |  |  |  | IF EFR+RFR <10X EFR then do additional calculation under Test 3
|  |  |  | Discharge Rate (C ) | 100 | m3/day | 0.0011574 |  |  | Here: EFR+RFR >10X EFR so not necessary to do calc under Test 3
[5 empty] | 0.0011574 | m3/s | Q95
|  |  |  | Receiving Watercourse Flow Rate (D ) | 1.559 | m3/s | Q95 river flow - Bescot upstream of Ray Hall STW
|  |  |  | Dilution Factor | 1347.976
Sewage Reduction Factor (E )
Substance | Discharge | Discharge | River Flow | STW | Discharge | Background | Process | Conc | EQS | Test 1 | Test 2 | Test 3 | Test 4
| Conc | Rate | Rate | Reduction | Conc | Conc | Contribution | after |  | (% of EQS) |  | PEC-BC | AA EQS-PEC
| (site) |  |  |  | (to River) | River(D) |  | mixing |  |  |  | EQS
| RC-Source | EFR | RFR | STRF | RC-Process | BC | PC | PEC | AA | Test Threshold 10% | Test Threshold 4% | Test Threshold 10%
Major Components | mg/l | m3/s | m3/s | Factor | mg/l | mg/l | mg/l | mg/l | mg/l
Ammoniacal-Nitrogen | 24.05 | 0.0011574 | 1.559 | 0.08 | 1.924 | 0.039 | 0.017842 | 0.040398 | 0.39 | 493.3% | 4.575% | 0.3586% | 0.3496
Chloride | 230 | 0.0011574 | 1.559 | 1 | 230 | 25 | 0.17063 | 25.1521 | 250 | 92% | 0.06825% | 0.06083% | 224.8479
Cadmium | 0.00018 | 0.0011574 | 1.559 | 0.89 | 0.0001602 | 8e-06 | 1.3353e-07 | 8.1129e-06 | 8e-05 | 200.2% | 0.1669% | 0.1411% | 7.1887e-05
Chromium | 0.01 | 0.0011574 | 1.559 | 0.16 | 0.0016 | 0.00047 | 7.4185e-06 | 0.00047084 | 0.0047 | 34.04% | 0.1578% | 0.01784% | 0.0042292
Copper | 0.013 | 0.0011574 | 1.559 | 0.58 | 0.00754 | 0.0001 | 9.6441e-06 | 0.00010552 | 0.001 | 754% | 0.9644% | 0.5519% | 0.00089448
Lead | 0.0024 | 0.0011574 | 1.559 | 0.67 | 0.001608 | 0.00012 | 1.7804e-06 | 0.0001211 | 0.0012 | 134% | 0.1484% | 0.09199% | 0.0010789
Nickel | 0.032 | 0.0011574 | 1.559 | 1 | 0.032 | 0.0004 | 2.3739e-05 | 0.00042344 | 0.004 | 800% | 0.5935% | 0.5861% | 0.0035766
Zinc | 0.099 | 0.0011574 | 1.559 | 1 | 0.099 | 0.00108 | 7.3443e-05 | 0.0011526 | 0.0108 | 916.7% | 0.68% | 0.6726% | 0.0096474
Sulphate | 674 | 0.0011574 | 1.559 |  | 674 | 40 | 0.50001 | 40.4703 | 400 | 168.5% | 0.125% | 0.1176% | 359.5297
Mercury | 0.023 | 0.0011574 | 1.559 | 1 | 0.023 | 7e-06 | 1.7063e-05 | 2.4057e-05 | 7e-05 | 32857% | 24.38% | 24.37% | 4.5943e-05
Mecoprop | 0.0004 | 0.0011574 | 1.559 |  | 0.0004 | 0.0018 | 2.9674e-07 | 0.001799 | 0.018 | 2.222% | 0.001649% | -0.00577% | 0.016201
Boron | 0.12 | 0.0011574 | 1.559 |  | 0.12 | 0.2 | 8.9022e-05 | 0.19994 | 2 | 6% | 0.004451% | -0.002967% | 1.8001
Iron | 0.461 | 0.0011574 | 1.559 |  | 0.461 | 0.1 | 0.00034199 | 0.10027 | 1 | 46.1% | 0.0342% | 0.02678% | 0.89973
Arsenic | 0.0093 | 0.0011574 | 1.559 |  | 0.0093 | 0.005 | 6.8992e-06 | 0.0050032 | 0.05 | 18.6% | 0.0138% | 0.00638% | 0.044997
Note on B14: Kathryn Wright: Max values

## Q95 Flow (Background) 50% EQS
[9 empty] | RFR+EFR | 1.5602
[9 empty] | 10 X EFR | 0.011574
[5 empty] | Discharge Consent |  |  |  | IF EFR+RFR <10X EFR then do additional calculation under Test 3
|  |  |  | Discharge Rate (C ) | 100 | m3/day |  |  | Here: EFR+RFR >10X EFR so not necessary to do calc under Test 3
[5 empty] | 0.0011574 | m3/s | Q95
|  |  |  | Receiving Watercourse Flow Rate (D ) | 1.559 | m3/s | Q95 river flow - Bescot upstream of Ray Hall STW
|  |  |  | Dilution Factor | 1347.976
Sewage Reduction Factor (E )
Substance | Discharge | Discharge | River Flow | STW | Discharge | Background | Process | Conc | EQS | Test 1 | Test 2 | Test 3 | Test 4
| Conc | Rate | Rate | Reduction | Conc | Conc | Contribution | after |  | (% of EQS) |  | PEC-BC | EQS-PEC
| (site) |  |  |  | (to River) | River (D) |  | mixing |  |  |  | AA EQS
| RC-Source | EFR | RFR | STRF | RC-Process | BC | PC | PEC | AA | Test Threshold 10% | Test Threshold 4% | Test Threshold 10%
Major Components | mg/l | m3/s | m3/s | Factor | mg/l | mg/l | mg/l | mg/l | mg/l
Ammoniacal-Nitrogen | 24.05 | 0.0011574 | 1.559 | 0.08 | 1.924 | 0.195 | 0.017842 | 0.19628 | 0.39 | 493.3% | 4.575% | 0.3289% | 0.19372
Chloride | 230 | 0.0011574 | 1.559 | 1 | 230 | 125 | 0.17063 | 125.0779 | 250 | 92% | 0.06825% | 0.03116% | 124.9221
Cadmium | 0.00018 | 0.0011574 | 1.559 | 0.89 | 0.0001602 | 4e-05 | 1.3353e-07 | 4.0089e-05 | 8e-05 | 200.2% | 0.1669% | 0.1115% | 3.9911e-05
Chromium | 0.01 | 0.0011574 | 1.559 | 0.16 | 0.0016 | 0.00235 | 7.4185e-06 | 0.0023494 | 0.0047 | 34.04% | 0.1578% | -0.01184% | 0.0023506
Copper | 0.013 | 0.0011574 | 1.559 | 0.58 | 0.00754 | 0.0005 | 9.6441e-06 | 0.00050522 | 0.001 | 754% | 0.9644% | 0.5223% | 0.00049478
Lead | 0.0024 | 0.0011574 | 1.559 | 0.67 | 0.001608 | 0.0006 | 1.7804e-06 | 0.00060075 | 0.0012 | 134% | 0.1484% | 0.06232% | 0.00059925
Nickel | 0.032 | 0.0011574 | 1.559 | 1 | 0.032 | 0.002 | 2.3739e-05 | 0.0020223 | 0.004 | 800% | 0.5935% | 0.5564% | 0.0019777
Zinc | 0.099 | 0.0011574 | 1.559 | 1 | 0.099 | 0.0054 | 7.3443e-05 | 0.0054694 | 0.0108 | 916.7% | 0.68% | 0.6429% | 0.0053306
Sulphate | 674 | 0.0011574 | 1.559 |  | 674 | 200 | 0.50001 | 200.3516 | 400 | 168.5% | 0.125% | 0.08791% | 199.6484
Mercury | 0.023 | 0.0011574 | 1.559 | 1 | 0.023 | 3.5e-05 | 1.7063e-05 | 5.2037e-05 | 7e-05 | 32857% | 24.38% | 24.34% | 1.7963e-05
Mecoprop | 0.0004 | 0.0011574 | 1.559 |  | 0.0004 | 0.009 | 2.9674e-07 | 0.0089936 | 0.018 | 2.222% | 0.001649% | -0.03544% | 0.0090064
Boron | 0.12 | 0.0011574 | 1.559 |  | 0.12 | 1 | 8.9022e-05 | 0.99935 | 2 | 6% | 0.004451% | -0.03264% | 1.0007
Iron | 0.461 | 0.0011574 | 1.559 |  | 0.461 | 0.5 | 0.00034199 | 0.49997 | 1 | 46.1% | 0.0342% | -0.002893% | 0.50003
Arsenic | 0.0093 | 0.0011574 | 1.559 |  | 0.0093 | 0.025 | 6.8992e-06 | 0.024988 | 0.05 | 18.6% | 0.0138% | -0.02329% | 0.025012
Note on B14: Kathryn Wright: Max values