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1 Introduction 
1.1 Roles and Responsibilities

The Site Manager (Andrew Newman) has responsibility for ensuring these procedures are adhered to.  The Site Manager is specifically responsible for:

· Ensuring the adequate training of staff and contractors working on site regarding the content of these procedures;

· Ensuring the adequate provision of resources such as personal protective equipment (PPE);
· Ensuring the provision and maintenance of hand held fire extinguishers and other fire fighting equipment at the site is adequate.

1.2 Purpose
The primary purpose of this Fire Prevention Plan (FPP) is to guide staff and contractors in the prevention of fire for National Tyre Recovery Limited.  This FPP also confirms the actions to be taken in the event of fire in order to minimise any impact on the environment and to control the fire where appropriate.  
This FPP will be issued to the Fire Brigade in the event of a fire to aid with fire fighting.
1.3 Scope 

This FPP has been prepared in accordance with Environment Agency guidance.
   
In addition, all fire prevention measures will meet the stringent insurance requirements for the business.
Annex A shows a site layout plan.
1.4 Liaison with Fire Rescue Service (FRS)

The FRS will be provided a copy of this FPP in advance of commencing operations.
1.5 General considerations

National Tyre Recovery Limited is located on Bottom Yard, Stipers Hill Rd, Kisses Barn Lane, Warton, B79 0JS between the M42 & A444 east of Tamworth. The site is approximately 0.22 Hectares in size.  At the time of writing this FPP, the site is currently consists of concrete impermeable surface in good order over the entire external site where waste is to be stored.  The site’s main activity is the storage, recycling, baling of waste tyres. The surrounding land use is a mix of light industrial and agricultural.
National Tyre Recovery Limited operate under an existing Environmental Management System [EMS] which identifies the potential sources of pollution from site activities and controls site operations to eradicate emissions or where that is not possible to minimise their effect on human and environmental health.

This Fire Prevention Plan [FPP] forms part of the EMS.

The individual fire emergency procedures for each part of the site form part of the FPP.
The site has sealed drainage for the storage of baled tyres consisting of an isolated baled area in the yard. See Annex B Site Drainage.
2 Causes of Fire
The following have been identified as potential causes of fire and their relevance to this site, when operational, is given in Table 1 
	Table 1 Causes of Fire and Applicability to the National Tyre Recovery Site

	Cause of Fire
	Applicability to the National Tyre Recovery Site

	· Arson or vandalism
	Yes – see section 3.5 Security

	· Self-combustion
	No – see 3.7 Self Combustion

	· Naked lights
	No – none on site 

	· Plant or equipment failure
	Yes – see  3.6 Planned Preventative Maintenance

	· Electrical faults
	No – none on site - occasional

	· Discarded smoking materials
	No – on site smoking is prohibited

	· Hot works
	No – see 3.8 Hot works

	· Hot exhausts
	Yes – see 3.10 Hot exhausts

	· Industrial heater
	No – none on site

	· Open burning (adjacent to site)
	No – no likely sources of burning adjacent to site 

	· Damaged or exposed electrical cables
	No – no live cables on the site or to be introduced

	· Reactions between incompatible materials
	Not relevant given the waste types

	· Neighbouring site activities
	No – no likely sources of risk from neighbouring land use

	· Sparks from loading buckets
	No – loading buckets will not be required (a FLT is used).

	· Hot loads deposited at the site
	No – not a risk given the types of materials and sources of materials.  


Mitigation measures in relation to these activities, where under control of National Tyre Recovery Limited, are set out in this FPP.

3 Fire Prevention Plan
National Tyre Recovery recognises that the risk of fire cannot be eliminated.  However, the site will be operated in accordance with a robust management system.  Operational Procedures are listed in the site’s EMS Manual Section 1.6 ‘Operational Control’. 
In addition to Operational Procedures, the following reasonable actions will be taken to minimise the risk of fire, in accordance with Environment Agency guidelines. 

3.1 Site Plan and Receptors
A Site Plan is given in Annex A showing the key features of the site relevant to the Fire Prevention Plan including site access, security, vehicle parking, materials storage, drainage and buildings. Annex C is a Fire Fighting Equipment plan including the location of hose reels and hydrants.

A map showing key receptors within 1 km of the site is in Annex D.

3.2 Material Receipt and Storage
Waste will be collected using the company’s vehicles which will be removed from the customer’s site and returned to National Tyre Recovery Limited. 

Waste acceptance procedures will be followed as set out in Annex E.  
Only the waste types and EWC codes named on the environmental permit will be accepted at the site namely 16-01-03. Wastes entering the site will be inspected and registered at the site. Non-compliant waste materials not allowed on the permit will be turned away from the site. A record will be made in the site diary.
3.2.1 Quarantine Area
The site plan shows the Fire Quarantine Area.  The Fire Quarantine Area will always be kept clear in case of emergency.  The area is located close to a water supply for quenching burning or smouldering material. 
The Fire Quarantine Area is a dedicated emergency or quarantine area with a clear area of 6m around it.   The rationale for this area is:
· The area is in the middle of the site, so is required to be kept clear, at all times, for access.

· Only small quantities of material would ever be put in this site i.e. those that can be dealt with safely by the staff on the site.  Larger fire would be dealt with by the FRS. 
· The quarantine area is 7.5m x7.5m x3m and can easily accommodate at least 50% of the largest waste pile (200 CUMEC) . See appendix A.
· In the event of a fire or observed self-combustion, burning waste, if safe to do so, will be moved to the Fire Quarantine Area.  

· The Fire Quarantine Area is signposted.
· Hot loads can be quarantines in this area until such times that they can be stored safely.  

· The quarantine area, when made safe, will be emptied immediately. Should it be necessary to moves wastes to an alternative site then a local permitted site will be used.
3.2.2 Waste storage times

All Wastes (including bales) will be stored  in their largest form and for a maximum of 3 months.  Consideration is given to the likely dry nature of the material and the implications this has for self-combustion.  See 3.2.3 (stock rotation and management).
National Tyre Recovery has key customers for each material. In addition, contingency customers are in place in case of a need to move material off site when the regular customer is not able to receive it.  In this way, the stock will not build up to levels over the permitted limits.

3.2.3 Stock rotation and management

The company will undertake monthly stock checks which will involve moving the waste within each pile.  The purpose of the stock check is:

· To turn wastes in order to ensure the waste is not at risk of self-combustion and any potential hotspots are dissipated;

· To ensure the waste volumes do not exceed those specified in the permit. 
· To ensure waste is not kept on site for longer than allowed by the permit
Records will be maintained in the site office of the physical monthly stock checks.
The site manager in charge of stock checking will be vigilant for signs of combustion or hotspots.  If any are found, these will immediately be quenched with water and reported to the management team. Stock rotation will be by mechanical means as necessary.
Waste will follow the first in/first out principle as detailed in Annex F points 10/11/12.
3.2.4 Waste storage 

waste tyres will be stored in the building and processed as soon as they arrive on site, the rest of the yard is also an impermeable surface. Combustible baled waste tyres will be stored in a kerbed storage area (these are all indicated on the site plan)
· 1x baled tyre piles of 10mx10mx2m =200 CUMEC. 6m clearance all round.
· Tyres in a secure sealed container = 8mx4mx3m = 96 CUMEC

No other waste materials are stored on site.
At least 10% of bales will be tested with a temperature probe during monitoring to ensure that temperatures do not exceed critical. Temperatures will be taken from the centre of bales and from bales within the centre of the pile. Bales will be turned regularly to make sure the waste stays cold.

· Total volumes: No more than 1000t at any one time
All bales are individually accessible and moveable
The metal sealed container (freight) is used to store part worn (non waste) tyres. It is accessible from at least one side and moveable by the companies own vehicles if necessary.

3.3 Signage

Signage will be positioned throughout the facility showing Fire Exits and the position of extinguishers and other relevant fire fighting equipment. 

All waste storage areas will be clearly marked to ensure waste throughput timescales are adhered to.

National Tyre Recovery will reinforce fire prevention messages using signs with key messages for staff.
3.4 Training, Awareness and Visitors

All staff and contractors working on-site will be aware and understand the contents of this FPP and the site Fire Response Plan.  Through site inductions and on-going staff awareness and training, National Tyre Recovery will ensure that all relevant staff and contractors will:
· Understand what they must do during a fire.

· Know where the fire prevention plan is kept

· Participate in regular exercises to test how well this FPP plan works and to confirm staff understand what to do.

For visitors to the site:

· They will be escorted at all times and signed in.
· They will understand the No Smoking policy for the site.
· When signing in, information on the fire exits and muster point will be provided. 
Training records are maintained as required by the site EMS.
Staff will be required to undergo regular fire training as part of the WAMITAB competency requirements. In addition, regular drills (annually) will be undertaken where desktop scenarios are played out and staff will be required to become familiar with this FPP as part of their ongoing competence. Mr Andrew Newman will be responsible for implementing this plan and detailing annual tests and drills.

3.5 Security

The following security features will reduce fire risks from vandalism and deliberate arson through preventing access to the site by unauthorised people:

· Gates are closed and locked outside of office hours to block access further.

· Regular checks of the Perimeter fencing and gates the premises is secured by fencing. Security fencing is in place to prevent access to the site and provide total site enclosure.
· Only one entrance/ exit point to the site to/ from the public highway is in place, which is secured by means of lockable metal gates to be locked shut at any time the site is left unattended.
· CCTV/heat detection which can be viewed remotely by the management team covering the whole of the permitted area including waste piles and buildings
· A CCTV system with 24 motion detection is employed for nigh time security. This sends alerts by mobile phone to all staff of National Tyre Recovery and would notify the owner if a fire were to break out during out of hours.
· The CCTV system will also detect hot spots by thermal imaging and send alerts above the preset threshold limit to the site owner.

3.6 Planned Preventative Maintenance

The site has a Planned Preventative Maintenance Programme to ensure all machinery and components continue to remain effective.

There is a programme of routine planned maintenance is for each item of plant and machinery to manufacturers specifications, as well as the processing equipment in order to prevent breakdown and faults which may pose a fire risk.
Limited Electrical equipment including CCTV, electronics, lights, baler will be used at the site. A PAT certificate will be provided to demonstrate that this equipment has been checked by a qualified electrician. A PPM schedule and maintenance contract will be in place to ensure that electrical equipment is fit for purpose and to minimise the risk of ignition sources.
All faults needing corrective action will be reported to the Site Manager to be implemented.

For contingency, National Tyre Recovery recognises that if needed to ensure a continued material throughput, machinery will be hired from specialists if a significant plant breakdown occurs.  This is to ensure continued effective operations and prevent excessive storage of materials which are likely to give rise to the exceeding of permitted waste quantities.
3.7 Self Combustion

Given the stock rotation throughput times and material type, there is a limited potential for self-combustion. EA Guidance states that the risk increases when wastes are stored over 3 months and that combustible materials must not be stored for more than 6 months.  
Daily checks are made on the site as part of the Fire Risk Daily Checks Form (Annex F) and this includes checking for signs of self-combustion and housekeeping issues which may impact on fire risk.  
The risk of combustion is medium, as the materials which will be managed on site are not anticipated to be contaminated with oil, however they will be dry.  As a result, a regime of turning the waste materials monthly during a stock take will be in place.  For details see 3.2.3 Stock Rotation and Management. 
Heat will be released from waste before storing in piles.
The company has considered the risk of self-combustion and consider that given the storage times, management procedures in place and materials stored, the waste is unlikely to generate hot spots.  However, during operation, if the site records show that hotspots do occur on site regularly, the Site Management will consider further measures such as temperature probes.
In warmer weather waste tyres will be sheeted or dampened as required to minimise the effects of external heating. The site benefits from shady areas and natural cover which will be used where possible to keep external waste tyres cool. Regular (daily) checks on external waste piles will be made and the results recorded in the site diary.
3.8 Hot Works
Hot works will not be conducted on site. 
No other combustible gases, chemicals, aerosols or fuels are kept on site
3.9 Mechanical Treatment
Mechanical treatment means the use of mobile plant.  The plant used on site will be as follows:

· 1 x diesel FLT

· 2 x tyre baler – 1xSino baler and 1 xCK108 TB both producing PAS 108 bales.
· 1 x shovel loader

· Vehicles/plant are used daily and an ongoing check is made as to exhaust and hot areas as potential combustion sources.
· All equipment inspected & maintained under PUWER
 requirements

· Mobile plant parked remotely, secured and key out when site closed (See Fire Risk Daily Checks Form Annex F)
· Trained staff operate equipment
· Mobile plant is stored at least 6m away from combustible waste when not in use.
· Fire extinguishers fitted, equipment switched off when not in use, parked in remote area of site when not in use, keys safely stored
3.10 Hot Exhausts

During operations, banksmen and site operatives will be vigilant for signs of ignition from operational hot exhausts. 
At the end of the working day, vehicles will be parked away from combustible materials as indicated on the site plan.  A Daily Site fire watch & Check at the end of the shift will be undertaken by the site manager or his nominee to check that there is no risk of ignition from exhausts.  See Fire Risk Daily Checks Form Annex F. 
3.11 Additional Actions
Further actions to mitigate fire risk on site include:

· Overnight parking of vehicles away from processing and storage areas.
· The access route into the waste site is always kept clear and will therefore provide access for emergency vehicles.
· Site walkovers taken each day will identify any accumulations of combustible dust, litter or material which may pose a fire risk in the areas used by vehicles.
· Litter/detritus will be restricted by the site perimeter curb/bunds and buildings to some extent. Visible litter will be picked daily at the end of the shift. Litter off site will be checked and removed at shift start and finish.
· Good housekeeping will be maintained at all times to ensure dust and wastes are prevented from accumulating on site.
· Operational vehicles will be fitted with fire extinguishers 
· Any fuel/oil spills from plant or vehicles will be cleaned up immediately with absorbent material and disposed of correctly
· Sources of ignition including non-energy efficient (heat emitting) light bulbs, lit cigarettes, naked flames and storage heaters will not be allowed on site.
· All other sources of ignition will be kept at least 6m from flammable & combustible waste

· Cleaning – The site will be cleaned daily at the end of the operational shift in order to prevent build up of dust, fluff and combustible waste. This will be focused on areas where dust may build up e.g. computer screens flat surfaces, disc cutter and mobile plant etc. Surfaces will be dusted, wiped and/or jet washed if appropriate.

· Mud on roads external to the site is not tolerated. Regular inspections of vehicles and the main roads are made to ensure that no annoyance to other road users and neighbours is apparent
· Activity location benefits from good sound attenuation provided by the remote location & industrial setting. All plant benefits from noise and dust suppression.
Ensure operations are only conducted within working hours and where practical noise is minimised by using the minimal movements of vehicles and materials onto and from site
4 Fire Detection and Management
4.1 Fire Detection

National Tyre Recovery will 

· provide portable extinguishers

· carry out regular inspections, including at the start and end of every working day
All staff are aware of this FPP and the risk of fire on site and are trained to remain vigilant. 

Security staff are trained in actions in case of fire detection and will be alerted by the site owner in the event of a fire. The site owner will be responsible for alerting the FRS.
Thermal cameras are installed in the yard and smoke detectors in the buildings. See appendices.

Thermal cameras will detect hot spots above 50 degrees C and send alerts to the owner out of hours. The cameras monitor the site 24/7 and are never turned off except for maintenance.

Incidents of heat in piles reaching 50degrees or over will initiate further investigation which may include turning, isolation, damping or other actions to reduce temperature levels.
Fire Suppression

The Site Fire Fighting Equipment Plan (Annex C) shows the following items for fire suppression:

· A Fire hydrant located to Kisses Barn Lane entrance to the site. With an estimated 2100l/minute (35 l/s) flow rate. 
· Fire extinguishers are provided at strategic points as well as within the office.  The site will be inspected daily by the Site Manager.  The site also hold fire blankets and extinguishers. Staff are trained in the use of these.
Within the office, hand held fire extinguishers are also provided.  
National Tyre Recovery considers that automatic fire suppression systems are unnecessary and uneconomic given that the waste will be stored & treated outside. 
Water Supplies

Table 2 shows the available water on site which can be delivered from hydrants. 
See Annex C & A2 for water supply site plan.
	Table 2: Volume of Water Available

	Hydrant Delivery (l/min)
	2,100

	Number of Hydrants
	1

	Total Hydrant Delivery (l/m)
	2,100


Water supplies for fire fighting can come from the fire hydrant close to the site (Annex A2) in addition to one or more FRS water supply truck if the FRS deems it necessary.

The largest stockpile likely to require water for fire fighting is considered to be the baled tyres in the yard - maximum of 200m3. 
4.2 Fire Fighting Strategy
In the event of a fire being suspected or detected, the following steps will be taken:
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The Site Manager, will liaise with the Emergency Services on their arrival.  The Site Manager will clearly identify him/herself to the Emergency Services on their arrival on site and update the FRS on the situation ensuring they are made aware of the location any compressed gases or flammable liquids on site.
Prior to arrival of the FRS on-site there are several measures that National Tyre Recovery can take to help fight fire, assuming there is no risk to life.
· Water bowsers can be deployed to help damp down and spray smaller areas of fire

· Hand held fire extinguishers can be deployed in order to contain fires where possible

· Access to the hydrant located in the road may be used by National Tyre Recovery staff if required
· Fire blankets/sheets can be used to smother smaller isolated sources of fire.

· The quarantine area is 7.5mx7.5mx3M (168 cubic metres) and can easily accommodate at least 50% of the largest waste pile (200 cubic metres). See appendix A.

· In the event of a fire or observed self-combustion, burning waste, if safe to do so, will be moved to the Fire Quarantine Area or alternative designated site. 

· The Fire Quarantine Area is signposted. 
· There is a hose from a domestic water supply as indicated. It will not be used to fight any major fires but will be used for any minor incidents or refilling bowsers as required. Domestic tap flow rate.
· There are two IBC’s (used as bowsers) of 1000l capacity each. These are always full and on standby around the edge of the yard. These can be hoisted onto FLT’s and used to fight smaller fires if required. National Tyre Recovery do not see these being used for major fires and National Tyre Recovery would defer to the FRS for safety reasons rather than fighting larger fires themselves. 
· An “alternative site” means another potential site that may be used to divert incoming tyres to if required in the event of a fire. There is only one quarantine area at National Tyre Recovery as indicated.
· The quarantine area, when made safe, will be emptied immediately. Should it be necessary to move or divert wastes to an alternative site then an alternative (permitted) location will be used. National Tyre Recovery has an agreement with this site. Vehicles will be directed to this site. (Note the only vehicles directed by National Tyre Recovery will enter the site not the general public so all drivers will be notified to divert to this location).
· Neighbours and local businesses downwind will be notified of any potential fire incident by the site operator as soon as possible from the local contact list. This will be completed by telephone and will be completed as soon as it is safe to do so. Local receptors will be notified in order of proximity to the site and prevailing wind direction. Local receptors will be kept updated as to the progress of firefighting as new information comes to light and fully debriefed at the end of the event.
· Once the fire has been dealt with, post fire de-contamination arrangements will be agreed with the local EA officer

· The waste storage area is an impermeable surface and will be scraped clean

· Drains and runs will be gulped out and cleaned by tankers if required
· Waste will be removed from site if necessary

· If necessary, soil and groundwater monitoring will be undertaken as agreed with the EA

· Once the local EA officer has agreed that the site is ready to become operational again then operations will recommence.
4.3 Managing Fire Water
Table 3 shows the potential volume of fire water which may need to be managed on site should the largest waste pile require quenching. 

	Table 3:  Volume of Water Required

	l/min/1m3 of waste *
	                  6.6 

	Largest Combustible Pile (m3)
	                 200 

	Water Required (l/min)
	1320             

	Total Requirement for 3 hours (l)
	       237,600

	*Based on EA guidance: 2000l of water minute is required for a 300m3 stockpile for three hours


Table 4 shows the volume of fire water which can be contained within the site. The site benefits from a 20cm curb/bund.  A boom will be deployed across the site entrance to retain water to a height of 20cm as per Annex C if required. 
	Table 4:  Volume of Firewater Contained within Site 

	Average Site Length (m)
	69

	Average Site Width (m)
	36

	Water Depth (m)* 
	0.20

	Site Volume (m3)
	496

	Site Volume (l)
	496,000       

	*minimum height of curb or boom


These tables show that the site (within the kerbed area) would be able to contain the volume of water needed in a worst-case scenario.  Therefore, the key receptors in Annex D which could be affected by firewater will be protected. The site benefits from a kerb of 20 cm. The kerb will be installed prior to operations commencing around the site. As can be seen from the surface water flow, the levels slope towards the middle of the site.. 
Booms are stored in the office and are accessible at all times. They are only required on the entrance to the site and total some 5m length in total. Staff are trained in deployment of the booms and are aware of the importance of isolating the site in the event of firewater being used on-site. If the booms fail it is likely that all water will be retained by the kerb in the baled tyre store. 
National Tyre Recovery has a contact for emergency spillage response with a company which provides tankers to remove firewater.  The company would come to site to remove water from the yard using the specified suction point in the drainage system and remove water from the site contained by the bund walls.  See Emergency Contacts, Annex G.
4.4 Future Actions

This plan is based on current planned operations.  National Tyre Recovery understand that it is important that this Fire Prevention Plan is maintained up to date and relevant to the business.  Therefore, it will be updated accordingly, in collaboration with the Environment Agency as required, should business operations change in the future.
5 Annex A: Site Layout

NOTE: Waste storage areas are covered with thicker impermeable concrete. Whole yard is concreted.
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6 Annex B: Site Drainage
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7 Annex C: Fire Fighting Access, Equipment and Water Supply Plan
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8 Annex D: Key Receptors
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	The receptors shown are within 1km of the site (black circle).  Sensitive human receptors include areas containing residential properties to the south west.  

The site is in on a small industrial estate which is  surrounded by farmland.  There are no designated SSSIs within 1 km or rivers closer than .75Km (river Anker).
Key infrastructure includes the railway running NW to SE some .75Km and Kisses Barn Lane to the N. The nearest Fire Response Service operation is Tamworth Rd, Polesworth, Tamworth B78 1HP, Some 0.85Km west of the site.
Wind Direction

According to the UK Met Office, the prevailing wind direction in the area is South/South-Westerly
. This means the prevailing winds blow over the site to the north east, which is away from the residential areas.


9 Annex E: Waste Acceptance Procedures
In order to identify non-compliant wastes including any hot loads, the following Waste Acceptance Procedure is implemented by National Tyre Recovery.

Waste Acceptance

The procedure that shall be adopted at site is detailed below

 1. Waste arrives on site.

2. Documentation is checked at the office the entrance. 

3. All vehicles will have their contents examined during unloading and this shall be crosschecked with the documentation presented. 

4. Staff will check that the type of waste is acceptable in terms of the waste licence. 

5. If the waste is unacceptable the waste shall be isolated and arrangements put in place for the contractor to remove the waste from site or for the waste to be segregated in the quarantine area until such times that it can be removed.
6. If the person who is checking in the load is suspicious of its contents the driver shall be directed to the waste inspection area near the reception office, where the load shall be sampled and inspected to ensure that it corresponds to the accompanying documentation. In any event compliance testing will be carried out at regular intervals.

 7. Assuming the on-site verification is satisfactory, the load is checked in and directed to the yard as appropriate. Here, the waste will be checked again to verify that the description is correct before tipping is allowed.

10 Annex F: Fire Risk Checks Form for Fire Prevention

The following regular check has been completed:

	Checks to be made

	1. Security – all security fencing and security equipment is intact (daily)

	2. Signs of Self Combustion – no smoke visible /potential hot spots identified (daily)

	3. Storage areas – housekeeping is suitable (daily)

	4. Storage areas – Bale sizes within permitted limits (daily)

	5. Exhausts – exhausts are cool and located away from combustible materials(daily)

	6. Fire fighting water – all hose reels and hydrants are accessible(daily)

	7. Fire extinguishers – all fire extinguishers are in the correct place and intact(daily)

	8. Fire Quarantine area – clear from waste and signage intact(daily)

	9. Mobile plant parked remotely, secured and key out when site closed(daily)

	10. Waste turned when? – recorded on waste inventory in site office(monthly)

	11. Waste in (t) – recorded on waste inventory weekly in site office. Waste removed in date order

	12. Waste out (t) – recorded on waste inventory weekly in site office. Waste removed in date order.


	Date
	Morning check (initials)
	Evening Check (Initials)
	Issues to Report to Site Manager

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	


11 Annex G: Emergency Contacts
	Name & Address
	Telephone Number

	Environment Agency 
	General Enquiries:
Incident Hotline Reporting:
	03708 506 506

0800 80 70 60

	Electricity Supplier & mains switch location
	
	

	Gas supplier & shut off valve location
	No gas on site
	No gas on site

	Water supplier & shut off valve location
	Severn Trent
	Warehouse

	Local Authority Emergency Services
	Tamworth
	

	Insurance Company and policy number
	
	TBC

	Nearest Hospital
	
	

	Emergency Spillage Response company
	
	


Details to be updated as required or on change of utilities supply.
12 Annex H: EMS Documents
           Drainage & Bund Checks
· A current site drainage plan will be drawn up and displayed in the office areas for information. The standard colour coding of blue for surface water drainage that discharge to the environment and red for sealed or foul drainage systems will be employed.

· The level of oil water mix in the water sump will be checked by a visual and dipping method by management.

· The kerbed areas will be maintained and emptied when necessary to ensure that it operates effectively at all times. As a minimum, oil will be removed, the sealed drainage de-sludged and the structural integrity of the sealed drainage and chamber will be carried out annually. The daily checks, annual inspection and any maintenance and waste removal will be recorded in the site diary.

· Sealed gullies, will be inspected daily and after any periods of heavy rain by the operator. Where sludge/oil levels within theare high, liquids will be gulped out transferred to an authorized waste collection agency. 
· The  & waste bunds/sumps will be emptied before it becomes full to maximum capacity. 
· The integrity of impermeable surfaces, the sumps and storage areas will be visually inspected by the operator on a monthly basis. To achieve this, it will be necessary to sweep/ wash clean the impermeable surface that form licensed area and clear any earth that has collected in the drain gulley to the front of the building. Where any defects are found, remedial steps will be taken promptly to maintain the integrity of the structure. If, however the integrity of the structure is breached a temporary repair will be made by the end of the working day and a full repair will be made within 10 days.           

	Area
	When Checked 
	Date
	Comments

	Yard
	weekly
	20/10/25
	Clean no gulping required

	Bunds/kerbed area
	weekly
	
	

	Hardstanding
	6 monthly
	
	

	Gulleys
	weekly
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	


Site Vehicle and Machinery Maintenance.

· All site vehicles and machinery will be fitted with working exhaust silencing equipment.

· Staff will not continue to operate any piece of machinery or equipment that appears to be visibly or audibly failing.

· All vehicles and machinery operated within the site will undergo regular planned preventive maintenance/ servicing and inspections, at the frequency deemed appropriate by manufacturer or required by legislation. As a minimum, this will be a statutory annual inspection of lifting (LOLER) and work (PUWER) equipment. Maintenance/ Servicing and inspection records will be kept on site for reference.

· Where the necessary maintenance and repair skill do not exists within the company, a contract for these services will be in place, so that the repair of site vehicles and machinery will be undertaken promptly.

· If mobile plant maintenance/ repair involves the removal/ loss of potentially polluting fluids from the vehicle, if possible, the vehicle should be moved to impermeable concrete area and worked on there, where any spills will land on an impermeable surface. All fluid leaks or drained oils will be collected in a container and removed.

· Where mobile plant must be repaired in the location that it breaks down, if this is on hard standing, drip trays and absorbent mats will be put in place under the vehicle before work begins, to capture any spills of potentially polluting substances and prevent contamination to the earth below.
Plant and Vehicles will be inspected and recorded below;

	Equipment
	When checked
	Date
	Comments
	signed

	Delivery vehicles
	weekly
	
	
	

	FLT’s
	Manufacturer’s Specification
	
	
	


Dealing with Spills

Scope: To detail how spills during normal and abnormal operations are dealt with to minimize impact on the environment

Responsibility: Site owner

Background: Spillage of oils and chemicals can have an impact on the soil and groundwater beneath the site.

The site carries quantities of absorbent granules and absorbent booms to mop up small quantities of hydrocarbon and other liquids if spilt. If used these are stored in the hazardous waste container until removed from the site by specialist contractor within a reasonable period of time.

· During normal operations, all staff have been made aware of the requirement to minimise fuel and liquid spills on site

· All staff have had appropriate training on how to deal with a fuel spill in the event of an incident occurring

· Absorbent is used to clean up the spill at source. If it is a larger spill and it is safe to do so then the source of the spill is curtailed if possible.

· The location of spill kits and absorbent material is identified on the site plan

· Where possible all spills are directed to the sealed drainage system for containment

· A store of general absorbent material will be kept on site in an easy accessible central location known to all site staff. The absorbent material will be hydrocarbon (fuel, oil etc.) absorbent, as this is the most likely material to be spilt on site.

· A boom will be kept on site. Management will know where the boom is stored on site and how it should be deployed so as to be effective. Booms length will be enough to cover the expanse of the entrance to the and to protect the gulley to the Sump water system.

· Where leakage from any storage container on site is found, actions to remedy the leak will be taken. Any such leakage and remedial action will be recorded in the site diary.

          In addition:

· The source of the leak or spill will be investigated, located and stopped.

· If any significant leaks or spills of substances occur, which have the potential to harm the environment or pose a risk to human health; the materials detailed under the section 'site provisions' will be utilized and disposed of appropriately.

· Any pooling leak or spill of a potentially polluting liquid will be soaked up with appropriate absorbent material, such as saw dust, sand or granules. The absorbent material will be cleared from the ground when it has soaked up all free polluting liquid. Where there is the potential to reuse absorbent material because it is not fully saturated, it will be stored in containers labeled 'absorbents for reuse' when fully saturated, absorbents will be placed in containers labeled 'absorbents for disposal'.

· In the event of a significant and/ or on-going leak or spill of a potentially polluting liquid, clay damit mats or suction covers will be applied to drain grills to seal them to prevent (further) liquid from entering the drainage system. 
· In the case of a leak or spill of potentially polluting liquid onto hard standing/ earth surfaces, the hard standing/ earth material will be removed and replaced with clean material of a similar nature.

· Covered leak proof containers will be available on site for the segregated storage of contaminated absorbent materials and contaminated hard standing/ earth.
· If any leaks or spills of substances occur, which have the potential to harm the environment or pose a risk to human health escape the site boundary, the management will inform the Environment Agency immediately. Any remedial action specified by the Environment Agency will be undertaken, a record of which will be made in the site diary.

     Waste Acceptance, Storage and Inspection     

     To deal with the acceptance, storage & inspection of waste on-site.

     Introduction

The company will introduce a system of storage on-site to minimise the potential for cross contamination and potential run off from wastes whilst stored on site.

Waste Types
Only the waste types and EWC codes named on the environmental permit will be accepted at the site. Wastes entering the site will be inspected and registered at the site. Non-compliant waste materials not allowed on the permit will be turned away from the site. A record will be made in the site diary. 
     Working Hours
     Normal working hours will be 0700-1730  Monday - Friday
     Saturday 0700-1300 and Sunday – closed

Responsibility

     The Environmental Manager (Andrew Newman) is responsible for identifying and  highlighting non-conforming waste. The Environmental Manager is responsible for inspecting, documenting and safe removal of any non-conforming waste. 

Waste Storage
Discreet areas will be nominated on-site for each waste type. These will be labelled and identified on the site plan. The site plan will be updated on a regular basis provide a record of what type of waste and quantity is stored where.

Waste Acceptance

The procedure that shall be adopted at site is detailed below

 1. Waste arrives on site.

2. Documentation is checked at the entrance. 

3. All vehicles will have their contents examined during unloading and this shall be crosschecked with the documentation presented. 

4. Staff will check that the type of waste is acceptable in terms of the waste licence. 

5. If the waste is unacceptable the waste shall be isolated and arrangements put in place for the contractor to remove the waste from site. 

6. If the person who is checking in the load is suspicious of its contents the driver shall be directed to the waste inspection area in the yard, where the load shall be inspected to ensure that it corresponds to the accompanying documentation. In any event compliance testing will be carried out at regular intervals.

 7. Assuming the on-site verification is satisfactory, the load is weighed in and directed to yard as appropriate. Here, the waste will be checked again to verify that the description is correct.
Waste Segregation

Waste will be segregated and stored as per TGN 7.01 To ensure that the potential for fire is minimised, waste types that are flammable will not be stored close to other flammable types and fire break areas will be maintained between piles. 

Waste Area Inspection
As part of the EMS waste areas are inspected routinely, deviations from normal operation conditions, result are logged and acted upon in the site log.

Records
National Tyre Recovery shall keep records of all waste loads rejected, these records will include; 

· Date

· Name of Carrier  

· Source of Waste  

· Vehicle Registration  

· Description of Waste

· EWC code 

· Quantity of Waste 

· Name of person carrying out inspection 

Destination of Load prior to rejection
Annex J – Fire extinguishers
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Annex K – electrical equipment
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Annex L – certificates, maintenance regimes and schedules for training, cameras and PAT equipment testing.
[image: image16.jpg]Certified Entity

HIKVISION DO BRA CO DE EQUI DE SEG LTDA
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Management System
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Certification Body
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View Certificate Information

Search here for details of UKAS accredited laboratories, inspection bodies and certification bodies.
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� Fire Prevention Plans, January 2021.


� Provision and Use of Work Equipment Regulations 1998 (PUWER)


� https://www.weatheronline.co.uk/weather/maps/city?FMM=1&FYY=2000&LMM=12&LYY=2020&WMO=03534&CONT=ukuk&REGION=0003&LAND=UK&ART=WDR&R=0&NOREGION=0&LEVEL=162&LANG=en&MOD=tab
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