## Containment Areas
RECOMMENDATIONS FROM STANTEC REPORT | ESTIMATING SCOPE
Figure 25: Proposed mitigation and settled sludge depth for Digester Tank
Figure 26: Proposed mitigation and settled sludge depth for Screened Sludge Tank
Total
|  | CONTAINMENT KERB | mm
Figure 27: Proposed mitigation and settled sludge depth for Digested Sludge Tank |  |  | m | [5 empty] | 0 | See sheet 'Kerbing Detail'
|  |  |  | Section 1 |  | Total
|  | CONTAINMENT WALL 1.5m (H) | mm | 234000
|  |  | m | 234 |  | 234 | See sheet ' Containment Wall'
|  |  |  | Section 2 | Section 4 |  | Total
|  | CONTAINMENT WALL 1.0m (H) | mm | 326000 | 100000
|  |  | m | 326 | 100 |  | 426 | See sheet ' Containment Wall'
|  |  |  | Section 3 |  |  |  | Total
|  | FLOOD GATE 1.0m (H) | mm | 17000
|  |  | m | 17 |  |  |  | 17 | See cheet 'CONTAINMENT ROAD BUND'
Figure 28: Proposed mitigation and settled sludge depth for Thickened Sludge Silo
Figure 28: Proposed mitigation and settled sludge depth for Thickened Sludge Silo
Figure 29: Proposed mitigation and settled sludge depth for Thickening Centrate Storage Tank
Figure 30: Proposed mitigation and settled sludge depth for Dewatering Centrate Buffer Tank
Section 1
Section 2
Section 3
Section 4

## Containment Wall
|  |  | CONTAINMENT WALL SECTION A 1.5m HIGH | 234 | m
[7 empty] | Approx . Backfill volume m3 | 106.1918
Assume imported material
C30 strength RC
[7 empty] | Approx. area 0.5m deep layer (mm2) | 26547944.5
[7 empty] | Approx. area 0.5m deep (m2) | 26.5479
[7 empty] | No. 0.5m deep layers | 4
|  |  | CONTAINMENT WALL SECTION B 1.0m HIGH | 426 | m
Additional items to consider:
| Vegetation removal | 200m x 10m
| Compensatory planting (shrubbed area including allowance for small trees) | 4000m2
| Existing fence removal & replacement | 200m
▲ESTIMATING SCOPE▲
▼ Jetting Calc ▼
Jetting distance
Section A
Vegetation removal & compenstory planting
Backfill / regraded area - Section C
Typical Section A (Proposed)
Containment wall
Typical Section (Proposed)
Containment retaining wall
Typical Section C (Proposed) Containment retaining wall and Containment wall
Section B
1500
1500
2000
1500
Typical Section B (Proposed)
Containment wall
1750

## SACRIFICIAL AREA DRAINAGE
ONLY REQUIRED FOR OPTION B1
Impermeable membrane area Strip existing surfacing (assume gravel), prep surface, lay membrane, reinstate surfacing | 8000 | m2
Length of French drains | 970 | m
No. of existing manhole connections | TBC | No.
https://uusp/engdel/Standards/engineering%20standards/Standard%20Details/STND_00%20Miscellaneous/Current%20Versions/STND-00-001_B.pdf
|  |  | ID | Area | Area | Connecting Manhole | CL | IL | EGL | Start IL | Gradient | DN | Length | End IL | Check
|  |  |  | mm2 | m2 | [10 empty] | https://www.uksuds.com/tools/members/surface-water-storage-volume-estimation-members
|  |  | A | 911450000 | 911.45 | MH | 89.99 | 88.7 | 89.99 | 89.29 | 0.5% | 150 | 112 | 88.73 | OK | Using this online tool to give inidcation of surface water capacity needed
[17 empty] | Notes for WwTW | LEIGH WwTW
|  |  | B | 282270000 | 282.27 | MH18 | 88.95 | 87.04 | 88.95 | 88.25 | 0.5% | 150 | 22 | 88.14 | OK | Site latitude | Use map zoom and drop pin on location | 53.486358° N
|  |  | C | 768260000 | 768.26 | MH12 | 89.71 | 87.3 | 89.71 | 89.01 | 0.5% | 150 | 42 | 88.8 | OK | Site longitude | Use map zoom and drop pin on location | 2.95812° W
|  |  | D | 1511280000 | 1511.28 | MH14 | 89.88 | 87.88 | 89.88 | 89.18 | 0.5% | 150 | 168 | 88.34 | OK | Total site area (m2) | Total additional impermeable area created by option | 8000
|  |  | E | 133770000 | 133.77 | TBC | TBC | TBC | TBC | #VALUE! | 0.5% | 150 | 36 | #VALUE! | #VALUE! | Total site area (ha) |  | 0.8
|  |  | F | 1408590000 | 1408.59 | MH | 91.89 | 90.19 | 91.89 | 91.19 | 0.5% | 150 | 170 | 90.34 | OK | Significant public open space (ha) |  | 0
|  |  | G | 402170000 | 402.17 | MH2 | 90.78 | 87.91 | 90.78 | 90.08 | 0.5% | 150 | 100 | 89.58 | OK | Area positively drained (ha) |  | 0.8
|  |  | H | 543110000 | 543.11 | TBC | TBC | TBC | TBC | #VALUE! | 0.5% | 150 | 45 | #VALUE! | #VALUE! | Impermeable area (ha) |  | 1.2
|  |  | J | 51810000 | 51.81 | MH1 | 91.45 | 89.34 | 91.45 | 90.75 | 0.5% | 150 | 50 | 90.5 | OK | Drained area that is impermeable (%) |  | 150%
|  |  | K | 1256780000 | 1256.78 | TBC | TBC | TBC | TBC | #VALUE! | 0.5% | 150 | 125 | #VALUE! | #VALUE! | Impervious area drained via infiltration (ha) |  | 0
|  |  | L | 114890000 | 114.89 | TBC | TBC | TBC | TBC | #VALUE! | 0.5% | 150 | 31 | #VALUE! | #VALUE! | Return period for infiltration system design (years) |  | 100
|  |  | M | 268530000 | 268.53 | TBC | TBC | TBC | TBC | #VALUE! | 0.5% | 150 | 65 | #VALUE! | #VALUE! | Impervious area drained to rainwater harvesting systems (ha) | Assume zero | 0
[5 empty] | 7652.91 | [7 empty] | 966 |  |  | Return period for rainwater harvesting system design (years) | Default | 10
[16 empty] | Compliance factor for rainwater harvesting system design (%) | Default | 66%
[16 empty] | Net site area for storage volume design (ha) | Calculated | 1.2
[16 empty] | Net impermeable area for storage volume design (ha) | Calculated | 1.2
[16 empty] | Pervious area contribution (%) | Default | 30
[16 empty] | Rainfall 100yrs 6hrs (mm) | Results using the IH24 method | 55
[16 empty] | Rainfall 100yrs 12hrs (mm) | Results using the IH24 method | 74.34
[16 empty] | Qbar (l/s) |  | 2.09
[16 empty] | 1 in 1 year (l/s) |  | 2
[16 empty] | 1 in 30 year (l/s) |  | 3.5
[16 empty] | 1 in 100 years (l/s) |  | 4.3
[16 empty] | Attenuation storage (m3) |  | 608
[16 empty] | Long term storage (m3) |  | 188
[16 empty] | Total storage (m3) |  | 796
[16 empty] | 1 in 30 year area rate (l/s/m2) |  | 0.0004375
[16 empty] | DN150 Proposal capacity (@1 in 200 ks=1.5mm) | l/s | 10.9052
[16 empty] | AREA PER PIPE( DN150) | m2 | 24926.2291
Area D
Area C
Area B
Area A
Area E
Area F
Area G
Area H
Area J
Area K
Area L
Area M