## README
VERSION DATE: April 2019
Air Quality Modelling and Assessment Unit (AQMAU)
Specified Generator Tranche B Screening Tool
Version 2.2
OVERVIEW:
This tool is for screening simple bespoke low risk Tranche B specified generators which cannot meet the available standard rules permits. You need to populate and run the tool. The run tool must be submitted with your simple bespoke application. To use the tool the specified generator needs to:
• be a Tranche B specified generator site, or a mixed Tranche A and B specified generator site where all Tranche A generators comply with the Tranche B requirements • be a single or group of new or existing engines that can achieve the Medium Combustion Plant Directive and/or specified generator emission limit values • have vertical stacks that are unimpeded by cowls or caps • be fuelled on natural gas, that is, there are insignificant emissions of sulphur dioxide and particulates • or, be fuelled on ultra low sulphur diesel with secondary abatement (SCR), used for balancing (no more than 500 hours), and aggregated to no more than 20MWth
Further information is provided in Environment Agency guidance:
Specified generator: comply with permit conditions (https://www.gov.uk/guidance/specified-generator-comply-with-permit-conditions)
Specified generator: apply for an environmental permit (https://www.gov.uk/guidance/specified-generator-apply-for-an-environmental-permit)
To discuss any site or application please contact:
MCPDHelp@environment-agency.gov.uk
COPYRIGHT © 2018 ENVIRONMENT AGENCY ALL RIGHTS RESERVED
Redistribution of this tool and use in source and binary forms, with or without modification, are permitted provided that the following conditions are met:
1. Redistributions of source code must retain the above copyright notice, this list of conditions and the following disclaimer.
2. Redistributions in binary form must reproduce the above copyright notice, this list of conditions and the following disclaimer in the documentation and/or other materials provided with the distribution.
DISCLAIMER:
THIS SOFTWARE IS PROVIDED BY THE ENVIRONMENT AGENCY, AND CONTRIBUTORS "AS IS" AND ANY EXPRESS OR IMPLIED WARRANTIES, INCLUDING, BUT NOT LIMITED TO, THE IMPLIED WARRANTIES OF MERCHANTABILITY AND FITNESS FOR A PARTICULAR PURPOSE ARE DISCLAIMED. IN NO EVENT SHALL THE ENVIRONMENT AGENCY OR CONTRIBUTORS BE LIABLE FOR ANY DIRECT, INDIRECT, INCIDENTAL, SPECIAL, EXEMPLARY, OR CONSEQUENTIAL DAMAGES (INCLUDING, BUT NOT LIMITED TO, PROCUREMENT OF SUBSTITUTE GOODS OR SERVICES; LOSS OF USE, DATA, OR PROFITS; OR BUSINESS INTERRUPTION) HOWEVER CAUSED AND ON ANY THEORY OF LIABILITY, WHETHER IN CONTRACT, STRICT LIABILITY, OR TORT (INCLUDING NEGLIGENCE OR OTHERWISE) ARISING IN ANY WAY OUT OF THE USE OF THIS SOFTWARE, EVEN IF ADVISED OF THE POSSIBILITY OF SUCH DAMAGE.
LICENCE:
Open Government Licence for public sector information
http://www.nationalarchives.gov.uk/doc/open-government-licence/version/3/

## User_Interface
Air Quality Modelling and Assessment Unit (AQMAU)
SPECIFIED GENERATOR TRANCHE B SCREENING TOOL
Version 2.2
STEP1: GENERAL SITE INFORMATION
|  |  |  | Type list | Yes/No | Existing/New | Background list | Fuel
Applicant name | Addo Foods |  | USER NOTES: Please enter the name that will appear on the environmental permit. | CHP | Yes | Existing | Rural | Natural gas
|  |  |  | Peaking | No | New | Suburban | Diesel (ultra low sulphur)
|  |  |  | Balancing |  | Other | Industrial
Specified generator usage type category (Select the cell and choose from the drop-down list) | CHP |  | USER NOTES: CHP - Combined heat and power plant typically used to provide mid-merit or base load electricity and therefore assumed to operate up to 8760 hours per year. Peaking - Peaking plants are used to provide power during grid peak demand periods and are assumed to operate between 501 and 1500 hours per year. Balancing - Balancing plants are considered to operate between 51 and 500 hours per year and are typically used to provide balancing power reserve to the grid. |  |  |  | Urban
Fuel (Select the cell and choose from the drop-down list) | Natural gas |  | USER NOTES: Natural gas - Can be used for screening of all usage types (CHP, Peaking and Balancing). Diesel (ultra low sulphur) - Can be used for screening for balancing operations only (between 51 and 500 hours per year).
Is it a mixed Tranche A and B specified generator site? (Select yes or no) | No |  | USER NOTES: Select yes, if there are any Tranche A generators on the specified generator site. If there are, then all Tranche A generators must comply with the Tranche B generator requirements. Select no, if there are no Tranche A generators on the specified generator site.
Specified generators aggregated rated thermal input | 3.517 | MW | USER NOTES: This is the total aggregated thermal input of all generators on the specified generator site. It should include Tranche A and B generators for mixed sites. CHPs - Screening distances for up to 25MWth aggregated plant have been calculated. Peaking and balancing plant - Screening distances for up to 50MWth aggregated plant have been calculated.
Operational hours per year | 8760 | hours | USER NOTES: Enter the number of operational hours per year. Select yes, if rolling average flexibility is required for the peaking or balancing plant. These are: rolling averages over a period of 3 years for new plant operating no more than 500 hours per year; and 5 years for existing plant operating no more than 500 hours per year or plant operating between 501 and 1500 hours per year. Otherwise select no.
If 'Peaking' or 'Balancing', is rolling average flexibility required? (Select yes or no) | No
Existing or new medium combustion plant generators? (Select the cell and choose from the drop-down list) | New |  | USER NOTES: Generators with rated thermal input greater than 1 MW and less than 50 MW are medium combustion plant. Those that operate more than 500 hours per year will be required to comply with MCPD ELVs, those that operate up to 500 hours must comply with the SG ELV. Existing - MCPs operating before 20 December 2018 and more than 500 hours (MCPD ELV 190mg/Nm3). New - MCPs operating after 20 December 2018 and more than 500 hours (MCPD ELV 95mg/Nm3). Other - MCPs operating up to 500 hours per year, or generators with individual rated thermal inputs less than 1 MW (SG ELV 190mg/Nm3).
Emission Limit Value (273K, dry and 15% O2) (Automatically selected) | 95 | mg/Nm3
Do the generators have secondary abatement fitted? (Select yes or no) | No |  | USER NOTES: Select yes, if secondary abatement is used to reduce emissions from generators on the specified generator site. Select no, if no secondary abatement is fitted.
Attainable emission concentration (273K, dry and 15% O2) |  | mg/Nm3 | USER NOTES: Enter the emission concentration that all the generators on the site can achieve. If it is a mixed Tranche A and B site, it should be no more than the specified generator ELV of 190mg/Nm3. A lower emission limit value can be set and screened against if it can be achieved. The lowest emission limit value possible is 35mg/Nm3, which can be achieved when secondary abatement is fitted. If left blank the screening emission limit value will be set automatically.
Screening Emission Limit Value (273K, dry and 15% O2) (Automatically selected) | 95 | mg/Nm3
STEP 2: RELEASE INFORMATION
Stack height | 15 | m | USER NOTES: The stack height is the height of the top of the stack above ground level of the release point. If there are multiple generator stacks then the lowest stack should be entered.
Is there one or more buildings within 5L and with heights more than 40% of the stack height? (Select yes or no) | Yes |  | USER NOTES: If yes, all buildings that could affect dispersion must be combined into a single effective combined block. Buildings that can affect dispersion must be both: • Within 5L of the stack, where L is the lowest of either the height of the building, or the maximum projected width (for example, the opposing corners of a roof). Typically, L will be the building height unless the building is a tower. • Have a height that is more than 40% of the stack height. Select no, only if there are no buildings that satisfy the above criteria.
Height of tallest building within 5L | 7 | m | USER NOTES: Enter height of tallest building that can affect dispersion. Enter the length and width of the building or the combined block building. If there are no buildings that could affect dispersion then leave blank.
Length (or length of combined block for multiple buildings) | 170 | m
Width (or width of combined block for multiple buildings) | 80 | m
Maximum downwash cavity length | 26 | m | USER NOTES: There are very high uncertainties when predicting impacts in the cavity region of buildings that cause downwash. Select yes, if there are any sensitive receptors within the calculated downwash cavity length from any side or corner of the inputted building. Otherwise, select no.
Are there any receptors within the downwash cavity length from the nearest edge/side of the building? (Select yes or no) | No
STEP 3: STUDY AREA SETTING AND BACKGROUND CONCENTRATIONS
Sensitive receptor setting (Select the cell and choose from the drop-down list) | Suburban |  | USER NOTES: The study area should be defined based on a 1km buffer zone around the site. Rural - Rural settings are locations in the open countryside, agricultural areas, villages and small towns. Suburban - Suburban settings are mixed-use or residential areas on the outskirts of a city or large town. Industrial - Industrial settings are locations where industry is the main land use and makes a contribution to the pollution burden. Urban - Urban settings are considered to be locations in the main areas of a city or large town.
Sensitive receptors near an A road or motorway network? (Select yes or no) | Yes |  | USER NOTES: Receptors near roads have elevated background NO2 concentrations. Select yes, if there is an A road (main road) or motorway within 50m of receptors in the study area. Otherwise, select no.
Sensitive receptors within an AQMA declared for NO2? (Select yes or no) | No |  | USER NOTES: If there are receptors within an Air Quality Management Area (AQMA), then there is likely to be little or no headroom. Find current AQMAs on Defra's UK Air website: https://uk-air.defra.gov.uk/aqma/maps Select yes, if the receptor is within an AQMA declared for nitrogen dioxide (NO2). Otherwise select no.
Baseline background NO2 concentration | 12 | µg/m3 | USER NOTES: Enter the assumed baseline background concentration for the study area. The local authority can give baseline background concentrations for the study area from their local air quality management responsibilities. The baseline background should not be a roadside or kerbside concentration.
STEP 4: RECEPTORS
Distance to nearest non-roadside human health receptor | 85 | m | USER NOTES: Enter the shortest distance from any generator stack to the nearest receptor where there is relevant public exposure. Non-roadside receptors are those where there is public exposure beyond 15m of any road or street. Roadside receptors are those where there is public exposure within 15m of a busy road or junction (10,000 vehicles/day or more), or a congested narrow streets (5,000 vehicles/day. Higher backgrounds are automatically assumed for these receptors. Select yes, if there if there is relevant public exposure within 15m of a busy road and enter the distance to the nearest roadside receptor. Otherwise, select no and enter no distance.
Are there any human health receptors where there is roadside public exposure? | Yes
Distance to nearest roadside human health receptor | 735 | m
Are there any SACs, SPAs, Ramsar sites within 5km or SSSIs within 2km? | Yes |  | USER NOTES: Select yes, if there is a SAC (Special Area of Conservation), SPA (Special Protection Area) or Ramsar site within 5km, or SSSI (Site of Special Scientific Interest) within 2km. If yes, enter the distance in meters from any generator stack to the nearest habitat site. Otherwise, select no and enter no distance. Find sites on Defra's Magic Map: http://magic.defra.gov.uk/MagicMap.aspx
Distance to nearest SAC, SPA, Ramsar site or SSSI | 285 | m
STEP 5: ENVIRONMENTAL RISK
Non-roadside human health screening distance is: | 150 | m
Roadside human health screening distance is: | 250 | m
The SAC, SPA, Ramsar site or SSSI screening distance is: | 800 | m
Screening result: | Screens in for human health and habitats. Complex bespoke application required.
Screening result: | Screens in based on the 'Balancing' diesel generators aggregated thermal input being more than 20MW. Complex bespoke application required.

## InputOutput calculations (hidden)
User input data
Type | CHP
Capacity | 3.517 | MW
Fuel | Natural gas
Operational hours | 8760 | hours per year
CHP opertional hour scaled capacity | 3.5 | MW | Temporary fix for no opertional hour look-up tables for CHPs.
Balancing capacity | 3.517 | MW | 2.5 factor based on (unabated emission at 1850 mg/Nm3 for 10 minutes and 190 mg/Nm3 for 50 minutes)
Rolling average | No
Secondary abatement | No
ELV | 95 | mg/Nm3
Stack height | 15 | m
Building height | 7 | m
Building length | 170 | m
Building width | 80 | m
Site setting | Suburban
Busy Road | Yes
AQMA | No
App baseline background | 12
Building calcualtions
Actual clearance | 8 | m
WB | 187.8829 | m
LB | 44.2078 | m
A | 1.0355 | m
B | 0.24
LR | 26.1437 | m | Max cavity length
Receptors within cavity? | No
Is downwash an issue? | No
Catagrosed tool data
Type | CHP-95 | CHP-190 | CHP-35 | Peaking-95 | Peaking-190 | Balancing
Capacity | 5 | 5 | 5 | 10 | 10 | 5 | MW
Operating hours | N/A | N/A | N/A | N/A | N/A | N/A | hours
Stack height | 10 | 10 | 10 | 10 | 10 | 10 | m
Clearance | 5 | 5 | 5 | 7 | 7 | 7
Tool background | 35 | 35 | 35 | 35 | 35 | 35
Final baseline background | 35 | 35 | 35 | 35 | 35 | 35
Roadside background | 40 | 40 | 40 | 40 | 40 | 40
Screening distances
HH screening distance | 150 | 250 | 0 | #N/A | #N/A | #N/A
HH screening distance-roadside | 250 | 400 | 0 | #N/A | #N/A | #N/A
Habitats screening distance | 800 | 1300 | 400 | #N/A | #N/A | #N/A
Roadside public exposure | Yes
Final HH screening distance | 150 | m
Final HH screening distance-roadside | 250 | m
Final habitats screening distance | 800 | m

## CHP lookup matrix (hidden)
Source group | Capacity | Stack height | Clearance | Background | Acceptable PC | Unique NO2 PC | NO2 Screening distance | Source group | Capacity | Stack height | Clearance | Background | Acceptable PC | Unique NOX PC | NOX Screening distance | Source group | Capacity | Stack height | Clearance | Background | Acceptable PC | Unique NO2 PC | NO2 Screening distance | Source group | Capacity | Stack height | Clearance | Background | Acceptable PC | Unique NOX PC | NOX Screening distance |  | Source group | Capacity | Stack height | Clearance | Background | Acceptable PC | Unique NO2 PC | NO2 Screening distance | Source group | Capacity | Stack height | Clearance | Background | Acceptable PC | Unique NOX PC | NOX Screening distance
CHP1 | 5 | 5 | 0 | 30 | 6 | 5.9234 | 100 | CHP1 | 5 | 5 | 0 | N/A | 0.45 | 0.41723 | 850 | CHP1 | 5 | 5 | 0 | 30 | 6 | 4.7909 | 200 | CHP1 | 5 | 5 | 0 | N/A | 0.45 | 0.44175 | 1300 | 3100 | CHP1 | 5 | 5 | 0 | 30 | 6 | 3.9012 | 50 | CHP1 | 5 | 5 | 0 | N/A | 0.45 | 0.38612 | 450
CHP1 | 5 | 5 | 0 | 35 | 3 | 2.3954 | 200 | CHP2 | 5 | 5 | 2.5 | N/A | 0.45 | 0.41934 | 850 | CHP1 | 5 | 5 | 0 | 35 | 3 | 2.6418 | 300 | CHP2 | 5 | 5 | 2.5 | N/A | 0.45 | 0.44534 | 1300 |  | CHP1 | 5 | 5 | 0 | 35 | 3 | 2.1823 | 100 | CHP2 | 5 | 5 | 2.5 | N/A | 0.45 | 0.3852 | 450
CHP1 | 5 | 5 | 0 | 40 | 1.6 | 1.3209 | 300 | CHP3 | 5 | 10 | 0 | N/A | 0.45 | 0.4425 | 800 | CHP1 | 5 | 5 | 0 | 40 | 1.6 | 1.4672 | 450 | CHP3 | 5 | 10 | 0 | N/A | 0.45 | 0.41967 | 1300 |  | CHP1 | 5 | 5 | 0 | 40 | 1.6 | 1.3192 | 150 | CHP3 | 5 | 10 | 0 | N/A | 0.45 | 0.38586 | 450
CHP2 | 5 | 5 | 2.5 | 30 | 6 | 5.273 | 100 | CHP4 | 5 | 10 | 5 | N/A | 0.45 | 0.41429 | 800 | CHP2 | 5 | 5 | 2.5 | 30 | 6 | 4.6495 | 200 | CHP4 | 5 | 10 | 5 | N/A | 0.45 | 0.40716 | 1300 |  | CHP2 | 5 | 5 | 2.5 | 30 | 6 | 2.8556 | 50 | CHP4 | 5 | 10 | 5 | N/A | 0.45 | 0.40191 | 400
CHP2 | 5 | 5 | 2.5 | 35 | 3 | 2.3248 | 200 | CHP5 | 5 | 20 | 0 | N/A | 0.45 | 0.44539 | 750 | CHP2 | 5 | 5 | 2.5 | 35 | 3 | 2.6154 | 300 | CHP5 | 5 | 20 | 0 | N/A | 0.45 | 0.43426 | 1200 |  | CHP2 | 5 | 5 | 2.5 | 35 | 3 | 2.8556 | 50 | CHP5 | 5 | 20 | 0 | N/A | 0.45 | 0.41759 | 400
CHP2 | 5 | 5 | 2.5 | 40 | 1.6 | 1.3077 | 300 | CHP6 | 5 | 20 | 5 | N/A | 0.45 | 0.43142 | 750 | CHP2 | 5 | 5 | 2.5 | 40 | 1.6 | 1.4638 | 450 | CHP6 | 5 | 20 | 5 | N/A | 0.45 | 0.42812 | 1200 |  | CHP2 | 5 | 5 | 2.5 | 40 | 1.6 | 1.2464 | 150 | CHP6 | 5 | 20 | 5 | N/A | 0.45 | 0.38625 | 400
CHP3 | 5 | 10 | 0 | 30 | 6 | 5.8451 | 100 | CHP7 | 5 | 20 | 10 | N/A | 0.45 | 0.44859 | 650 | CHP3 | 5 | 10 | 0 | 30 | 6 | 4.8759 | 200 | CHP7 | 5 | 20 | 10 | N/A | 0.45 | 0.43156 | 1100 |  | CHP3 | 5 | 10 | 0 | 30 | 6 | 2.6043 | 50 | CHP7 | 5 | 20 | 10 | N/A | 0.45 | 0.38628 | 350
CHP3 | 5 | 10 | 0 | 35 | 3 | 2.4379 | 200 | CHP8 | 10 | 5 | 0 | N/A | 0.45 | 0.42264 | 1200 | CHP3 | 5 | 10 | 0 | 35 | 3 | 2.6666 | 300 | CHP8 | 10 | 5 | 0 | N/A | 0.45 | 0.43318 | 1900 |  | CHP3 | 5 | 10 | 0 | 35 | 3 | 2.6043 | 50 | CHP8 | 10 | 5 | 0 | N/A | 0.45 | 0.41129 | 600
CHP3 | 5 | 10 | 0 | 40 | 1.6 | 1.3333 | 300 | CHP9 | 10 | 5 | 2.5 | N/A | 0.45 | 0.42402 | 1200 | CHP3 | 5 | 10 | 0 | 40 | 1.6 | 1.4663 | 450 | CHP9 | 10 | 5 | 2.5 | N/A | 0.45 | 0.4357 | 1900 |  | CHP3 | 5 | 10 | 0 | 40 | 1.6 | 1.3479 | 150 | CHP9 | 10 | 5 | 2.5 | N/A | 0.45 | 0.41086 | 600
CHP4 | 5 | 10 | 5 | 30 | 6 | 2.5792 | 0 | CHP10 | 10 | 10 | 0 | N/A | 0.45 | 0.39689 | 1200 | CHP4 | 5 | 10 | 5 | 30 | 6 | 5.2101 | 150 | CHP10 | 10 | 10 | 0 | N/A | 0.45 | 0.43694 | 1800 |  | CHP4 | 5 | 10 | 5 | 30 | 6 | 0.95023 | 0 | CHP10 | 10 | 10 | 0 | N/A | 0.45 | 0.44817 | 550
CHP4 | 5 | 10 | 5 | 35 | 3 | 2.605 | 150 | CHP11 | 10 | 10 | 5 | N/A | 0.45 | 0.44162 | 1100 | CHP4 | 5 | 10 | 5 | 35 | 3 | 2.9108 | 250 | CHP11 | 10 | 10 | 5 | N/A | 0.45 | 0.43687 | 1800 |  | CHP4 | 5 | 10 | 5 | 35 | 3 | 0.95023 | 0 | CHP11 | 10 | 10 | 5 | N/A | 0.45 | 0.4169 | 550
CHP4 | 5 | 10 | 5 | 40 | 1.6 | 1.4554 | 250 | CHP12 | 10 | 20 | 0 | N/A | 0.45 | 0.43744 | 1100 | CHP4 | 5 | 10 | 5 | 40 | 1.6 | 1.5273 | 400 | CHP12 | 10 | 20 | 0 | N/A | 0.45 | 0.4197 | 1800 |  | CHP4 | 5 | 10 | 5 | 40 | 1.6 | 0.95023 | 0 | CHP12 | 10 | 20 | 0 | N/A | 0.45 | 0.44673 | 550
CHP5 | 5 | 20 | 0 | 30 | 6 | 4.3572 | 50 | CHP13 | 10 | 20 | 5 | N/A | 0.45 | 0.41837 | 1100 | CHP5 | 5 | 20 | 0 | 30 | 6 | 4.4104 | 200 | CHP13 | 10 | 20 | 5 | N/A | 0.45 | 0.44198 | 1700 |  | CHP5 | 5 | 20 | 0 | 30 | 6 | 1.6053 | 50 | CHP13 | 10 | 20 | 5 | N/A | 0.45 | 0.40553 | 550
CHP5 | 5 | 20 | 0 | 35 | 3 | 2.2052 | 200 | CHP14 | 10 | 20 | 10 | N/A | 0.45 | 0.44786 | 950 | CHP5 | 5 | 20 | 0 | 35 | 3 | 2.438 | 300 | CHP14 | 10 | 20 | 10 | N/A | 0.45 | 0.44022 | 1600 |  | CHP5 | 5 | 20 | 0 | 35 | 3 | 1.6053 | 50 | CHP14 | 10 | 20 | 10 | N/A | 0.45 | 0.44467 | 450
CHP5 | 5 | 20 | 0 | 40 | 1.6 | 1.5987 | 250 | CHP15 | 15 | 5 | 0 | N/A | 0.45 | 0.41189 | 1500 | CHP5 | 5 | 20 | 0 | 40 | 1.6 | 1.5868 | 400 | CHP15 | 15 | 5 | 0 | N/A | 0.45 | #N/A | 2400 |  | CHP5 | 5 | 20 | 0 | 40 | 1.6 | 1.3646 | 100 | CHP15 | 15 | 5 | 0 | N/A | 0.45 | 0.4314 | 700
CHP6 | 5 | 20 | 5 | 30 | 6 | 1.0349 | 0 | CHP16 | 15 | 5 | 2.5 | N/A | 0.45 | 0.41279 | 1500 | CHP6 | 5 | 20 | 5 | 30 | 6 | 2.0699 | 0 | CHP16 | 15 | 5 | 2.5 | N/A | 0.45 | #N/A | 2400 |  | CHP6 | 5 | 20 | 5 | 30 | 6 | 0.38129 | 0 | CHP16 | 15 | 5 | 2.5 | N/A | 0.45 | 0.4311 | 700
CHP6 | 5 | 20 | 5 | 35 | 3 | 1.0349 | 0 | CHP17 | 15 | 10 | 0 | N/A | 0.45 | 0.42247 | 1400 | CHP6 | 5 | 20 | 5 | 35 | 3 | 2.8534 | 250 | CHP17 | 15 | 10 | 0 | N/A | 0.45 | #N/A | 2200 |  | CHP6 | 5 | 20 | 5 | 35 | 3 | 0.38129 | 0 | CHP17 | 15 | 10 | 0 | N/A | 0.45 | 0.40766 | 700
CHP6 | 5 | 20 | 5 | 40 | 1.6 | 1.4267 | 250 | CHP18 | 15 | 10 | 5 | N/A | 0.45 | 0.42221 | 1400 | CHP6 | 5 | 20 | 5 | 40 | 1.6 | 1.4677 | 400 | CHP18 | 15 | 10 | 5 | N/A | 0.45 | #N/A | 2300 |  | CHP6 | 5 | 20 | 5 | 40 | 1.6 | 0.38129 | 0 | CHP18 | 15 | 10 | 5 | N/A | 0.45 | 0.43261 | 650
CHP7 | 5 | 20 | 10 | 30 | 6 | 0.12269 | 0 | CHP19 | 15 | 20 | 0 | N/A | 0.45 | 0.42025 | 1400 | CHP7 | 5 | 20 | 10 | 30 | 6 | 0.24538 | 0 | CHP19 | 15 | 20 | 0 | N/A | 0.45 | #N/A | 2300 |  | CHP7 | 5 | 20 | 10 | 30 | 6 | 0.045201 | 0 | CHP19 | 15 | 20 | 0 | N/A | 0.45 | 0.42252 | 700
CHP7 | 5 | 20 | 10 | 35 | 3 | 0.12269 | 0 | CHP20 | 15 | 20 | 5 | N/A | 0.45 | 0.4391 | 1300 | CHP7 | 5 | 20 | 10 | 35 | 3 | 2.747 | 200 | CHP20 | 15 | 20 | 5 | N/A | 0.45 | #N/A | 2100 |  | CHP7 | 5 | 20 | 10 | 35 | 3 | 0.045201 | 0 | CHP20 | 15 | 20 | 5 | N/A | 0.45 | 0.41692 | 650
CHP7 | 5 | 20 | 10 | 40 | 1.6 | 1.3735 | 200 | CHP21 | 15 | 20 | 10 | N/A | 0.45 | 0.4398 | 1200 | CHP7 | 5 | 20 | 10 | 40 | 1.6 | 1.4679 | 350 | CHP21 | 15 | 20 | 10 | N/A | 0.45 | 0.44147 | 2000 |  | CHP7 | 5 | 20 | 10 | 40 | 1.6 | 0.045201 | 0 | CHP21 | 15 | 20 | 10 | N/A | 0.45 | 0.44529 | 550
CHP8 | 10 | 5 | 0 | 30 | 6 | 5.2265 | 150 | CHP22 | 20 | 5 | 0 | N/A | 0.45 | 0.42443 | 1700 | CHP8 | 10 | 5 | 0 | 30 | 6 | 5.3907 | 250 | CHP22 | 20 | 5 | 0 | N/A | 0.45 | #N/A | 2800 |  | CHP8 | 10 | 5 | 0 | 30 | 6 | 4.4135 | 50 | CHP22 | 20 | 5 | 0 | N/A | 0.45 | 0.43126 | 800
CHP8 | 10 | 5 | 0 | 35 | 3 | 2.6953 | 250 | CHP23 | 20 | 5 | 2.5 | N/A | 0.45 | 0.42483 | 1700 | CHP8 | 10 | 5 | 0 | 35 | 3 | 2.7539 | 400 | CHP23 | 20 | 5 | 2.5 | N/A | 0.45 | #N/A | 2800 |  | CHP8 | 10 | 5 | 0 | 35 | 3 | 2.9447 | 100 | CHP23 | 20 | 5 | 2.5 | N/A | 0.45 | 0.43096 | 800
CHP8 | 10 | 5 | 0 | 40 | 1.6 | 1.3769 | 400 | CHP24 | 20 | 10 | 0 | N/A | 0.45 | 0.431 | 1600 | CHP8 | 10 | 5 | 0 | 40 | 1.6 | 1.5629 | 600 | CHP24 | 20 | 10 | 0 | N/A | 0.45 | #N/A | 2600 |  | CHP8 | 10 | 5 | 0 | 40 | 1.6 | 1.3443 | 200 | CHP24 | 20 | 10 | 0 | N/A | 0.45 | 0.44055 | 750
CHP9 | 10 | 5 | 2.5 | 30 | 6 | 4.9802 | 150 | CHP25 | 20 | 10 | 5 | N/A | 0.45 | 0.43164 | 1600 | CHP9 | 10 | 5 | 2.5 | 30 | 6 | 5.3118 | 250 | CHP25 | 20 | 10 | 5 | N/A | 0.45 | #N/A | 2700 |  | CHP9 | 10 | 5 | 2.5 | 30 | 6 | 3.3007 | 50 | CHP25 | 20 | 10 | 5 | N/A | 0.45 | 0.42849 | 750
CHP9 | 10 | 5 | 2.5 | 35 | 3 | 2.6559 | 250 | CHP26 | 20 | 20 | 0 | N/A | 0.45 | 0.43287 | 1600 | CHP9 | 10 | 5 | 2.5 | 35 | 3 | 2.746 | 400 | CHP26 | 20 | 20 | 0 | N/A | 0.45 | #N/A | 2600 |  | CHP9 | 10 | 5 | 2.5 | 35 | 3 | 2.6633 | 100 | CHP26 | 20 | 20 | 0 | N/A | 0.45 | 0.42589 | 800
CHP9 | 10 | 5 | 2.5 | 40 | 1.6 | 1.373 | 400 | CHP27 | 20 | 20 | 5 | N/A | 0.45 | 0.4301 | 1500 | CHP9 | 10 | 5 | 2.5 | 40 | 1.6 | 1.5613 | 600 | CHP27 | 20 | 20 | 5 | N/A | 0.45 | #N/A | 2400 |  | CHP9 | 10 | 5 | 2.5 | 40 | 1.6 | 1.3094 | 200 | CHP27 | 20 | 20 | 5 | N/A | 0.45 | 0.44502 | 700
CHP10 | 10 | 10 | 0 | 30 | 6 | 5.4518 | 150 | CHP28 | 20 | 20 | 10 | N/A | 0.45 | 0.44133 | 1400 | CHP10 | 10 | 10 | 0 | 30 | 6 | 5.4535 | 250 | CHP28 | 20 | 20 | 10 | N/A | 0.45 | #N/A | 2400 |  | CHP10 | 10 | 10 | 0 | 30 | 6 | 3.0383 | 50 | CHP28 | 20 | 20 | 10 | N/A | 0.45 | 0.43032 | 650
CHP10 | 10 | 10 | 0 | 35 | 3 | 2.7268 | 250 | CHP29 | 25 | 5 | 0 | N/A | 0.45 | 0.42553 | 1900 | CHP10 | 10 | 10 | 0 | 35 | 3 | 2.707 | 400 | CHP29 | 25 | 5 | 0 | N/A | 0.45 | #N/A | 3100 |  | CHP10 | 10 | 10 | 0 | 35 | 3 | 2.9407 | 100 | CHP29 | 25 | 5 | 0 | N/A | 0.45 | 0.4223 | 900
CHP10 | 10 | 10 | 0 | 40 | 1.6 | 1.3535 | 400 | CHP30 | 25 | 5 | 2.5 | N/A | 0.45 | 0.42573 | 1900 | CHP10 | 10 | 10 | 0 | 40 | 1.6 | 1.5048 | 600 | CHP30 | 25 | 5 | 2.5 | N/A | 0.45 | #N/A | 3100 |  | CHP10 | 10 | 10 | 0 | 40 | 1.6 | 1.3828 | 200 | CHP30 | 25 | 5 | 2.5 | N/A | 0.45 | 0.422 | 900
CHP11 | 10 | 10 | 5 | 30 | 6 | 2.6238 | 0 | CHP31 | 25 | 10 | 0 | N/A | 0.45 | 0.42758 | 1800 | CHP11 | 10 | 10 | 5 | 30 | 6 | 5.7931 | 200 | CHP31 | 25 | 10 | 0 | N/A | 0.45 | #N/A | 3000 |  | CHP11 | 10 | 10 | 5 | 30 | 6 | 0.96666 | 0 | CHP31 | 25 | 10 | 0 | N/A | 0.45 | 0.42443 | 850
CHP11 | 10 | 10 | 5 | 35 | 3 | 2.8966 | 200 | CHP32 | 25 | 10 | 5 | N/A | 0.45 | 0.42906 | 1800 | CHP11 | 10 | 10 | 5 | 35 | 3 | 2.9431 | 350 | CHP32 | 25 | 10 | 5 | N/A | 0.45 | #N/A | 3000 |  | CHP11 | 10 | 10 | 5 | 35 | 3 | 0.96666 | 0 | CHP32 | 25 | 10 | 5 | N/A | 0.45 | 0.41646 | 850
CHP11 | 10 | 10 | 5 | 40 | 1.6 | 1.4715 | 350 | CHP33 | 25 | 20 | 0 | N/A | 0.45 | 0.43026 | 1800 | CHP11 | 10 | 10 | 5 | 40 | 1.6 | 1.5842 | 550 | CHP33 | 25 | 20 | 0 | N/A | 0.45 | #N/A | 2900 |  | CHP11 | 10 | 10 | 5 | 40 | 1.6 | 1.3754 | 150 | CHP33 | 25 | 20 | 0 | N/A | 0.45 | 0.41691 | 900
CHP12 | 10 | 20 | 0 | 30 | 6 | 5.3609 | 50 | CHP34 | 25 | 20 | 5 | N/A | 0.45 | 0.42084 | 1700 | CHP12 | 10 | 20 | 0 | 30 | 6 | 5.3316 | 250 | CHP34 | 25 | 20 | 5 | N/A | 0.45 | #N/A | 2700 |  | CHP12 | 10 | 20 | 0 | 30 | 6 | 1.9751 | 50 | CHP34 | 25 | 20 | 5 | N/A | 0.45 | 0.42092 | 800
CHP12 | 10 | 20 | 0 | 35 | 3 | 2.6658 | 250 | CHP35 | 25 | 20 | 10 | N/A | 0.45 | 0.43468 | 1600 | CHP12 | 10 | 20 | 0 | 35 | 3 | 2.6944 | 400 | CHP35 | 25 | 20 | 10 | N/A | 0.45 | #N/A | 2700 |  | CHP12 | 10 | 20 | 0 | 35 | 3 | 1.9751 | 50 | CHP35 | 25 | 20 | 10 | N/A | 0.45 | 0.44861 | 700
CHP12 | 10 | 20 | 0 | 40 | 1.6 | 1.3472 | 400 | CHP36 | 1 | 5 | 0 | N/A | 0.45 | 0.37705 | 400 | CHP12 | 10 | 20 | 0 | 40 | 1.6 | 1.497 | 600 | CHP36 | 1 | 5 | 0 | N/A | 0.45 | 0.39859 | 600 |  | CHP12 | 10 | 20 | 0 | 40 | 1.6 | 1.3312 | 200 | CHP36 | 1 | 5 | 0 | N/A | 0.45 | 0.40656 | 200
CHP13 | 10 | 20 | 5 | 30 | 6 | 1.1084 | 0 | CHP37 | 1 | 5 | 2.5 | N/A | 0.45 | 0.37459 | 400 | CHP13 | 10 | 20 | 5 | 30 | 6 | 5.9807 | 200 | CHP37 | 1 | 5 | 2.5 | N/A | 0.45 | 0.40068 | 600 |  | CHP13 | 10 | 20 | 5 | 30 | 6 | 0.40836 | 0 | CHP37 | 1 | 5 | 2.5 | N/A | 0.45 | 0.38713 | 200
CHP13 | 10 | 20 | 5 | 35 | 3 | 2.9903 | 200 | CHP38 | 1 | 10 | 0 | N/A | 0.45 | 0.43926 | 350 | CHP13 | 10 | 20 | 5 | 35 | 3 | 2.9121 | 350 | CHP38 | 1 | 10 | 0 | N/A | 0.45 | 0.43045 | 550 |  | CHP13 | 10 | 20 | 5 | 35 | 3 | 0.40836 | 0 | CHP38 | 1 | 10 | 0 | N/A | 0.45 | 0.38368 | 200
CHP13 | 10 | 20 | 5 | 40 | 1.6 | 1.4561 | 350 | CHP39 | 1 | 10 | 5 | N/A | 0.45 | 0.39438 | 400 | CHP13 | 10 | 20 | 5 | 40 | 1.6 | 1.541 | 550 | CHP39 | 1 | 10 | 5 | N/A | 0.45 | 0.42898 | 600 |  | CHP13 | 10 | 20 | 5 | 40 | 1.6 | 0.40836 | 0 | CHP39 | 1 | 10 | 5 | N/A | 0.45 | 0.39051 | 200
CHP14 | 10 | 20 | 10 | 30 | 6 | 0.1101 | 0 | CHP40 | 1 | 20 | 0 | N/A | 0.45 | 0.36425 | 350 | CHP14 | 10 | 20 | 10 | 30 | 6 | 0.2202 | 0 | CHP40 | 1 | 20 | 0 | N/A | 0.45 | 0.43321 | 500 |  | CHP14 | 10 | 20 | 10 | 30 | 6 | 0.040563 | 0 | CHP40 | 1 | 20 | 0 | N/A | 0.45 | 0.30984 | 200
CHP14 | 10 | 20 | 10 | 35 | 3 | 0.1101 | 0 | CHP41 | 1 | 20 | 5 | N/A | 0.45 | 0.43288 | 300 | CHP14 | 10 | 20 | 10 | 35 | 3 | 2.7488 | 300 | CHP41 | 1 | 20 | 5 | N/A | 0.45 | 0.41074 | 500 |  | CHP14 | 10 | 20 | 10 | 35 | 3 | 0.040563 | 0 | CHP41 | 1 | 20 | 5 | N/A | 0.45 | 0.41921 | 150
CHP14 | 10 | 20 | 10 | 40 | 1.6 | 1.3744 | 300 | CHP42 | 1 | 20 | 10 | N/A | 0.45 | 0.37309 | 350 | CHP14 | 10 | 20 | 10 | 40 | 1.6 | 1.4714 | 500 | CHP42 | 1 | 20 | 10 | N/A | 0.45 | 0.44793 | 500 |  | CHP14 | 10 | 20 | 10 | 40 | 1.6 | 0.040563 | 0 | CHP42 | 1 | 20 | 10 | N/A | 0.45 | 0.061741 | 0
CHP15 | 15 | 5 | 0 | 30 | 6 | 4.5261 | 200 | CHP43 | 2.5 | 5 | 0 | N/A | 0.45 | 0.41321 | 600 | CHP15 | 15 | 5 | 0 | 30 | 6 | 5.3178 | 300 | CHP43 | 2.5 | 5 | 0 | N/A | 0.45 | 0.44438 | 900 |  | CHP15 | 15 | 5 | 0 | 30 | 6 | 4.4784 | 50 | CHP43 | 2.5 | 5 | 0 | N/A | 0.45 | 0.42727 | 300
CHP15 | 15 | 5 | 0 | 35 | 3 | 2.6589 | 300 | CHP44 | 2.5 | 5 | 2.5 | N/A | 0.45 | 0.41562 | 600 | CHP15 | 15 | 5 | 0 | 35 | 3 | 2.5897 | 500 | CHP44 | 2.5 | 5 | 2.5 | N/A | 0.45 | 0.44927 | 900 |  | CHP15 | 15 | 5 | 0 | 35 | 3 | 2.3192 | 150 | CHP44 | 2.5 | 5 | 2.5 | N/A | 0.45 | 0.42241 | 300
CHP15 | 15 | 5 | 0 | 40 | 1.6 | 1.5013 | 450 | CHP45 | 2.5 | 10 | 0 | N/A | 0.45 | 0.40329 | 600 | CHP15 | 15 | 5 | 0 | 40 | 1.6 | 1.4955 | 750 | CHP45 | 2.5 | 10 | 0 | N/A | 0.45 | 0.42761 | 900 |  | CHP15 | 15 | 5 | 0 | 40 | 1.6 | 1.2537 | 250 | CHP45 | 2.5 | 10 | 0 | N/A | 0.45 | 0.42545 | 300
CHP16 | 15 | 5 | 2.5 | 30 | 6 | 4.4251 | 200 | CHP46 | 2.5 | 10 | 5 | N/A | 0.45 | 0.42495 | 650 | CHP16 | 15 | 5 | 2.5 | 30 | 6 | 5.282 | 300 | CHP46 | 2.5 | 10 | 5 | N/A | 0.45 | 0.44421 | 1000 |  | CHP16 | 15 | 5 | 2.5 | 30 | 6 | 3.4249 | 50 | CHP46 | 2.5 | 10 | 5 | N/A | 0.45 | 0.38896 | 350
CHP16 | 15 | 5 | 2.5 | 35 | 3 | 2.641 | 300 | CHP47 | 2.5 | 20 | 0 | N/A | 0.45 | 0.39953 | 550 | CHP16 | 15 | 5 | 2.5 | 35 | 3 | 2.5887 | 500 | CHP47 | 2.5 | 20 | 0 | N/A | 0.45 | 0.41499 | 850 |  | CHP16 | 15 | 5 | 2.5 | 35 | 3 | 2.2239 | 150 | CHP47 | 2.5 | 20 | 0 | N/A | 0.45 | 0.36568 | 300
CHP16 | 15 | 5 | 2.5 | 40 | 1.6 | 1.5002 | 450 | CHP48 | 2.5 | 20 | 5 | N/A | 0.45 | 0.44422 | 500 | CHP16 | 15 | 5 | 2.5 | 40 | 1.6 | 1.4946 | 750 | CHP48 | 2.5 | 20 | 5 | N/A | 0.45 | 0.44305 | 800 |  | CHP16 | 15 | 5 | 2.5 | 40 | 1.6 | 1.2383 | 250 | CHP48 | 2.5 | 20 | 5 | N/A | 0.45 | 0.44263 | 250
CHP17 | 15 | 10 | 0 | 30 | 6 | 4.6134 | 200 | CHP49 | 2.5 | 20 | 10 | N/A | 0.45 | 0.44116 | 550 | CHP17 | 15 | 10 | 0 | 30 | 6 | 5.2693 | 300 | CHP49 | 2.5 | 20 | 10 | N/A | 0.45 | 0.42484 | 900 |  | CHP17 | 15 | 10 | 0 | 30 | 6 | 3.1803 | 50 | CHP49 | 2.5 | 20 | 10 | N/A | 0.45 | 0.37455 | 300
CHP17 | 15 | 10 | 0 | 35 | 3 | 2.6346 | 300 | CHP50 | 1.5 | 5 | 0 | N/A | 0.45 | 0.3984 | 500 | CHP17 | 15 | 10 | 0 | 35 | 3 | 2.9065 | 450 | CHP50 | 1.5 | 5 | 0 | N/A | 0.45 | 0.4207 | 750 |  | CHP17 | 15 | 10 | 0 | 35 | 3 | 2.4022 | 150 | CHP50 | 1.5 | 5 | 0 | N/A | 0.45 | 0.43154 | 250
CHP17 | 15 | 10 | 0 | 40 | 1.6 | 1.4532 | 450 | CHP51 | 1.5 | 5 | 2.5 | N/A | 0.45 | 0.39873 | 500 | CHP17 | 15 | 10 | 0 | 40 | 1.6 | 1.5491 | 700 | CHP51 | 1.5 | 5 | 2.5 | N/A | 0.45 | 0.42451 | 750 |  | CHP17 | 15 | 10 | 0 | 40 | 1.6 | 1.2576 | 250 | CHP51 | 1.5 | 5 | 2.5 | N/A | 0.45 | 0.41761 | 250
CHP18 | 15 | 10 | 5 | 30 | 6 | 2.5486 | 50 | CHP52 | 1.5 | 10 | 0 | N/A | 0.45 | 0.44301 | 450 | CHP18 | 15 | 10 | 5 | 30 | 6 | 5.6895 | 250 | CHP52 | 1.5 | 10 | 0 | N/A | 0.45 | 0.44202 | 700 |  | CHP18 | 15 | 10 | 5 | 30 | 6 | 0.93897 | 50 | CHP52 | 1.5 | 10 | 0 | N/A | 0.45 | 0.40809 | 250
CHP18 | 15 | 10 | 5 | 35 | 3 | 2.8448 | 250 | CHP53 | 1.5 | 10 | 5 | N/A | 0.45 | 0.42301 | 500 | CHP18 | 15 | 10 | 5 | 35 | 3 | 2.7076 | 450 | CHP53 | 1.5 | 10 | 5 | N/A | 0.45 | 0.42003 | 800 |  | CHP18 | 15 | 10 | 5 | 35 | 3 | 0.93897 | 50 | CHP53 | 1.5 | 10 | 5 | N/A | 0.45 | 0.43203 | 250
CHP18 | 15 | 10 | 5 | 40 | 1.6 | 1.5874 | 400 | CHP54 | 1.5 | 20 | 0 | N/A | 0.45 | 0.44828 | 400 | CHP18 | 15 | 10 | 5 | 40 | 1.6 | 1.49 | 700 | CHP54 | 1.5 | 20 | 0 | N/A | 0.45 | 0.44144 | 650 |  | CHP18 | 15 | 10 | 5 | 40 | 1.6 | 1.3159 | 200 | CHP54 | 1.5 | 20 | 0 | N/A | 0.45 | 0.33186 | 250
CHP19 | 15 | 20 | 0 | 30 | 6 | 5.7812 | 0 | CHP55 | 1.5 | 20 | 5 | N/A | 0.45 | 0.42752 | 400 | CHP19 | 15 | 20 | 0 | 30 | 6 | 5.4071 | 300 | CHP55 | 1.5 | 20 | 5 | N/A | 0.45 | 0.4168 | 650 |  | CHP19 | 15 | 20 | 0 | 30 | 6 | 2.1299 | 0 | CHP55 | 1.5 | 20 | 5 | N/A | 0.45 | 0.4306 | 200
CHP19 | 15 | 20 | 0 | 35 | 3 | 2.7036 | 300 | CHP56 | 1.5 | 20 | 10 | N/A | 0.45 | 0.39176 | 450 | CHP19 | 15 | 20 | 0 | 35 | 3 | 2.5838 | 500 | CHP56 | 1.5 | 20 | 10 | N/A | 0.45 | 0.40947 | 700 |  | CHP19 | 15 | 20 | 0 | 35 | 3 | 2.1299 | 0 | CHP56 | 1.5 | 20 | 10 | N/A | 0.45 | 0.42428 | 200
CHP19 | 15 | 20 | 0 | 40 | 1.6 | 1.5032 | 450 | CHP57 | 2 | 5 | 0 | N/A | 0.45 | 0.43533 | 500 | CHP19 | 15 | 20 | 0 | 40 | 1.6 | 1.4563 | 750 | CHP57 | 2 | 5 | 0 | N/A | 0.45 | 0.42609 | 800 |  | CHP19 | 15 | 20 | 0 | 40 | 1.6 | 1.2855 | 250 | CHP57 | 2 | 5 | 0 | N/A | 0.45 | 0.44949 | 250
CHP20 | 15 | 20 | 5 | 30 | 6 | 1.1047 | 0 | CHP58 | 2 | 5 | 2.5 | N/A | 0.45 | 0.43643 | 500 | CHP20 | 15 | 20 | 5 | 30 | 6 | 5.8314 | 250 | CHP58 | 2 | 5 | 2.5 | N/A | 0.45 | 0.43023 | 800 |  | CHP20 | 15 | 20 | 5 | 30 | 6 | 0.40698 | 0 | CHP58 | 2 | 5 | 2.5 | N/A | 0.45 | 0.44096 | 250
CHP20 | 15 | 20 | 5 | 35 | 3 | 2.9157 | 250 | CHP59 | 2 | 10 | 0 | N/A | 0.45 | 0.42836 | 500 | CHP20 | 15 | 20 | 5 | 35 | 3 | 2.6545 | 450 | CHP59 | 2 | 10 | 0 | N/A | 0.45 | 0.4114 | 800 |  | CHP20 | 15 | 20 | 5 | 35 | 3 | 0.40698 | 0 | CHP59 | 2 | 10 | 0 | N/A | 0.45 | 0.44767 | 250
CHP20 | 15 | 20 | 5 | 40 | 1.6 | 1.5672 | 400 | CHP60 | 2 | 10 | 5 | N/A | 0.45 | 0.43558 | 550 | CHP20 | 15 | 20 | 5 | 40 | 1.6 | 1.5843 | 650 | CHP60 | 2 | 10 | 5 | N/A | 0.45 | 0.41643 | 900 |  | CHP20 | 15 | 20 | 5 | 40 | 1.6 | 1.3701 | 200 | CHP60 | 2 | 10 | 5 | N/A | 0.45 | 0.38511 | 300
CHP21 | 15 | 20 | 10 | 30 | 6 | 0.098661 | 0 | CHP61 | 2 | 20 | 0 | N/A | 0.45 | 0.43335 | 450 | CHP21 | 15 | 20 | 10 | 30 | 6 | 0.19732 | 0 | CHP61 | 2 | 20 | 0 | N/A | 0.45 | 0.44354 | 700 |  | CHP21 | 15 | 20 | 10 | 30 | 6 | 0.036349 | 0 | CHP61 | 2 | 20 | 0 | N/A | 0.45 | 0.38458 | 250
CHP21 | 15 | 20 | 10 | 35 | 3 | 0.098661 | 0 | CHP62 | 2 | 20 | 5 | N/A | 0.45 | 0.41313 | 450 | CHP21 | 15 | 20 | 10 | 35 | 3 | 2.9272 | 350 | CHP62 | 2 | 20 | 5 | N/A | 0.45 | 0.43364 | 700 |  | CHP21 | 15 | 20 | 10 | 35 | 3 | 0.036349 | 0 | CHP62 | 2 | 20 | 5 | N/A | 0.45 | 0.3541 | 250
CHP21 | 15 | 20 | 10 | 40 | 1.6 | 1.4636 | 350 | CHP63 | 2 | 20 | 10 | N/A | 0.45 | 0.40554 | 500 | CHP21 | 15 | 20 | 10 | 40 | 1.6 | 1.5101 | 600 | CHP63 | 2 | 20 | 10 | N/A | 0.45 | 0.4457 | 750 |  | CHP21 | 15 | 20 | 10 | 40 | 1.6 | 0.036349 | 0 | CHP63 | 2 | 20 | 10 | N/A | 0.45 | 0.37516 | 250
CHP22 | 20 | 5 | 0 | 30 | 6 | 5.2093 | 200 | [8 empty] | CHP22 | 20 | 5 | 0 | 30 | 6 | 5.08 | 350 | [9 empty] | CHP22 | 20 | 5 | 0 | 30 | 6 | 4.4581 | 50
CHP22 | 20 | 5 | 0 | 35 | 3 | 2.54 | 350 | [8 empty] | CHP22 | 20 | 5 | 0 | 35 | 3 | 2.7019 | 550 | [9 empty] | CHP22 | 20 | 5 | 0 | 35 | 3 | 2.6089 | 150
CHP22 | 20 | 5 | 0 | 40 | 1.6 | 1.5421 | 500 | [8 empty] | CHP22 | 20 | 5 | 0 | 40 | 1.6 | 1.5145 | 850 | [9 empty] | CHP22 | 20 | 5 | 0 | 40 | 1.6 | 1.4637 | 250
CHP23 | 20 | 5 | 2.5 | 30 | 6 | 5.1041 | 200 | [8 empty] | CHP23 | 20 | 5 | 2.5 | 30 | 6 | 5.066 | 350 | [9 empty] | CHP23 | 20 | 5 | 2.5 | 30 | 6 | 3.4598 | 50
CHP23 | 20 | 5 | 2.5 | 35 | 3 | 2.533 | 350 | [8 empty] | CHP23 | 20 | 5 | 2.5 | 35 | 3 | 2.7031 | 550 | [9 empty] | CHP23 | 20 | 5 | 2.5 | 35 | 3 | 2.512 | 150
CHP23 | 20 | 5 | 2.5 | 40 | 1.6 | 1.5428 | 500 | [8 empty] | CHP23 | 20 | 5 | 2.5 | 40 | 1.6 | 1.5135 | 850 | [9 empty] | CHP23 | 20 | 5 | 2.5 | 40 | 1.6 | 1.4473 | 250
CHP24 | 20 | 10 | 0 | 30 | 6 | 5.2383 | 200 | [8 empty] | CHP24 | 20 | 10 | 0 | 30 | 6 | 4.9405 | 350 | [9 empty] | CHP24 | 20 | 10 | 0 | 30 | 6 | 3.2415 | 50
CHP24 | 20 | 10 | 0 | 35 | 3 | 2.4703 | 350 | [8 empty] | CHP24 | 20 | 10 | 0 | 35 | 3 | 2.952 | 500 | [9 empty] | CHP24 | 20 | 10 | 0 | 35 | 3 | 2.6716 | 150
CHP24 | 20 | 10 | 0 | 40 | 1.6 | 1.476 | 500 | [8 empty] | CHP24 | 20 | 10 | 0 | 40 | 1.6 | 1.5357 | 800 | [9 empty] | CHP24 | 20 | 10 | 0 | 40 | 1.6 | 1.4509 | 250
CHP25 | 20 | 10 | 5 | 30 | 6 | 2.4674 | 50 | [8 empty] | CHP25 | 20 | 10 | 5 | 30 | 6 | 5.406 | 300 | [9 empty] | CHP25 | 20 | 10 | 5 | 30 | 6 | 0.90903 | 50
CHP25 | 20 | 10 | 5 | 35 | 3 | 2.703 | 300 | [8 empty] | CHP25 | 20 | 10 | 5 | 35 | 3 | 2.804 | 500 | [9 empty] | CHP25 | 20 | 10 | 5 | 35 | 3 | 0.90903 | 50
CHP25 | 20 | 10 | 5 | 40 | 1.6 | 1.402 | 500 | [8 empty] | CHP25 | 20 | 10 | 5 | 40 | 1.6 | 1.4976 | 800 | [9 empty] | CHP25 | 20 | 10 | 5 | 40 | 1.6 | 1.5063 | 200
CHP26 | 20 | 20 | 0 | 30 | 6 | 5.5172 | 200 | [8 empty] | CHP26 | 20 | 20 | 0 | 30 | 6 | 5.2147 | 350 | [9 empty] | CHP26 | 20 | 20 | 0 | 30 | 6 | 2.2136 | 0
CHP26 | 20 | 20 | 0 | 35 | 3 | 2.6074 | 350 | [8 empty] | CHP26 | 20 | 20 | 0 | 35 | 3 | 2.7222 | 550 | [9 empty] | CHP26 | 20 | 20 | 0 | 35 | 3 | 2.2136 | 0
CHP26 | 20 | 20 | 0 | 40 | 1.6 | 1.5591 | 500 | [8 empty] | CHP26 | 20 | 20 | 0 | 40 | 1.6 | 1.4881 | 850 | [9 empty] | CHP26 | 20 | 20 | 0 | 40 | 1.6 | 1.5345 | 250
CHP27 | 20 | 20 | 5 | 30 | 6 | 1.0906 | 0 | [8 empty] | CHP27 | 20 | 20 | 5 | 30 | 6 | 5.4413 | 300 | [9 empty] | CHP27 | 20 | 20 | 5 | 30 | 6 | 0.40182 | 0
CHP27 | 20 | 20 | 5 | 35 | 3 | 2.7207 | 300 | [8 empty] | CHP27 | 20 | 20 | 5 | 35 | 3 | 2.7201 | 500 | [9 empty] | CHP27 | 20 | 20 | 5 | 35 | 3 | 0.40182 | 0
CHP27 | 20 | 20 | 5 | 40 | 1.6 | 1.5778 | 450 | [8 empty] | CHP27 | 20 | 20 | 5 | 40 | 1.6 | 1.5375 | 750 | [9 empty] | CHP27 | 20 | 20 | 5 | 40 | 1.6 | 1.5605 | 200
CHP28 | 20 | 20 | 10 | 30 | 6 | 0.090684 | 0 | [8 empty] | CHP28 | 20 | 20 | 10 | 30 | 6 | 0.18137 | 0 | [9 empty] | CHP28 | 20 | 20 | 10 | 30 | 6 | 0.03341 | 0
CHP28 | 20 | 20 | 10 | 35 | 3 | 0.090684 | 0 | [8 empty] | CHP28 | 20 | 20 | 10 | 35 | 3 | 2.971 | 400 | [9 empty] | CHP28 | 20 | 20 | 10 | 35 | 3 | 0.03341 | 0
CHP28 | 20 | 20 | 10 | 40 | 1.6 | 1.4855 | 400 | [8 empty] | CHP28 | 20 | 20 | 10 | 40 | 1.6 | 1.4849 | 700 | [9 empty] | CHP28 | 20 | 20 | 10 | 40 | 1.6 | 0.03341 | 0
CHP29 | 25 | 5 | 0 | 30 | 6 | 5.751 | 200 | [8 empty] | CHP29 | 25 | 5 | 0 | 30 | 6 | 5.7526 | 350 | [9 empty] | CHP29 | 25 | 5 | 0 | 30 | 6 | 4.3781 | 50
CHP29 | 25 | 5 | 0 | 35 | 3 | 2.8763 | 350 | [8 empty] | CHP29 | 25 | 5 | 0 | 35 | 3 | 2.7308 | 600 | [9 empty] | CHP29 | 25 | 5 | 0 | 35 | 3 | 2.826 | 150
CHP29 | 25 | 5 | 0 | 40 | 1.6 | 1.539 | 550 | [8 empty] | CHP29 | 25 | 5 | 0 | 40 | 1.6 | 1.4981 | 950 | [9 empty] | CHP29 | 25 | 5 | 0 | 40 | 1.6 | 1.3 | 300
CHP30 | 25 | 5 | 2.5 | 30 | 6 | 5.6437 | 200 | [8 empty] | CHP30 | 25 | 5 | 2.5 | 30 | 6 | 5.7389 | 350 | [9 empty] | CHP30 | 25 | 5 | 2.5 | 30 | 6 | 3.4441 | 50
CHP30 | 25 | 5 | 2.5 | 35 | 3 | 2.8694 | 350 | [8 empty] | CHP30 | 25 | 5 | 2.5 | 35 | 3 | 2.7334 | 600 | [9 empty] | CHP30 | 25 | 5 | 2.5 | 35 | 3 | 2.7291 | 150
CHP30 | 25 | 5 | 2.5 | 40 | 1.6 | 1.5408 | 550 | [8 empty] | CHP30 | 25 | 5 | 2.5 | 40 | 1.6 | 1.497 | 950 | [9 empty] | CHP30 | 25 | 5 | 2.5 | 40 | 1.6 | 1.2929 | 300
CHP31 | 25 | 10 | 0 | 30 | 6 | 5.7381 | 200 | [8 empty] | CHP31 | 25 | 10 | 0 | 30 | 6 | 5.5534 | 350 | [9 empty] | CHP31 | 25 | 10 | 0 | 30 | 6 | 3.2553 | 50
CHP31 | 25 | 10 | 0 | 35 | 3 | 2.7767 | 350 | [8 empty] | CHP31 | 25 | 10 | 0 | 35 | 3 | 2.9252 | 550 | [9 empty] | CHP31 | 25 | 10 | 0 | 35 | 3 | 2.8625 | 150
CHP31 | 25 | 10 | 0 | 40 | 1.6 | 1.4626 | 550 | [8 empty] | CHP31 | 25 | 10 | 0 | 40 | 1.6 | 1.4974 | 900 | [9 empty] | CHP31 | 25 | 10 | 0 | 40 | 1.6 | 1.2639 | 300
CHP32 | 25 | 10 | 5 | 30 | 6 | 2.3864 | 50 | [8 empty] | CHP32 | 25 | 10 | 5 | 30 | 6 | 5.0704 | 350 | [9 empty] | CHP32 | 25 | 10 | 5 | 30 | 6 | 0.87921 | 50
CHP32 | 25 | 10 | 5 | 35 | 3 | 2.5352 | 350 | [8 empty] | CHP32 | 25 | 10 | 5 | 35 | 3 | 2.8156 | 550 | [9 empty] | CHP32 | 25 | 10 | 5 | 35 | 3 | 0.87921 | 50
CHP32 | 25 | 10 | 5 | 40 | 1.6 | 1.4078 | 550 | [8 empty] | CHP32 | 25 | 10 | 5 | 40 | 1.6 | 1.5825 | 850 | [9 empty] | CHP32 | 25 | 10 | 5 | 40 | 1.6 | 1.3582 | 250
CHP33 | 25 | 20 | 0 | 30 | 6 | 4.7295 | 250 | [8 empty] | CHP33 | 25 | 20 | 0 | 30 | 6 | 5.977 | 350 | [9 empty] | CHP33 | 25 | 20 | 0 | 30 | 6 | 2.2545 | 0
CHP33 | 25 | 20 | 0 | 35 | 3 | 2.9885 | 350 | [8 empty] | CHP33 | 25 | 20 | 0 | 35 | 3 | 2.7618 | 600 | [9 empty] | CHP33 | 25 | 20 | 0 | 35 | 3 | 2.2545 | 0
CHP33 | 25 | 20 | 0 | 40 | 1.6 | 1.5627 | 550 | [8 empty] | CHP33 | 25 | 20 | 0 | 40 | 1.6 | 1.5842 | 900 | [9 empty] | CHP33 | 25 | 20 | 0 | 40 | 1.6 | 1.3656 | 300
CHP34 | 25 | 20 | 5 | 30 | 6 | 1.0705 | 0 | [8 empty] | CHP34 | 25 | 20 | 5 | 30 | 6 | 4.992 | 350 | [9 empty] | CHP34 | 25 | 20 | 5 | 30 | 6 | 0.3944 | 0
CHP34 | 25 | 20 | 5 | 35 | 3 | 2.496 | 350 | [8 empty] | CHP34 | 25 | 20 | 5 | 35 | 3 | 2.6959 | 550 | [9 empty] | CHP34 | 25 | 20 | 5 | 35 | 3 | 0.3944 | 0
CHP34 | 25 | 20 | 5 | 40 | 1.6 | 1.5403 | 500 | [8 empty] | CHP34 | 25 | 20 | 5 | 40 | 1.6 | 1.5995 | 800 | [9 empty] | CHP34 | 25 | 20 | 5 | 40 | 1.6 | 1.3771 | 250
CHP35 | 25 | 20 | 10 | 30 | 6 | 0.084562 | 0 | [8 empty] | CHP35 | 25 | 20 | 10 | 30 | 6 | 0.16912 | 0 | [9 empty] | CHP35 | 25 | 20 | 10 | 30 | 6 | 0.031154 | 0
CHP35 | 25 | 20 | 10 | 35 | 3 | 0.084562 | 0 | [8 empty] | CHP35 | 25 | 20 | 10 | 35 | 3 | 2.9431 | 450 | [9 empty] | CHP35 | 25 | 20 | 10 | 35 | 3 | 0.031154 | 0
CHP35 | 25 | 20 | 10 | 40 | 1.6 | 1.4715 | 450 | [8 empty] | CHP35 | 25 | 20 | 10 | 40 | 1.6 | 1.5597 | 750 | [9 empty] | CHP35 | 25 | 20 | 10 | 40 | 1.6 | 0.031154 | 0
CHP36 | 1 | 5 | 0 | 30 | 6 | 5.4911 | 50 | [8 empty] | CHP36 | 1 | 5 | 0 | 30 | 6 | 4.4947 | 100 | [9 empty] | CHP36 | 1 | 5 | 0 | 30 | 6 | 2.023 | 50
CHP36 | 1 | 5 | 0 | 35 | 3 | 2.2474 | 100 | [8 empty] | CHP36 | 1 | 5 | 0 | 35 | 3 | 2.4219 | 150 | [9 empty] | CHP36 | 1 | 5 | 0 | 35 | 3 | 2.023 | 50
CHP36 | 1 | 5 | 0 | 40 | 1.6 | 1.2109 | 150 | [8 empty] | CHP36 | 1 | 5 | 0 | 40 | 1.6 | 1.5449 | 200 | [9 empty] | CHP36 | 1 | 5 | 0 | 40 | 1.6 | 0.82798 | 100
CHP37 | 1 | 5 | 2.5 | 30 | 6 | 3.9101 | 50 | [8 empty] | CHP37 | 1 | 5 | 2.5 | 30 | 6 | 3.8962 | 100 | [9 empty] | CHP37 | 1 | 5 | 2.5 | 30 | 6 | 1.4405 | 50
CHP37 | 1 | 5 | 2.5 | 35 | 3 | 1.9481 | 100 | [8 empty] | CHP37 | 1 | 5 | 2.5 | 35 | 3 | 2.2406 | 150 | [9 empty] | CHP37 | 1 | 5 | 2.5 | 35 | 3 | 1.4405 | 50
CHP37 | 1 | 5 | 2.5 | 40 | 1.6 | 1.1203 | 150 | [8 empty] | CHP37 | 1 | 5 | 2.5 | 40 | 1.6 | 1.4711 | 200 | [9 empty] | CHP37 | 1 | 5 | 2.5 | 40 | 1.6 | 1.4405 | 50
CHP38 | 1 | 10 | 0 | 30 | 6 | 3.483 | 50 | [8 empty] | CHP38 | 1 | 10 | 0 | 30 | 6 | 4.0905 | 100 | [9 empty] | CHP38 | 1 | 10 | 0 | 30 | 6 | 1.2832 | 50
CHP38 | 1 | 10 | 0 | 35 | 3 | 2.0453 | 100 | [8 empty] | CHP38 | 1 | 10 | 0 | 35 | 3 | 2.2742 | 150 | [9 empty] | CHP38 | 1 | 10 | 0 | 35 | 3 | 1.2832 | 50
CHP38 | 1 | 10 | 0 | 40 | 1.6 | 1.1371 | 150 | [8 empty] | CHP38 | 1 | 10 | 0 | 40 | 1.6 | 1.458 | 200 | [9 empty] | CHP38 | 1 | 10 | 0 | 40 | 1.6 | 1.2832 | 50
CHP39 | 1 | 10 | 5 | 30 | 6 | 1.899 | 0 | [8 empty] | CHP39 | 1 | 10 | 5 | 30 | 6 | 3.798 | 0 | [9 empty] | CHP39 | 1 | 10 | 5 | 30 | 6 | 0.69964 | 0
CHP39 | 1 | 10 | 5 | 35 | 3 | 1.899 | 0 | [8 empty] | CHP39 | 1 | 10 | 5 | 35 | 3 | 2.1481 | 150 | [9 empty] | CHP39 | 1 | 10 | 5 | 35 | 3 | 0.69964 | 0
CHP39 | 1 | 10 | 5 | 40 | 1.6 | 1.0741 | 150 | [8 empty] | CHP39 | 1 | 10 | 5 | 40 | 1.6 | 1.4839 | 200 | [9 empty] | CHP39 | 1 | 10 | 5 | 40 | 1.6 | 0.69964 | 0
CHP40 | 1 | 20 | 0 | 30 | 6 | 1.914 | 50 | [8 empty] | CHP40 | 1 | 20 | 0 | 30 | 6 | 3.828 | 50 | [9 empty] | CHP40 | 1 | 20 | 0 | 30 | 6 | 0.70516 | 50
CHP40 | 1 | 20 | 0 | 35 | 3 | 1.914 | 50 | [8 empty] | CHP40 | 1 | 20 | 0 | 35 | 3 | 2.5899 | 100 | [9 empty] | CHP40 | 1 | 20 | 0 | 35 | 3 | 0.70516 | 50
CHP40 | 1 | 20 | 0 | 40 | 1.6 | 1.295 | 100 | [8 empty] | CHP40 | 1 | 20 | 0 | 40 | 1.6 | 1.1774 | 200 | [9 empty] | CHP40 | 1 | 20 | 0 | 40 | 1.6 | 0.70516 | 50
CHP41 | 1 | 20 | 5 | 30 | 6 | 0.60894 | 0 | [8 empty] | CHP41 | 1 | 20 | 5 | 30 | 6 | 1.2179 | 0 | [9 empty] | CHP41 | 1 | 20 | 5 | 30 | 6 | 0.22435 | 0
CHP41 | 1 | 20 | 5 | 35 | 3 | 0.60894 | 0 | [8 empty] | CHP41 | 1 | 20 | 5 | 35 | 3 | 1.2179 | 0 | [9 empty] | CHP41 | 1 | 20 | 5 | 35 | 3 | 0.22435 | 0
CHP41 | 1 | 20 | 5 | 40 | 1.6 | 0.60894 | 0 | [8 empty] | CHP41 | 1 | 20 | 5 | 40 | 1.6 | 1.593 | 150 | [9 empty] | CHP41 | 1 | 20 | 5 | 40 | 1.6 | 0.22435 | 0
CHP42 | 1 | 20 | 10 | 30 | 6 | 0.11731 | 0 | [8 empty] | CHP42 | 1 | 20 | 10 | 30 | 6 | 0.23462 | 0 | [9 empty] | CHP42 | 1 | 20 | 10 | 30 | 6 | 0.043219 | 0
CHP42 | 1 | 20 | 10 | 35 | 3 | 0.11731 | 0 | [8 empty] | CHP42 | 1 | 20 | 10 | 35 | 3 | 0.23462 | 0 | [9 empty] | CHP42 | 1 | 20 | 10 | 35 | 3 | 0.043219 | 0
CHP42 | 1 | 20 | 10 | 40 | 1.6 | 0.11731 | 0 | [8 empty] | CHP42 | 1 | 20 | 10 | 40 | 1.6 | 0.23462 | 0 | [9 empty] | CHP42 | 1 | 20 | 10 | 40 | 1.6 | 0.043219 | 0
CHP43 | 2.5 | 5 | 0 | 30 | 6 | 4.0599 | 100 | [8 empty] | CHP43 | 2.5 | 5 | 0 | 30 | 6 | 4.6065 | 150 | [9 empty] | CHP43 | 2.5 | 5 | 0 | 30 | 6 | 3.1191 | 50
CHP43 | 2.5 | 5 | 0 | 35 | 3 | 2.3033 | 150 | [8 empty] | CHP43 | 2.5 | 5 | 0 | 35 | 3 | 2.9949 | 200 | [9 empty] | CHP43 | 2.5 | 5 | 0 | 35 | 3 | 1.4958 | 100
CHP43 | 2.5 | 5 | 0 | 40 | 1.6 | 1.4974 | 200 | [8 empty] | CHP43 | 2.5 | 5 | 0 | 40 | 1.6 | 1.2919 | 350 | [9 empty] | CHP43 | 2.5 | 5 | 0 | 40 | 1.6 | 1.4958 | 100
CHP44 | 2.5 | 5 | 2.5 | 30 | 6 | 3.5715 | 100 | [8 empty] | CHP44 | 2.5 | 5 | 2.5 | 30 | 6 | 4.33 | 150 | [9 empty] | CHP44 | 2.5 | 5 | 2.5 | 30 | 6 | 2.2461 | 50
CHP44 | 2.5 | 5 | 2.5 | 35 | 3 | 2.165 | 150 | [8 empty] | CHP44 | 2.5 | 5 | 2.5 | 35 | 3 | 2.8972 | 200 | [9 empty] | CHP44 | 2.5 | 5 | 2.5 | 35 | 3 | 2.2461 | 50
CHP44 | 2.5 | 5 | 2.5 | 40 | 1.6 | 1.4486 | 200 | [8 empty] | CHP44 | 2.5 | 5 | 2.5 | 40 | 1.6 | 1.2835 | 350 | [9 empty] | CHP44 | 2.5 | 5 | 2.5 | 40 | 1.6 | 1.3158 | 100
CHP45 | 2.5 | 10 | 0 | 30 | 6 | 5.5232 | 50 | [8 empty] | CHP45 | 2.5 | 10 | 0 | 30 | 6 | 4.5704 | 150 | [9 empty] | CHP45 | 2.5 | 10 | 0 | 30 | 6 | 2.0349 | 50
CHP45 | 2.5 | 10 | 0 | 35 | 3 | 2.2852 | 150 | [8 empty] | CHP45 | 2.5 | 10 | 0 | 35 | 3 | 2.9822 | 200 | [9 empty] | CHP45 | 2.5 | 10 | 0 | 35 | 3 | 2.0349 | 50
CHP45 | 2.5 | 10 | 0 | 40 | 1.6 | 1.4911 | 200 | [8 empty] | CHP45 | 2.5 | 10 | 0 | 40 | 1.6 | 1.2843 | 350 | [9 empty] | CHP45 | 2.5 | 10 | 0 | 40 | 1.6 | 1.4321 | 100
CHP46 | 2.5 | 10 | 5 | 30 | 6 | 2.5959 | 0 | [8 empty] | CHP46 | 2.5 | 10 | 5 | 30 | 6 | 5.1918 | 0 | [9 empty] | CHP46 | 2.5 | 10 | 5 | 30 | 6 | 0.95638 | 0
CHP46 | 2.5 | 10 | 5 | 35 | 3 | 2.5959 | 0 | [8 empty] | CHP46 | 2.5 | 10 | 5 | 35 | 3 | 2.3282 | 250 | [9 empty] | CHP46 | 2.5 | 10 | 5 | 35 | 3 | 0.95638 | 0
CHP46 | 2.5 | 10 | 5 | 40 | 1.6 | 1.5411 | 200 | [8 empty] | CHP46 | 2.5 | 10 | 5 | 40 | 1.6 | 1.4781 | 350 | [9 empty] | CHP46 | 2.5 | 10 | 5 | 40 | 1.6 | 0.95638 | 0
CHP47 | 2.5 | 20 | 0 | 30 | 6 | 3.2299 | 50 | [8 empty] | CHP47 | 2.5 | 20 | 0 | 30 | 6 | 4.9128 | 100 | [9 empty] | CHP47 | 2.5 | 20 | 0 | 30 | 6 | 1.19 | 50
CHP47 | 2.5 | 20 | 0 | 35 | 3 | 2.4564 | 100 | [8 empty] | CHP47 | 2.5 | 20 | 0 | 35 | 3 | 2.5455 | 200 | [9 empty] | CHP47 | 2.5 | 20 | 0 | 35 | 3 | 1.19 | 50
CHP47 | 2.5 | 20 | 0 | 40 | 1.6 | 1.2728 | 200 | [8 empty] | CHP47 | 2.5 | 20 | 0 | 40 | 1.6 | 1.3896 | 300 | [9 empty] | CHP47 | 2.5 | 20 | 0 | 40 | 1.6 | 1.19 | 50
CHP48 | 2.5 | 20 | 5 | 30 | 6 | 0.87752 | 0 | [8 empty] | CHP48 | 2.5 | 20 | 5 | 30 | 6 | 1.755 | 0 | [9 empty] | CHP48 | 2.5 | 20 | 5 | 30 | 6 | 0.3233 | 0
CHP48 | 2.5 | 20 | 5 | 35 | 3 | 0.87752 | 0 | [8 empty] | CHP48 | 2.5 | 20 | 5 | 35 | 3 | 2.2925 | 200 | [9 empty] | CHP48 | 2.5 | 20 | 5 | 35 | 3 | 0.3233 | 0
CHP48 | 2.5 | 20 | 5 | 40 | 1.6 | 1.1463 | 200 | [8 empty] | CHP48 | 2.5 | 20 | 5 | 40 | 1.6 | 1.2943 | 300 | [9 empty] | CHP48 | 2.5 | 20 | 5 | 40 | 1.6 | 0.3233 | 0
CHP49 | 2.5 | 20 | 10 | 30 | 6 | 0.14898 | 0 | [8 empty] | CHP49 | 2.5 | 20 | 10 | 30 | 6 | 0.29797 | 0 | [9 empty] | CHP49 | 2.5 | 20 | 10 | 30 | 6 | 0.054889 | 0
CHP49 | 2.5 | 20 | 10 | 35 | 3 | 0.14898 | 0 | [8 empty] | CHP49 | 2.5 | 20 | 10 | 35 | 3 | 0.29797 | 0 | [9 empty] | CHP49 | 2.5 | 20 | 10 | 35 | 3 | 0.054889 | 0
CHP49 | 2.5 | 20 | 10 | 40 | 1.6 | 0.14898 | 0 | [8 empty] | CHP49 | 2.5 | 20 | 10 | 40 | 1.6 | 1.4233 | 300 | [9 empty] | CHP49 | 2.5 | 20 | 10 | 40 | 1.6 | 0.054889 | 0
CHP50 | 1.5 | 5 | 0 | 30 | 6 | 3.3711 | 100 | [8 empty] | CHP50 | 1.5 | 5 | 0 | 30 | 6 | 3.6328 | 150 | [9 empty] | CHP50 | 1.5 | 5 | 0 | 30 | 6 | 2.9739 | 50
CHP50 | 1.5 | 5 | 0 | 35 | 3 | 1.8164 | 150 | [8 empty] | CHP50 | 1.5 | 5 | 0 | 35 | 3 | 2.3174 | 200 | [9 empty] | CHP50 | 1.5 | 5 | 0 | 35 | 3 | 2.9739 | 50
CHP50 | 1.5 | 5 | 0 | 40 | 1.6 | 1.1587 | 200 | [8 empty] | CHP50 | 1.5 | 5 | 0 | 40 | 1.6 | 1.2382 | 300 | [9 empty] | CHP50 | 1.5 | 5 | 0 | 40 | 1.6 | 1.242 | 100
CHP51 | 1.5 | 5 | 2.5 | 30 | 6 | 5.8651 | 50 | [8 empty] | CHP51 | 1.5 | 5 | 2.5 | 30 | 6 | 5.8443 | 100 | [9 empty] | CHP51 | 1.5 | 5 | 2.5 | 30 | 6 | 2.1608 | 50
CHP51 | 1.5 | 5 | 2.5 | 35 | 3 | 2.9222 | 100 | [8 empty] | CHP51 | 1.5 | 5 | 2.5 | 35 | 3 | 2.2066 | 200 | [9 empty] | CHP51 | 1.5 | 5 | 2.5 | 35 | 3 | 2.1608 | 50
CHP51 | 1.5 | 5 | 2.5 | 40 | 1.6 | 1.1033 | 200 | [8 empty] | CHP51 | 1.5 | 5 | 2.5 | 40 | 1.6 | 1.5869 | 250 | [9 empty] | CHP51 | 1.5 | 5 | 2.5 | 40 | 1.6 | 1.0766 | 100
CHP52 | 1.5 | 10 | 0 | 30 | 6 | 5.2245 | 50 | [8 empty] | CHP52 | 1.5 | 10 | 0 | 30 | 6 | 3.4113 | 150 | [9 empty] | CHP52 | 1.5 | 10 | 0 | 30 | 6 | 1.9248 | 50
CHP52 | 1.5 | 10 | 0 | 35 | 3 | 1.7057 | 150 | [8 empty] | CHP52 | 1.5 | 10 | 0 | 35 | 3 | 2.187 | 200 | [9 empty] | CHP52 | 1.5 | 10 | 0 | 35 | 3 | 1.9248 | 50
CHP52 | 1.5 | 10 | 0 | 40 | 1.6 | 1.0935 | 200 | [8 empty] | CHP52 | 1.5 | 10 | 0 | 40 | 1.6 | 1.5507 | 250 | [9 empty] | CHP52 | 1.5 | 10 | 0 | 40 | 1.6 | 1.1303 | 100
CHP53 | 1.5 | 10 | 5 | 30 | 6 | 2.8485 | 0 | [8 empty] | CHP53 | 1.5 | 10 | 5 | 30 | 6 | 5.6971 | 0 | [9 empty] | CHP53 | 1.5 | 10 | 5 | 30 | 6 | 1.0495 | 0
CHP53 | 1.5 | 10 | 5 | 35 | 3 | 2.8485 | 0 | [8 empty] | CHP53 | 1.5 | 10 | 5 | 35 | 3 | 2.2259 | 200 | [9 empty] | CHP53 | 1.5 | 10 | 5 | 35 | 3 | 1.0495 | 0
CHP53 | 1.5 | 10 | 5 | 40 | 1.6 | 1.113 | 200 | [8 empty] | CHP53 | 1.5 | 10 | 5 | 40 | 1.6 | 1.2674 | 300 | [9 empty] | CHP53 | 1.5 | 10 | 5 | 40 | 1.6 | 1.0495 | 0
CHP54 | 1.5 | 20 | 0 | 30 | 6 | 2.871 | 50 | [8 empty] | CHP54 | 1.5 | 20 | 0 | 30 | 6 | 5.742 | 50 | [9 empty] | CHP54 | 1.5 | 20 | 0 | 30 | 6 | 1.0577 | 50
CHP54 | 1.5 | 20 | 0 | 35 | 3 | 2.871 | 50 | [8 empty] | CHP54 | 1.5 | 20 | 0 | 35 | 3 | 2.6697 | 150 | [9 empty] | CHP54 | 1.5 | 20 | 0 | 35 | 3 | 1.0577 | 50
CHP54 | 1.5 | 20 | 0 | 40 | 1.6 | 1.3349 | 150 | [8 empty] | CHP54 | 1.5 | 20 | 0 | 40 | 1.6 | 1.2611 | 250 | [9 empty] | CHP54 | 1.5 | 20 | 0 | 40 | 1.6 | 1.0577 | 50
CHP55 | 1.5 | 20 | 5 | 30 | 6 | 0.91341 | 0 | [8 empty] | CHP55 | 1.5 | 20 | 5 | 30 | 6 | 1.8268 | 0 | [9 empty] | CHP55 | 1.5 | 20 | 5 | 30 | 6 | 0.33652 | 0
CHP55 | 1.5 | 20 | 5 | 35 | 3 | 0.91341 | 0 | [8 empty] | CHP55 | 1.5 | 20 | 5 | 35 | 3 | 2.3895 | 150 | [9 empty] | CHP55 | 1.5 | 20 | 5 | 35 | 3 | 0.33652 | 0
CHP55 | 1.5 | 20 | 5 | 40 | 1.6 | 0.91341 | 0 | [8 empty] | CHP55 | 1.5 | 20 | 5 | 40 | 1.6 | 1.1861 | 250 | [9 empty] | CHP55 | 1.5 | 20 | 5 | 40 | 1.6 | 0.33652 | 0
CHP56 | 1.5 | 20 | 10 | 30 | 6 | 0.17596 | 0 | [8 empty] | CHP56 | 1.5 | 20 | 10 | 30 | 6 | 0.35192 | 0 | [9 empty] | CHP56 | 1.5 | 20 | 10 | 30 | 6 | 0.064828 | 0
CHP56 | 1.5 | 20 | 10 | 35 | 3 | 0.17596 | 0 | [8 empty] | CHP56 | 1.5 | 20 | 10 | 35 | 3 | 0.35192 | 0 | [9 empty] | CHP56 | 1.5 | 20 | 10 | 35 | 3 | 0.064828 | 0
CHP56 | 1.5 | 20 | 10 | 40 | 1.6 | 0.17596 | 0 | [8 empty] | CHP56 | 1.5 | 20 | 10 | 40 | 1.6 | 1.2275 | 250 | [9 empty] | CHP56 | 1.5 | 20 | 10 | 40 | 1.6 | 0.064828 | 0
CHP57 | 2 | 5 | 0 | 30 | 6 | 3.2479 | 100 | [8 empty] | CHP57 | 2 | 5 | 0 | 30 | 6 | 3.6852 | 150 | [9 empty] | CHP57 | 2 | 5 | 0 | 30 | 6 | 2.4952 | 50
CHP57 | 2 | 5 | 0 | 35 | 3 | 1.8426 | 150 | [8 empty] | CHP57 | 2 | 5 | 0 | 35 | 3 | 2.3959 | 200 | [9 empty] | CHP57 | 2 | 5 | 0 | 35 | 3 | 2.4952 | 50
CHP57 | 2 | 5 | 0 | 40 | 1.6 | 1.198 | 200 | [8 empty] | CHP57 | 2 | 5 | 0 | 40 | 1.6 | 1.2989 | 300 | [9 empty] | CHP57 | 2 | 5 | 0 | 40 | 1.6 | 1.1966 | 100
CHP58 | 2 | 5 | 2.5 | 30 | 6 | 4.8773 | 50 | [8 empty] | CHP58 | 2 | 5 | 2.5 | 30 | 6 | 5.7145 | 100 | [9 empty] | CHP58 | 2 | 5 | 2.5 | 30 | 6 | 1.7969 | 50
CHP58 | 2 | 5 | 2.5 | 35 | 3 | 2.8572 | 100 | [8 empty] | CHP58 | 2 | 5 | 2.5 | 35 | 3 | 2.3178 | 200 | [9 empty] | CHP58 | 2 | 5 | 2.5 | 35 | 3 | 1.7969 | 50
CHP58 | 2 | 5 | 2.5 | 40 | 1.6 | 1.1589 | 200 | [8 empty] | CHP58 | 2 | 5 | 2.5 | 40 | 1.6 | 1.2841 | 300 | [9 empty] | CHP58 | 2 | 5 | 2.5 | 40 | 1.6 | 1.0527 | 100
CHP59 | 2 | 10 | 0 | 30 | 6 | 4.4186 | 50 | [8 empty] | CHP59 | 2 | 10 | 0 | 30 | 6 | 3.6563 | 150 | [9 empty] | CHP59 | 2 | 10 | 0 | 30 | 6 | 1.6279 | 50
CHP59 | 2 | 10 | 0 | 35 | 3 | 1.8282 | 150 | [8 empty] | CHP59 | 2 | 10 | 0 | 35 | 3 | 2.3857 | 200 | [9 empty] | CHP59 | 2 | 10 | 0 | 35 | 3 | 1.6279 | 50
CHP59 | 2 | 10 | 0 | 40 | 1.6 | 1.1929 | 200 | [8 empty] | CHP59 | 2 | 10 | 0 | 40 | 1.6 | 1.2934 | 300 | [9 empty] | CHP59 | 2 | 10 | 0 | 40 | 1.6 | 1.1457 | 100
CHP60 | 2 | 10 | 5 | 30 | 6 | 2.0767 | 0 | [8 empty] | CHP60 | 2 | 10 | 5 | 30 | 6 | 4.1534 | 0 | [9 empty] | CHP60 | 2 | 10 | 5 | 30 | 6 | 0.7651 | 0
CHP60 | 2 | 10 | 5 | 35 | 3 | 2.0767 | 0 | [8 empty] | CHP60 | 2 | 10 | 5 | 35 | 3 | 2.4657 | 200 | [9 empty] | CHP60 | 2 | 10 | 5 | 35 | 3 | 0.7651 | 0
CHP60 | 2 | 10 | 5 | 40 | 1.6 | 1.2329 | 200 | [8 empty] | CHP60 | 2 | 10 | 5 | 40 | 1.6 | 1.4634 | 300 | [9 empty] | CHP60 | 2 | 10 | 5 | 40 | 1.6 | 0.7651 | 0
CHP61 | 2 | 20 | 0 | 30 | 6 | 2.5839 | 50 | [8 empty] | CHP61 | 2 | 20 | 0 | 30 | 6 | 5.1678 | 50 | [9 empty] | CHP61 | 2 | 20 | 0 | 30 | 6 | 0.95197 | 50
CHP61 | 2 | 20 | 0 | 35 | 3 | 2.5839 | 50 | [8 empty] | CHP61 | 2 | 20 | 0 | 35 | 3 | 2.0364 | 200 | [9 empty] | CHP61 | 2 | 20 | 0 | 35 | 3 | 0.95197 | 50
CHP61 | 2 | 20 | 0 | 40 | 1.6 | 1.5055 | 150 | [8 empty] | CHP61 | 2 | 20 | 0 | 40 | 1.6 | 1.4614 | 250 | [9 empty] | CHP61 | 2 | 20 | 0 | 40 | 1.6 | 0.95197 | 50
CHP62 | 2 | 20 | 5 | 30 | 6 | 0.70202 | 0 | [8 empty] | CHP62 | 2 | 20 | 5 | 30 | 6 | 1.404 | 0 | [9 empty] | CHP62 | 2 | 20 | 5 | 30 | 6 | 0.25864 | 0
CHP62 | 2 | 20 | 5 | 35 | 3 | 0.70202 | 0 | [8 empty] | CHP62 | 2 | 20 | 5 | 35 | 3 | 2.6008 | 150 | [9 empty] | CHP62 | 2 | 20 | 5 | 35 | 3 | 0.25864 | 0
CHP62 | 2 | 20 | 5 | 40 | 1.6 | 0.70202 | 0 | [8 empty] | CHP62 | 2 | 20 | 5 | 40 | 1.6 | 1.3456 | 250 | [9 empty] | CHP62 | 2 | 20 | 5 | 40 | 1.6 | 0.25864 | 0
CHP63 | 2 | 20 | 10 | 30 | 6 | 0.11919 | 0 | [8 empty] | CHP63 | 2 | 20 | 10 | 30 | 6 | 0.23837 | 0 | [9 empty] | CHP63 | 2 | 20 | 10 | 30 | 6 | 0.043911 | 0
CHP63 | 2 | 20 | 10 | 35 | 3 | 0.11919 | 0 | [8 empty] | CHP63 | 2 | 20 | 10 | 35 | 3 | 0.23837 | 0 | [9 empty] | CHP63 | 2 | 20 | 10 | 35 | 3 | 0.043911 | 0
CHP63 | 2 | 20 | 10 | 40 | 1.6 | 0.11919 | 0 | [8 empty] | CHP63 | 2 | 20 | 10 | 40 | 1.6 | 1.4256 | 250 | [9 empty] | CHP63 | 2 | 20 | 10 | 40 | 1.6 | 0.043911 | 0

## Peaking Lookup matrix (hidden)
Source group | Capacity | Stack height | Clearance | Operational hours | Background | Acceptable PC | Unique NO2 PC | NO2 Screening distance | Source group | Capacity | Stack height | Clearance | Operational hours | Background | Acceptable PC | Unique NOX PC | NOX Screening distance | Source group | Capacity | Stack height | Clearance | Operational hours | Background | Acceptable PC | Unique NO2 PC | NO2 Screening distance | Source group | Capacity | Stack height | Clearance | Operational hours | Background | Acceptable PC | Unique NOX PC | NOX Screening distance
Peak1 | 10 | 3 | 0 | 750 | 30 | 6 | 3.3046 | 50 | Peak1 | 10 | 3 | 0 | 750 | N/A | 0.45 | 0.39064 | 300 | Peak1 | 10 | 3 | 0 | 750 | 30 | 6 | 2.8142 | 100 | Peak1 | 10 | 3 | 0 | 750 | N/A | 0.45 | 0.43129 | 450
Peak1 | 10 | 3 | 0 | 750 | 35 | 3 | 1.4071 | 100 | Peak2 | 10 | 6 | 3 | 750 | N/A | 0.45 | 0.36566 | 300 | Peak1 | 10 | 3 | 0 | 750 | 35 | 3 | 2.8142 | 100 | Peak2 | 10 | 6 | 3 | 750 | N/A | 0.45 | 0.40474 | 450
Peak1 | 10 | 3 | 0 | 750 | 40 | 1.6 | 1.4071 | 100 | Peak3 | 10 | 10 | 7 | 750 | N/A | 0.45 | 0.42579 | 250 | Peak1 | 10 | 3 | 0 | 750 | 40 | 1.6 | 1.5628 | 150 | Peak3 | 10 | 10 | 7 | 750 | N/A | 0.45 | 0.43543 | 400
Peak2 | 10 | 6 | 3 | 750 | 30 | 6 | 1.9028 | 50 | Peak4 | 15 | 3 | 0 | 750 | N/A | 0.45 | 0.41293 | 350 | Peak2 | 10 | 6 | 3 | 750 | 30 | 6 | 3.8056 | 50 | Peak4 | 15 | 3 | 0 | 750 | N/A | 0.45 | 0.43036 | 550
Peak2 | 10 | 6 | 3 | 750 | 35 | 3 | 1.9028 | 50 | Peak5 | 15 | 6 | 3 | 750 | N/A | 0.45 | 0.38896 | 350 | Peak2 | 10 | 6 | 3 | 750 | 35 | 3 | 2.3247 | 100 | Peak5 | 15 | 6 | 3 | 750 | N/A | 0.45 | 0.40632 | 550
Peak2 | 10 | 6 | 3 | 750 | 40 | 1.6 | 1.1623 | 100 | Peak6 | 15 | 10 | 7 | 750 | N/A | 0.45 | 0.44192 | 300 | Peak2 | 10 | 6 | 3 | 750 | 40 | 1.6 | 1.4024 | 150 | Peak6 | 15 | 10 | 7 | 750 | N/A | 0.45 | 0.42636 | 500
Peak3 | 10 | 10 | 7 | 750 | 30 | 6 | 0.65804 | 0 | Peak7 | 20 | 3 | 0 | 750 | N/A | 0.45 | 0.41379 | 400 | Peak3 | 10 | 10 | 7 | 750 | 30 | 6 | 1.3161 | 0 | Peak7 | 20 | 3 | 0 | 750 | N/A | 0.45 | 0.4146 | 650
Peak3 | 10 | 10 | 7 | 750 | 35 | 3 | 0.65804 | 0 | Peak8 | 20 | 6 | 3 | 750 | N/A | 0.45 | 0.39104 | 400 | Peak3 | 10 | 10 | 7 | 750 | 35 | 3 | 1.3161 | 0 | Peak8 | 20 | 6 | 3 | 750 | N/A | 0.45 | 0.43999 | 600
Peak3 | 10 | 10 | 7 | 750 | 40 | 1.6 | 0.65804 | 0 | Peak9 | 20 | 10 | 7 | 750 | N/A | 0.45 | 0.43537 | 350 | Peak3 | 10 | 10 | 7 | 750 | 40 | 1.6 | 1.3161 | 0 | Peak9 | 20 | 10 | 7 | 750 | N/A | 0.45 | 0.40567 | 600
Peak4 | 15 | 3 | 0 | 750 | 30 | 6 | 3.9395 | 50 | Peak10 | 25 | 3 | 0 | 750 | N/A | 0.45 | 0.40516 | 450 | Peak4 | 15 | 3 | 0 | 750 | 30 | 6 | 3.6024 | 100 | Peak10 | 25 | 3 | 0 | 750 | N/A | 0.45 | 0.43547 | 700
Peak4 | 15 | 3 | 0 | 750 | 35 | 3 | 1.8012 | 100 | Peak11 | 25 | 6 | 3 | 750 | N/A | 0.45 | 0.38374 | 450 | Peak4 | 15 | 3 | 0 | 750 | 35 | 3 | 2.0525 | 150 | Peak11 | 25 | 6 | 3 | 750 | N/A | 0.45 | 0.41349 | 700
Peak4 | 15 | 3 | 0 | 750 | 40 | 1.6 | 1.0262 | 150 | Peak12 | 25 | 10 | 7 | 750 | N/A | 0.45 | 0.42 | 400 | Peak4 | 15 | 3 | 0 | 750 | 40 | 1.6 | 1.34 | 200 | Peak12 | 25 | 10 | 7 | 750 | N/A | 0.45 | 0.42438 | 650
Peak5 | 15 | 6 | 3 | 750 | 30 | 6 | 2.2478 | 50 | Peak13 | 30 | 3 | 0 | 750 | N/A | 0.45 | 0.4291 | 550 | Peak5 | 15 | 6 | 3 | 750 | 30 | 6 | 4.4957 | 50 | Peak13 | 30 | 3 | 0 | 750 | N/A | 0.45 | 0.41467 | 900
Peak5 | 15 | 6 | 3 | 750 | 35 | 3 | 2.2478 | 50 | Peak14 | 30 | 6 | 3 | 750 | N/A | 0.45 | 0.40554 | 550 | Peak5 | 15 | 6 | 3 | 750 | 35 | 3 | 2.9521 | 100 | Peak14 | 30 | 6 | 3 | 750 | N/A | 0.45 | 0.43083 | 850
Peak5 | 15 | 6 | 3 | 750 | 40 | 1.6 | 1.476 | 100 | Peak15 | 30 | 10 | 7 | 750 | N/A | 0.45 | 0.42617 | 500 | Peak5 | 15 | 6 | 3 | 750 | 40 | 1.6 | 1.2373 | 200 | Peak15 | 30 | 10 | 7 | 750 | N/A | 0.45 | 0.43766 | 800
Peak6 | 15 | 10 | 7 | 750 | 30 | 6 | 0.7661 | 0 | Peak16 | 40 | 3 | 0 | 750 | N/A | 0.45 | 0.41357 | 650 | Peak6 | 15 | 10 | 7 | 750 | 30 | 6 | 1.5322 | 0 | Peak16 | 40 | 3 | 0 | 750 | N/A | 0.45 | 0.44106 | 1000
Peak6 | 15 | 10 | 7 | 750 | 35 | 3 | 0.7661 | 0 | Peak17 | 40 | 6 | 3 | 750 | N/A | 0.45 | 0.43924 | 600 | Peak6 | 15 | 10 | 7 | 750 | 35 | 3 | 1.5322 | 0 | Peak17 | 40 | 6 | 3 | 750 | N/A | 0.45 | 0.42172 | 1000
Peak6 | 15 | 10 | 7 | 750 | 40 | 1.6 | 0.7661 | 0 | Peak18 | 40 | 10 | 7 | 750 | N/A | 0.45 | 0.40552 | 600 | Peak6 | 15 | 10 | 7 | 750 | 40 | 1.6 | 1.4597 | 150 | Peak18 | 40 | 10 | 7 | 750 | N/A | 0.45 | 0.42475 | 950
Peak7 | 20 | 3 | 0 | 750 | 30 | 6 | 4.41 | 50 | Peak19 | 50 | 3 | 0 | 750 | N/A | 0.45 | 0.4345 | 700 | Peak7 | 20 | 3 | 0 | 750 | 30 | 6 | 4.2469 | 100 | Peak19 | 50 | 3 | 0 | 750 | N/A | 0.45 | 0.39806 | 1200
Peak7 | 20 | 3 | 0 | 750 | 35 | 3 | 2.1234 | 100 | Peak20 | 50 | 6 | 3 | 750 | N/A | 0.45 | 0.4129 | 700 | Peak7 | 20 | 3 | 0 | 750 | 35 | 3 | 2.4683 | 150 | Peak20 | 50 | 6 | 3 | 750 | N/A | 0.45 | 0.43336 | 1100
Peak7 | 20 | 3 | 0 | 750 | 40 | 1.6 | 1.2341 | 150 | Peak21 | 50 | 10 | 7 | 750 | N/A | 0.45 | 0.42424 | 650 | Peak7 | 20 | 3 | 0 | 750 | 40 | 1.6 | 1.1649 | 250 | Peak21 | 50 | 10 | 7 | 750 | N/A | 0.45 | 0.40672 | 1100
Peak8 | 20 | 6 | 3 | 750 | 30 | 6 | 2.4944 | 50 | Peak1 | 10 | 3 | 0 | 1000 | N/A | 0.45 | 0.41502 | 350 | Peak8 | 20 | 6 | 3 | 750 | 30 | 6 | 4.9887 | 50 | Peak1 | 10 | 3 | 0 | 1000 | N/A | 0.45 | 0.42722 | 550
Peak8 | 20 | 6 | 3 | 750 | 35 | 3 | 2.4944 | 50 | Peak2 | 10 | 6 | 3 | 1000 | N/A | 0.45 | 0.38852 | 350 | Peak8 | 20 | 6 | 3 | 750 | 35 | 3 | 2.1945 | 150 | Peak2 | 10 | 6 | 3 | 1000 | N/A | 0.45 | 0.403 | 550
Peak8 | 20 | 6 | 3 | 750 | 40 | 1.6 | 1.0972 | 150 | Peak3 | 10 | 10 | 7 | 1000 | N/A | 0.45 | 0.43918 | 300 | Peak8 | 20 | 6 | 3 | 750 | 40 | 1.6 | 1.498 | 200 | Peak3 | 10 | 10 | 7 | 1000 | N/A | 0.45 | 0.42183 | 500
Peak9 | 20 | 10 | 7 | 750 | 30 | 6 | 0.84051 | 0 | Peak4 | 15 | 3 | 0 | 1000 | N/A | 0.45 | 0.3829 | 450 | Peak9 | 20 | 10 | 7 | 750 | 30 | 6 | 1.681 | 0 | Peak4 | 15 | 3 | 0 | 1000 | N/A | 0.45 | 0.44958 | 650
Peak9 | 20 | 10 | 7 | 750 | 35 | 3 | 0.84051 | 0 | Peak5 | 15 | 6 | 3 | 1000 | N/A | 0.45 | 0.42695 | 400 | Peak9 | 20 | 10 | 7 | 750 | 35 | 3 | 1.681 | 0 | Peak5 | 15 | 6 | 3 | 1000 | N/A | 0.45 | 0.42614 | 650
Peak9 | 20 | 10 | 7 | 750 | 40 | 1.6 | 0.84051 | 0 | Peak6 | 15 | 10 | 7 | 1000 | N/A | 0.45 | 0.39072 | 400 | Peak9 | 20 | 10 | 7 | 750 | 40 | 1.6 | 1.2795 | 200 | Peak6 | 15 | 10 | 7 | 1000 | N/A | 0.45 | 0.43963 | 600
Peak10 | 25 | 3 | 0 | 750 | 30 | 6 | 4.7667 | 50 | Peak7 | 20 | 3 | 0 | 1000 | N/A | 0.45 | 0.40134 | 500 | Peak10 | 25 | 3 | 0 | 750 | 30 | 6 | 4.7872 | 100 | Peak7 | 20 | 3 | 0 | 1000 | N/A | 0.45 | 0.44955 | 750
Peak10 | 25 | 3 | 0 | 750 | 35 | 3 | 2.3936 | 100 | Peak8 | 20 | 6 | 3 | 1000 | N/A | 0.45 | 0.44013 | 450 | Peak10 | 25 | 3 | 0 | 750 | 35 | 3 | 2.8275 | 150 | Peak8 | 20 | 6 | 3 | 1000 | N/A | 0.45 | 0.42748 | 750
Peak10 | 25 | 3 | 0 | 750 | 40 | 1.6 | 1.4137 | 150 | Peak9 | 20 | 10 | 7 | 1000 | N/A | 0.45 | 0.40547 | 450 | Peak10 | 25 | 3 | 0 | 750 | 40 | 1.6 | 1.3514 | 250 | Peak9 | 20 | 10 | 7 | 1000 | N/A | 0.45 | 0.43639 | 700
Peak11 | 25 | 6 | 3 | 750 | 30 | 6 | 2.6737 | 50 | Peak10 | 25 | 3 | 0 | 1000 | N/A | 0.45 | 0.40724 | 550 | Peak11 | 25 | 6 | 3 | 750 | 30 | 6 | 5.3473 | 50 | Peak10 | 25 | 3 | 0 | 1000 | N/A | 0.45 | 0.44005 | 850
Peak11 | 25 | 6 | 3 | 750 | 35 | 3 | 2.6737 | 50 | Peak11 | 25 | 6 | 3 | 1000 | N/A | 0.45 | 0.44054 | 500 | Peak11 | 25 | 6 | 3 | 750 | 35 | 3 | 2.503 | 150 | Peak11 | 25 | 6 | 3 | 1000 | N/A | 0.45 | 0.4194 | 850
Peak11 | 25 | 6 | 3 | 750 | 40 | 1.6 | 1.2515 | 150 | Peak12 | 25 | 10 | 7 | 1000 | N/A | 0.45 | 0.40778 | 500 | Peak11 | 25 | 6 | 3 | 750 | 40 | 1.6 | 1.2639 | 250 | Peak12 | 25 | 10 | 7 | 1000 | N/A | 0.45 | 0.42486 | 800
Peak12 | 25 | 10 | 7 | 750 | 30 | 6 | 0.89253 | 0 | Peak13 | 30 | 3 | 0 | 1000 | N/A | 0.45 | 0.44836 | 650 | Peak12 | 25 | 10 | 7 | 750 | 30 | 6 | 1.7851 | 0 | Peak13 | 30 | 3 | 0 | 1000 | N/A | 0.45 | 0.40894 | 1100
Peak12 | 25 | 10 | 7 | 750 | 35 | 3 | 0.89253 | 0 | Peak14 | 30 | 6 | 3 | 1000 | N/A | 0.45 | 0.42541 | 650 | Peak12 | 25 | 10 | 7 | 750 | 35 | 3 | 1.7851 | 0 | Peak14 | 30 | 6 | 3 | 1000 | N/A | 0.45 | 0.39138 | 1100
Peak12 | 25 | 10 | 7 | 750 | 40 | 1.6 | 0.89253 | 0 | Peak15 | 30 | 10 | 7 | 1000 | N/A | 0.45 | 0.43947 | 600 | Peak12 | 25 | 10 | 7 | 750 | 40 | 1.6 | 1.4702 | 200 | Peak15 | 30 | 10 | 7 | 1000 | N/A | 0.45 | 0.42172 | 1000
Peak13 | 30 | 3 | 0 | 750 | 30 | 6 | 3.6 | 100 | Peak16 | 40 | 3 | 0 | 1000 | N/A | 0.45 | 0.44852 | 750 | Peak13 | 30 | 3 | 0 | 750 | 30 | 6 | 4.0914 | 150 | Peak16 | 40 | 3 | 0 | 1000 | N/A | 0.45 | 0.4485 | 1200
Peak13 | 30 | 3 | 0 | 750 | 35 | 3 | 2.0457 | 150 | Peak17 | 40 | 6 | 3 | 1000 | N/A | 0.45 | 0.42686 | 750 | Peak13 | 30 | 3 | 0 | 750 | 35 | 3 | 2.6698 | 200 | Peak17 | 40 | 6 | 3 | 1000 | N/A | 0.45 | 0.42966 | 1200
Peak13 | 30 | 3 | 0 | 750 | 40 | 1.6 | 1.3349 | 200 | Peak18 | 40 | 10 | 7 | 1000 | N/A | 0.45 | 0.43626 | 700 | Peak13 | 30 | 3 | 0 | 750 | 40 | 1.6 | 1.4474 | 300 | Peak18 | 40 | 10 | 7 | 1000 | N/A | 0.45 | 0.40382 | 1200
Peak14 | 30 | 6 | 3 | 750 | 30 | 6 | 4.2258 | 50 | Peak19 | 50 | 3 | 0 | 1000 | N/A | 0.45 | 0.43918 | 850 | Peak14 | 30 | 6 | 3 | 750 | 30 | 6 | 5.8558 | 100 | Peak19 | 50 | 3 | 0 | 1000 | N/A | 0.45 | 0.42271 | 1400
Peak14 | 30 | 6 | 3 | 750 | 35 | 3 | 2.9279 | 100 | Peak20 | 50 | 6 | 3 | 1000 | N/A | 0.45 | 0.41889 | 850 | Peak14 | 30 | 6 | 3 | 750 | 35 | 3 | 2.4663 | 200 | Peak20 | 50 | 6 | 3 | 1000 | N/A | 0.45 | 0.40587 | 1400
Peak14 | 30 | 6 | 3 | 750 | 40 | 1.6 | 1.2331 | 200 | Peak21 | 50 | 10 | 7 | 1000 | N/A | 0.45 | 0.42476 | 800 | Peak14 | 30 | 6 | 3 | 750 | 40 | 1.6 | 1.3639 | 300 | Peak21 | 50 | 10 | 7 | 1000 | N/A | 0.45 | 0.42637 | 1300
Peak15 | 30 | 10 | 7 | 750 | 30 | 6 | 1.4552 | 0 | Peak1 | 10 | 3 | 0 | 1500 | N/A | 0.45 | 0.43129 | 450 | Peak15 | 30 | 10 | 7 | 750 | 30 | 6 | 2.9103 | 0 | Peak1 | 10 | 3 | 0 | 1500 | N/A | 0.45 | 0.44578 | 700
Peak15 | 30 | 10 | 7 | 750 | 35 | 3 | 1.4552 | 0 | Peak2 | 10 | 6 | 3 | 1500 | N/A | 0.45 | 0.40474 | 450 | Peak15 | 30 | 10 | 7 | 750 | 35 | 3 | 2.8968 | 150 | Peak2 | 10 | 6 | 3 | 1500 | N/A | 0.45 | 0.42253 | 700
Peak15 | 30 | 10 | 7 | 750 | 40 | 1.6 | 1.4484 | 150 | Peak3 | 10 | 10 | 7 | 1500 | N/A | 0.45 | 0.43543 | 400 | Peak15 | 30 | 10 | 7 | 750 | 40 | 1.6 | 1.5877 | 250 | Peak3 | 10 | 10 | 7 | 1500 | N/A | 0.45 | 0.43383 | 650
Peak16 | 40 | 3 | 0 | 750 | 30 | 6 | 4.243 | 100 | Peak4 | 15 | 3 | 0 | 1500 | N/A | 0.45 | 0.43036 | 550 | Peak16 | 40 | 3 | 0 | 750 | 30 | 6 | 4.92 | 150 | Peak4 | 15 | 3 | 0 | 1500 | N/A | 0.45 | 0.41565 | 900
Peak16 | 40 | 3 | 0 | 750 | 35 | 3 | 2.46 | 150 | Peak5 | 15 | 6 | 3 | 1500 | N/A | 0.45 | 0.40632 | 550 | Peak16 | 40 | 3 | 0 | 750 | 35 | 3 | 2.3215 | 250 | Peak5 | 15 | 6 | 3 | 1500 | N/A | 0.45 | 0.43146 | 850
Peak16 | 40 | 3 | 0 | 750 | 40 | 1.6 | 1.1607 | 250 | Peak6 | 15 | 10 | 7 | 1500 | N/A | 0.45 | 0.42636 | 500 | Peak16 | 40 | 3 | 0 | 750 | 40 | 1.6 | 1.4033 | 350 | Peak6 | 15 | 10 | 7 | 1500 | N/A | 0.45 | 0.43774 | 800
Peak17 | 40 | 6 | 3 | 750 | 30 | 6 | 4.6941 | 50 | Peak7 | 20 | 3 | 0 | 1500 | N/A | 0.45 | 0.4146 | 650 | Peak17 | 40 | 6 | 3 | 750 | 30 | 6 | 4.3683 | 150 | Peak7 | 20 | 3 | 0 | 1500 | N/A | 0.45 | 0.44193 | 1000
Peak17 | 40 | 6 | 3 | 750 | 35 | 3 | 2.1841 | 150 | Peak8 | 20 | 6 | 3 | 1500 | N/A | 0.45 | 0.43999 | 600 | Peak17 | 40 | 6 | 3 | 750 | 35 | 3 | 2.9855 | 200 | Peak8 | 20 | 6 | 3 | 1500 | N/A | 0.45 | 0.42223 | 1000
Peak17 | 40 | 6 | 3 | 750 | 40 | 1.6 | 1.4928 | 200 | Peak9 | 20 | 10 | 7 | 1500 | N/A | 0.45 | 0.40567 | 600 | Peak17 | 40 | 6 | 3 | 750 | 40 | 1.6 | 1.3278 | 350 | Peak9 | 20 | 10 | 7 | 1500 | N/A | 0.45 | 0.42481 | 950
Peak18 | 40 | 10 | 7 | 750 | 30 | 6 | 1.6047 | 0 | Peak10 | 25 | 3 | 0 | 1500 | N/A | 0.45 | 0.43547 | 700 | Peak18 | 40 | 10 | 7 | 750 | 30 | 6 | 3.2094 | 0 | Peak10 | 25 | 3 | 0 | 1500 | N/A | 0.45 | 0.3987 | 1200
Peak18 | 40 | 10 | 7 | 750 | 35 | 3 | 1.6047 | 0 | Peak11 | 25 | 6 | 3 | 1500 | N/A | 0.45 | 0.41349 | 700 | Peak18 | 40 | 10 | 7 | 750 | 35 | 3 | 2.5496 | 200 | Peak11 | 25 | 6 | 3 | 1500 | N/A | 0.45 | 0.43379 | 1100
Peak18 | 40 | 10 | 7 | 750 | 40 | 1.6 | 1.2748 | 200 | Peak12 | 25 | 10 | 7 | 1500 | N/A | 0.45 | 0.42438 | 650 | Peak18 | 40 | 10 | 7 | 750 | 40 | 1.6 | 1.5117 | 300 | Peak12 | 25 | 10 | 7 | 1500 | N/A | 0.45 | 0.40676 | 1100
Peak19 | 50 | 3 | 0 | 750 | 30 | 6 | 4.7797 | 100 | Peak13 | 30 | 3 | 0 | 1500 | N/A | 0.45 | 0.41467 | 900 | Peak19 | 50 | 3 | 0 | 750 | 30 | 6 | 5.6362 | 150 | Peak13 | 30 | 3 | 0 | 1500 | N/A | 0.45 | 0.42657 | 1400
Peak19 | 50 | 3 | 0 | 750 | 35 | 3 | 2.8181 | 150 | Peak14 | 30 | 6 | 3 | 1500 | N/A | 0.45 | 0.43083 | 850 | Peak19 | 50 | 3 | 0 | 750 | 35 | 3 | 2.6935 | 250 | Peak14 | 30 | 6 | 3 | 1500 | N/A | 0.45 | 0.40927 | 1400
Peak19 | 50 | 3 | 0 | 750 | 40 | 1.6 | 1.3467 | 250 | Peak15 | 30 | 10 | 7 | 1500 | N/A | 0.45 | 0.43766 | 800 | Peak19 | 50 | 3 | 0 | 750 | 40 | 1.6 | 1.3399 | 400 | Peak15 | 30 | 10 | 7 | 1500 | N/A | 0.45 | 0.42999 | 1300
Peak20 | 50 | 6 | 3 | 750 | 30 | 6 | 5.0333 | 50 | Peak16 | 40 | 3 | 0 | 1500 | N/A | 0.45 | 0.44106 | 1000 | Peak20 | 50 | 6 | 3 | 750 | 30 | 6 | 4.9802 | 150 | Peak16 | 40 | 3 | 0 | 1500 | N/A | 0.45 | 0.43823 | 1600
Peak20 | 50 | 6 | 3 | 750 | 35 | 3 | 2.4901 | 150 | Peak17 | 40 | 6 | 3 | 1500 | N/A | 0.45 | 0.42172 | 1000 | Peak20 | 50 | 6 | 3 | 750 | 35 | 3 | 2.5205 | 250 | Peak17 | 40 | 6 | 3 | 1500 | N/A | 0.45 | 0.42097 | 1600
Peak20 | 50 | 6 | 3 | 750 | 40 | 1.6 | 1.2603 | 250 | Peak18 | 40 | 10 | 7 | 1500 | N/A | 0.45 | 0.42475 | 950 | Peak20 | 50 | 6 | 3 | 750 | 40 | 1.6 | 1.5449 | 350 | Peak18 | 40 | 10 | 7 | 1500 | N/A | 0.45 | 0.43766 | 1500
Peak21 | 50 | 10 | 7 | 750 | 30 | 6 | 1.7112 | 0 | Peak19 | 50 | 3 | 0 | 1500 | N/A | 0.45 | 0.39806 | 1200 | Peak21 | 50 | 10 | 7 | 750 | 30 | 6 | 3.4224 | 0 | Peak19 | 50 | 3 | 0 | 1500 | N/A | 0.45 | 0.43765 | 1800
Peak21 | 50 | 10 | 7 | 750 | 35 | 3 | 1.7112 | 0 | Peak20 | 50 | 6 | 3 | 1500 | N/A | 0.45 | 0.43336 | 1100 | Peak21 | 50 | 10 | 7 | 750 | 35 | 3 | 2.929 | 200 | Peak20 | 50 | 6 | 3 | 1500 | N/A | 0.45 | 0.42118 | 1800
Peak21 | 50 | 10 | 7 | 750 | 40 | 1.6 | 1.4645 | 200 | Peak21 | 50 | 10 | 7 | 1500 | N/A | 0.45 | 0.40672 | 1100 | Peak21 | 50 | 10 | 7 | 750 | 40 | 1.6 | 1.4195 | 350 | Peak21 | 50 | 10 | 7 | 1500 | N/A | 0.45 | 0.43427 | 1700
Peak1 | 10 | 3 | 0 | 1000 | 30 | 6 | 4.4061 | 50 | Peak1 | 10 | 3 | 0 | 2250 | N/A | 0.45 | 0.42184 | 600 | Peak1 | 10 | 3 | 0 | 1000 | 30 | 6 | 3.7522 | 100 | Peak1 | 10 | 3 | 0 | 2250 | N/A | 0.45 | 0.42014 | 950
Peak1 | 10 | 3 | 0 | 1000 | 35 | 3 | 1.8761 | 100 | Peak2 | 10 | 6 | 3 | 2250 | N/A | 0.45 | 0.39876 | 600 | Peak1 | 10 | 3 | 0 | 1000 | 35 | 3 | 2.0837 | 150 | Peak2 | 10 | 6 | 3 | 2250 | N/A | 0.45 | 0.43407 | 900
Peak1 | 10 | 3 | 0 | 1000 | 40 | 1.6 | 1.0418 | 150 | Peak3 | 10 | 10 | 7 | 2250 | N/A | 0.45 | 0.4141 | 550 | Peak1 | 10 | 3 | 0 | 1000 | 40 | 1.6 | 1.3473 | 200 | Peak3 | 10 | 10 | 7 | 2250 | N/A | 0.45 | 0.43837 | 850
Peak2 | 10 | 6 | 3 | 1000 | 30 | 6 | 2.5371 | 50 | Peak4 | 15 | 3 | 0 | 2250 | N/A | 0.45 | 0.40933 | 750 | Peak2 | 10 | 6 | 3 | 1000 | 30 | 6 | 5.0742 | 50 | Peak4 | 15 | 3 | 0 | 2250 | N/A | 0.45 | 0.40439 | 1200
Peak2 | 10 | 6 | 3 | 1000 | 35 | 3 | 2.5371 | 50 | Peak5 | 15 | 6 | 3 | 2250 | N/A | 0.45 | 0.43044 | 700 | Peak2 | 10 | 6 | 3 | 1000 | 35 | 3 | 1.8699 | 150 | Peak5 | 15 | 6 | 3 | 2250 | N/A | 0.45 | 0.44086 | 1100
Peak2 | 10 | 6 | 3 | 1000 | 40 | 1.6 | 1.5498 | 100 | Peak6 | 15 | 10 | 7 | 2250 | N/A | 0.45 | 0.44173 | 650 | Peak2 | 10 | 6 | 3 | 1000 | 40 | 1.6 | 1.2448 | 200 | Peak6 | 15 | 10 | 7 | 2250 | N/A | 0.45 | 0.41247 | 1100
Peak3 | 10 | 10 | 7 | 1000 | 30 | 6 | 0.87739 | 0 | Peak7 | 20 | 3 | 0 | 2250 | N/A | 0.45 | 0.42128 | 850 | Peak3 | 10 | 10 | 7 | 1000 | 30 | 6 | 1.7548 | 0 | Peak7 | 20 | 3 | 0 | 2250 | N/A | 0.45 | 0.4486 | 1300
Peak3 | 10 | 10 | 7 | 1000 | 35 | 3 | 0.87739 | 0 | Peak8 | 20 | 6 | 3 | 2250 | N/A | 0.45 | 0.43829 | 800 | Peak3 | 10 | 10 | 7 | 1000 | 35 | 3 | 1.7548 | 0 | Peak8 | 20 | 6 | 3 | 2250 | N/A | 0.45 | 0.42978 | 1300
Peak3 | 10 | 10 | 7 | 1000 | 40 | 1.6 | 0.87739 | 0 | Peak9 | 20 | 10 | 7 | 2250 | N/A | 0.45 | 0.44574 | 750 | Peak3 | 10 | 10 | 7 | 1000 | 40 | 1.6 | 1.4995 | 150 | Peak9 | 20 | 10 | 7 | 2250 | N/A | 0.45 | 0.40435 | 1300
Peak4 | 15 | 3 | 0 | 1000 | 30 | 6 | 5.2527 | 50 | Peak10 | 25 | 3 | 0 | 2250 | N/A | 0.45 | 0.42139 | 950 | Peak4 | 15 | 3 | 0 | 1000 | 30 | 6 | 4.8033 | 100 | Peak10 | 25 | 3 | 0 | 2250 | N/A | 0.45 | 0.43011 | 1500
Peak4 | 15 | 3 | 0 | 1000 | 35 | 3 | 2.4016 | 100 | Peak11 | 25 | 6 | 3 | 2250 | N/A | 0.45 | 0.43488 | 900 | Peak4 | 15 | 3 | 0 | 1000 | 35 | 3 | 2.7366 | 150 | Peak11 | 25 | 6 | 3 | 2250 | N/A | 0.45 | 0.41299 | 1500
Peak4 | 15 | 3 | 0 | 1000 | 40 | 1.6 | 1.3683 | 150 | Peak12 | 25 | 10 | 7 | 2250 | N/A | 0.45 | 0.4393 | 850 | Peak4 | 15 | 3 | 0 | 1000 | 40 | 1.6 | 1.2747 | 250 | Peak12 | 25 | 10 | 7 | 2250 | N/A | 0.45 | 0.431 | 1400
Peak5 | 15 | 6 | 3 | 1000 | 30 | 6 | 2.9971 | 50 | Peak13 | 30 | 3 | 0 | 2250 | N/A | 0.45 | 0.40355 | 1200 | Peak5 | 15 | 6 | 3 | 1000 | 30 | 6 | 5.9942 | 50 | Peak13 | 30 | 3 | 0 | 2250 | N/A | 0.45 | 0.44062 | 1800
Peak5 | 15 | 6 | 3 | 1000 | 35 | 3 | 2.9971 | 50 | Peak14 | 30 | 6 | 3 | 2250 | N/A | 0.45 | 0.44031 | 1100 | Peak5 | 15 | 6 | 3 | 1000 | 35 | 3 | 2.4443 | 150 | Peak14 | 30 | 6 | 3 | 2250 | N/A | 0.45 | 0.42196 | 1800
Peak5 | 15 | 6 | 3 | 1000 | 40 | 1.6 | 1.2221 | 150 | Peak15 | 30 | 10 | 7 | 2250 | N/A | 0.45 | 0.41243 | 1100 | Peak5 | 15 | 6 | 3 | 1000 | 40 | 1.6 | 1.1936 | 250 | Peak15 | 30 | 10 | 7 | 2250 | N/A | 0.45 | 0.43489 | 1700
Peak6 | 15 | 10 | 7 | 1000 | 30 | 6 | 1.0215 | 0 | Peak16 | 40 | 3 | 0 | 2250 | N/A | 0.45 | 0.44783 | 1300 | Peak6 | 15 | 10 | 7 | 1000 | 30 | 6 | 2.0429 | 0 | Peak16 | 40 | 3 | 0 | 2250 | N/A | 0.45 | #N/A | 2100
Peak6 | 15 | 10 | 7 | 1000 | 35 | 3 | 1.0215 | 0 | Peak17 | 40 | 6 | 3 | 2250 | N/A | 0.45 | 0.42933 | 1300 | Peak6 | 15 | 10 | 7 | 1000 | 35 | 3 | 2.0429 | 0 | Peak17 | 40 | 6 | 3 | 2250 | N/A | 0.45 | #N/A | 2100
Peak6 | 15 | 10 | 7 | 1000 | 40 | 1.6 | 1.0215 | 0 | Peak18 | 40 | 10 | 7 | 2250 | N/A | 0.45 | 0.40432 | 1300 | Peak6 | 15 | 10 | 7 | 1000 | 40 | 1.6 | 1.4131 | 200 | Peak18 | 40 | 10 | 7 | 2250 | N/A | 0.45 | 0.43253 | 2000
Peak7 | 20 | 3 | 0 | 1000 | 30 | 6 | 5.8801 | 50 | Peak19 | 50 | 3 | 0 | 2250 | N/A | 0.45 | 0.4295 | 1500 | Peak7 | 20 | 3 | 0 | 1000 | 30 | 6 | 5.6625 | 100 | Peak19 | 50 | 3 | 0 | 2250 | N/A | 0.45 | #N/A | 2400
Peak7 | 20 | 3 | 0 | 1000 | 35 | 3 | 2.8313 | 100 | Peak20 | 50 | 6 | 3 | 2250 | N/A | 0.45 | 0.41265 | 1500 | Peak7 | 20 | 3 | 0 | 1000 | 35 | 3 | 2.1689 | 200 | Peak20 | 50 | 6 | 3 | 2250 | N/A | 0.45 | #N/A | 2300
Peak7 | 20 | 3 | 0 | 1000 | 40 | 1.6 | 1.0845 | 200 | Peak21 | 50 | 10 | 7 | 2250 | N/A | 0.45 | 0.43098 | 1400 | Peak7 | 20 | 3 | 0 | 1000 | 40 | 1.6 | 1.5532 | 250 | Peak21 | 50 | 10 | 7 | 2250 | N/A | 0.45 | #N/A | 2300
Peak8 | 20 | 6 | 3 | 1000 | 30 | 6 | 3.3258 | 50 | [9 empty] | Peak8 | 20 | 6 | 3 | 1000 | 30 | 6 | 4.6096 | 100
Peak8 | 20 | 6 | 3 | 1000 | 35 | 3 | 2.3048 | 100 | [9 empty] | Peak8 | 20 | 6 | 3 | 1000 | 35 | 3 | 2.926 | 150
Peak8 | 20 | 6 | 3 | 1000 | 40 | 1.6 | 1.463 | 150 | [9 empty] | Peak8 | 20 | 6 | 3 | 1000 | 40 | 1.6 | 1.4544 | 250
Peak9 | 20 | 10 | 7 | 1000 | 30 | 6 | 1.1207 | 0 | [9 empty] | Peak9 | 20 | 10 | 7 | 1000 | 30 | 6 | 2.2414 | 0
Peak9 | 20 | 10 | 7 | 1000 | 35 | 3 | 1.1207 | 0 | [9 empty] | Peak9 | 20 | 10 | 7 | 1000 | 35 | 3 | 2.3171 | 150
Peak9 | 20 | 10 | 7 | 1000 | 40 | 1.6 | 1.1207 | 0 | [9 empty] | Peak9 | 20 | 10 | 7 | 1000 | 40 | 1.6 | 1.2908 | 250
Peak10 | 25 | 3 | 0 | 1000 | 30 | 6 | 3.1915 | 100 | [9 empty] | Peak10 | 25 | 3 | 0 | 1000 | 30 | 6 | 3.7699 | 150
Peak10 | 25 | 3 | 0 | 1000 | 35 | 3 | 1.885 | 150 | [9 empty] | Peak10 | 25 | 3 | 0 | 1000 | 35 | 3 | 2.5053 | 200
Peak10 | 25 | 3 | 0 | 1000 | 40 | 1.6 | 1.2527 | 200 | [9 empty] | Peak10 | 25 | 3 | 0 | 1000 | 40 | 1.6 | 1.3713 | 300
Peak11 | 25 | 6 | 3 | 1000 | 30 | 6 | 3.5649 | 50 | [9 empty] | Peak11 | 25 | 6 | 3 | 1000 | 30 | 6 | 5.1607 | 100
Peak11 | 25 | 6 | 3 | 1000 | 35 | 3 | 2.5804 | 100 | [9 empty] | Peak11 | 25 | 6 | 3 | 1000 | 35 | 3 | 2.3012 | 200
Peak11 | 25 | 6 | 3 | 1000 | 40 | 1.6 | 1.1506 | 200 | [9 empty] | Peak11 | 25 | 6 | 3 | 1000 | 40 | 1.6 | 1.2941 | 300
Peak12 | 25 | 10 | 7 | 1000 | 30 | 6 | 1.19 | 0 | [9 empty] | Peak12 | 25 | 10 | 7 | 1000 | 30 | 6 | 2.3801 | 0
Peak12 | 25 | 10 | 7 | 1000 | 35 | 3 | 1.19 | 0 | [9 empty] | Peak12 | 25 | 10 | 7 | 1000 | 35 | 3 | 2.6308 | 150
Peak12 | 25 | 10 | 7 | 1000 | 40 | 1.6 | 1.3154 | 150 | [9 empty] | Peak12 | 25 | 10 | 7 | 1000 | 40 | 1.6 | 1.4938 | 250
Peak13 | 30 | 3 | 0 | 1000 | 30 | 6 | 4.8 | 100 | [9 empty] | Peak13 | 30 | 3 | 0 | 1000 | 30 | 6 | 5.4552 | 150
Peak13 | 30 | 3 | 0 | 1000 | 35 | 3 | 2.7276 | 150 | [9 empty] | Peak13 | 30 | 3 | 0 | 1000 | 35 | 3 | 2.5398 | 250
Peak13 | 30 | 3 | 0 | 1000 | 40 | 1.6 | 1.2699 | 250 | [9 empty] | Peak13 | 30 | 3 | 0 | 1000 | 40 | 1.6 | 1.5363 | 350
Peak14 | 30 | 6 | 3 | 1000 | 30 | 6 | 5.6344 | 50 | [9 empty] | Peak14 | 30 | 6 | 3 | 1000 | 30 | 6 | 4.867 | 150
Peak14 | 30 | 6 | 3 | 1000 | 35 | 3 | 2.4335 | 150 | [9 empty] | Peak14 | 30 | 6 | 3 | 1000 | 35 | 3 | 2.3804 | 250
Peak14 | 30 | 6 | 3 | 1000 | 40 | 1.6 | 1.1902 | 250 | [9 empty] | Peak14 | 30 | 6 | 3 | 1000 | 40 | 1.6 | 1.4487 | 350
Peak15 | 30 | 10 | 7 | 1000 | 30 | 6 | 1.9402 | 0 | [9 empty] | Peak15 | 30 | 10 | 7 | 1000 | 30 | 6 | 3.8804 | 0
Peak15 | 30 | 10 | 7 | 1000 | 35 | 3 | 1.9402 | 0 | [9 empty] | Peak15 | 30 | 10 | 7 | 1000 | 35 | 3 | 2.8167 | 200
Peak15 | 30 | 10 | 7 | 1000 | 40 | 1.6 | 1.4083 | 200 | [9 empty] | Peak15 | 30 | 10 | 7 | 1000 | 40 | 1.6 | 1.3241 | 350
Peak16 | 40 | 3 | 0 | 1000 | 30 | 6 | 5.6573 | 100 | [9 empty] | Peak16 | 40 | 3 | 0 | 1000 | 30 | 6 | 4.322 | 200
Peak16 | 40 | 3 | 0 | 1000 | 35 | 3 | 2.161 | 200 | [9 empty] | Peak16 | 40 | 3 | 0 | 1000 | 35 | 3 | 2.353 | 300
Peak16 | 40 | 3 | 0 | 1000 | 40 | 1.6 | 1.5476 | 250 | [9 empty] | Peak16 | 40 | 3 | 0 | 1000 | 40 | 1.6 | 1.5401 | 400
Peak17 | 40 | 6 | 3 | 1000 | 30 | 6 | 4.5661 | 100 | [9 empty] | Peak17 | 40 | 6 | 3 | 1000 | 30 | 6 | 5.8244 | 150
Peak17 | 40 | 6 | 3 | 1000 | 35 | 3 | 2.9122 | 150 | [9 empty] | Peak17 | 40 | 6 | 3 | 1000 | 35 | 3 | 2.9005 | 250
Peak17 | 40 | 6 | 3 | 1000 | 40 | 1.6 | 1.4502 | 250 | [9 empty] | Peak17 | 40 | 6 | 3 | 1000 | 40 | 1.6 | 1.4569 | 400
Peak18 | 40 | 10 | 7 | 1000 | 30 | 6 | 2.1396 | 0 | [9 empty] | Peak18 | 40 | 10 | 7 | 1000 | 30 | 6 | 4.2792 | 0
Peak18 | 40 | 10 | 7 | 1000 | 35 | 3 | 2.1396 | 0 | [9 empty] | Peak18 | 40 | 10 | 7 | 1000 | 35 | 3 | 2.5764 | 250
Peak18 | 40 | 10 | 7 | 1000 | 40 | 1.6 | 1.2882 | 250 | [9 empty] | Peak18 | 40 | 10 | 7 | 1000 | 40 | 1.6 | 1.3425 | 400
Peak19 | 50 | 3 | 0 | 1000 | 30 | 6 | 3.7575 | 150 | [9 empty] | Peak19 | 50 | 3 | 0 | 1000 | 30 | 6 | 4.9924 | 200
Peak19 | 50 | 3 | 0 | 1000 | 35 | 3 | 2.4962 | 200 | [9 empty] | Peak19 | 50 | 3 | 0 | 1000 | 35 | 3 | 2.7337 | 300
Peak19 | 50 | 3 | 0 | 1000 | 40 | 1.6 | 1.3668 | 300 | [9 empty] | Peak19 | 50 | 3 | 0 | 1000 | 40 | 1.6 | 1.5084 | 450
Peak20 | 50 | 6 | 3 | 1000 | 30 | 6 | 5.1075 | 100 | [9 empty] | Peak20 | 50 | 6 | 3 | 1000 | 30 | 6 | 4.5861 | 200
Peak20 | 50 | 6 | 3 | 1000 | 35 | 3 | 2.293 | 200 | [9 empty] | Peak20 | 50 | 6 | 3 | 1000 | 35 | 3 | 2.582 | 300
Peak20 | 50 | 6 | 3 | 1000 | 40 | 1.6 | 1.291 | 300 | [9 empty] | Peak20 | 50 | 6 | 3 | 1000 | 40 | 1.6 | 1.43 | 450
Peak21 | 50 | 10 | 7 | 1000 | 30 | 6 | 2.2816 | 0 | [9 empty] | Peak21 | 50 | 10 | 7 | 1000 | 30 | 6 | 5.2159 | 150
Peak21 | 50 | 10 | 7 | 1000 | 35 | 3 | 2.608 | 150 | [9 empty] | Peak21 | 50 | 10 | 7 | 1000 | 35 | 3 | 2.9812 | 250
Peak21 | 50 | 10 | 7 | 1000 | 40 | 1.6 | 1.4906 | 250 | [9 empty] | Peak21 | 50 | 10 | 7 | 1000 | 40 | 1.6 | 1.5669 | 400
Peak1 | 10 | 3 | 0 | 1500 | 30 | 6 | 2.8142 | 100 | [9 empty] | Peak1 | 10 | 3 | 0 | 1500 | 30 | 6 | 5.6284 | 100
Peak1 | 10 | 3 | 0 | 1500 | 35 | 3 | 2.8142 | 100 | [9 empty] | Peak1 | 10 | 3 | 0 | 1500 | 35 | 3 | 2.0209 | 200
Peak1 | 10 | 3 | 0 | 1500 | 40 | 1.6 | 1.5628 | 150 | [9 empty] | Peak1 | 10 | 3 | 0 | 1500 | 40 | 1.6 | 1.4381 | 250
Peak2 | 10 | 6 | 3 | 1500 | 30 | 6 | 3.8056 | 50 | [9 empty] | Peak2 | 10 | 6 | 3 | 1500 | 30 | 6 | 4.6494 | 100
Peak2 | 10 | 6 | 3 | 1500 | 35 | 3 | 2.3247 | 100 | [9 empty] | Peak2 | 10 | 6 | 3 | 1500 | 35 | 3 | 2.8048 | 150
Peak2 | 10 | 6 | 3 | 1500 | 40 | 1.6 | 1.4024 | 150 | [9 empty] | Peak2 | 10 | 6 | 3 | 1500 | 40 | 1.6 | 1.343 | 250
Peak3 | 10 | 10 | 7 | 1500 | 30 | 6 | 1.3161 | 0 | [9 empty] | Peak3 | 10 | 10 | 7 | 1500 | 30 | 6 | 2.6322 | 0
Peak3 | 10 | 10 | 7 | 1500 | 35 | 3 | 1.3161 | 0 | [9 empty] | Peak3 | 10 | 10 | 7 | 1500 | 35 | 3 | 2.2493 | 150
Peak3 | 10 | 10 | 7 | 1500 | 40 | 1.6 | 1.3161 | 0 | [9 empty] | Peak3 | 10 | 10 | 7 | 1500 | 40 | 1.6 | 1.1922 | 250
Peak4 | 15 | 3 | 0 | 1500 | 30 | 6 | 3.6024 | 100 | [9 empty] | Peak4 | 15 | 3 | 0 | 1500 | 30 | 6 | 4.1049 | 150
Peak4 | 15 | 3 | 0 | 1500 | 35 | 3 | 2.0525 | 150 | [9 empty] | Peak4 | 15 | 3 | 0 | 1500 | 35 | 3 | 2.6801 | 200
Peak4 | 15 | 3 | 0 | 1500 | 40 | 1.6 | 1.34 | 200 | [9 empty] | Peak4 | 15 | 3 | 0 | 1500 | 40 | 1.6 | 1.4526 | 300
Peak5 | 15 | 6 | 3 | 1500 | 30 | 6 | 4.4957 | 50 | [9 empty] | Peak5 | 15 | 6 | 3 | 1500 | 30 | 6 | 5.9041 | 100
Peak5 | 15 | 6 | 3 | 1500 | 35 | 3 | 2.9521 | 100 | [9 empty] | Peak5 | 15 | 6 | 3 | 1500 | 35 | 3 | 2.4745 | 200
Peak5 | 15 | 6 | 3 | 1500 | 40 | 1.6 | 1.2373 | 200 | [9 empty] | Peak5 | 15 | 6 | 3 | 1500 | 40 | 1.6 | 1.3673 | 300
Peak6 | 15 | 10 | 7 | 1500 | 30 | 6 | 1.5322 | 0 | [9 empty] | Peak6 | 15 | 10 | 7 | 1500 | 30 | 6 | 3.0644 | 0
Peak6 | 15 | 10 | 7 | 1500 | 35 | 3 | 1.5322 | 0 | [9 empty] | Peak6 | 15 | 10 | 7 | 1500 | 35 | 3 | 2.9195 | 150
Peak6 | 15 | 10 | 7 | 1500 | 40 | 1.6 | 1.4597 | 150 | [9 empty] | Peak6 | 15 | 10 | 7 | 1500 | 40 | 1.6 | 1.5906 | 250
Peak7 | 20 | 3 | 0 | 1500 | 30 | 6 | 4.2469 | 100 | [9 empty] | Peak7 | 20 | 3 | 0 | 1500 | 30 | 6 | 4.9366 | 150
Peak7 | 20 | 3 | 0 | 1500 | 35 | 3 | 2.4683 | 150 | [9 empty] | Peak7 | 20 | 3 | 0 | 1500 | 35 | 3 | 2.3298 | 250
Peak7 | 20 | 3 | 0 | 1500 | 40 | 1.6 | 1.1649 | 250 | [9 empty] | Peak7 | 20 | 3 | 0 | 1500 | 40 | 1.6 | 1.4079 | 350
Peak8 | 20 | 6 | 3 | 1500 | 30 | 6 | 4.9887 | 50 | [9 empty] | Peak8 | 20 | 6 | 3 | 1500 | 30 | 6 | 4.389 | 150
Peak8 | 20 | 6 | 3 | 1500 | 35 | 3 | 2.1945 | 150 | [9 empty] | Peak8 | 20 | 6 | 3 | 1500 | 35 | 3 | 2.9959 | 200
Peak8 | 20 | 6 | 3 | 1500 | 40 | 1.6 | 1.498 | 200 | [9 empty] | Peak8 | 20 | 6 | 3 | 1500 | 40 | 1.6 | 1.3307 | 350
Peak9 | 20 | 10 | 7 | 1500 | 30 | 6 | 1.681 | 0 | [9 empty] | Peak9 | 20 | 10 | 7 | 1500 | 30 | 6 | 3.362 | 0
Peak9 | 20 | 10 | 7 | 1500 | 35 | 3 | 1.681 | 0 | [9 empty] | Peak9 | 20 | 10 | 7 | 1500 | 35 | 3 | 2.559 | 200
Peak9 | 20 | 10 | 7 | 1500 | 40 | 1.6 | 1.2795 | 200 | [9 empty] | Peak9 | 20 | 10 | 7 | 1500 | 40 | 1.6 | 1.5137 | 300
Peak10 | 25 | 3 | 0 | 1500 | 30 | 6 | 4.7872 | 100 | [9 empty] | Peak10 | 25 | 3 | 0 | 1500 | 30 | 6 | 5.6549 | 150
Peak10 | 25 | 3 | 0 | 1500 | 35 | 3 | 2.8275 | 150 | [9 empty] | Peak10 | 25 | 3 | 0 | 1500 | 35 | 3 | 2.7029 | 250
Peak10 | 25 | 3 | 0 | 1500 | 40 | 1.6 | 1.3514 | 250 | [9 empty] | Peak10 | 25 | 3 | 0 | 1500 | 40 | 1.6 | 1.3438 | 400
Peak11 | 25 | 6 | 3 | 1500 | 30 | 6 | 5.3473 | 50 | [9 empty] | Peak11 | 25 | 6 | 3 | 1500 | 30 | 6 | 5.0059 | 150
Peak11 | 25 | 6 | 3 | 1500 | 35 | 3 | 2.503 | 150 | [9 empty] | Peak11 | 25 | 6 | 3 | 1500 | 35 | 3 | 2.5277 | 250
Peak11 | 25 | 6 | 3 | 1500 | 40 | 1.6 | 1.2639 | 250 | [9 empty] | Peak11 | 25 | 6 | 3 | 1500 | 40 | 1.6 | 1.5482 | 350
Peak12 | 25 | 10 | 7 | 1500 | 30 | 6 | 1.7851 | 0 | [9 empty] | Peak12 | 25 | 10 | 7 | 1500 | 30 | 6 | 3.5701 | 0
Peak12 | 25 | 10 | 7 | 1500 | 35 | 3 | 1.7851 | 0 | [9 empty] | Peak12 | 25 | 10 | 7 | 1500 | 35 | 3 | 2.9404 | 200
Peak12 | 25 | 10 | 7 | 1500 | 40 | 1.6 | 1.4702 | 200 | [9 empty] | Peak12 | 25 | 10 | 7 | 1500 | 40 | 1.6 | 1.4209 | 350
Peak13 | 30 | 3 | 0 | 1500 | 30 | 6 | 4.0914 | 150 | [9 empty] | Peak13 | 30 | 3 | 0 | 1500 | 30 | 6 | 5.3395 | 200
Peak13 | 30 | 3 | 0 | 1500 | 35 | 3 | 2.6698 | 200 | [9 empty] | Peak13 | 30 | 3 | 0 | 1500 | 35 | 3 | 2.8948 | 300
Peak13 | 30 | 3 | 0 | 1500 | 40 | 1.6 | 1.4474 | 300 | [9 empty] | Peak13 | 30 | 3 | 0 | 1500 | 40 | 1.6 | 1.3784 | 500
Peak14 | 30 | 6 | 3 | 1500 | 30 | 6 | 5.8558 | 100 | [9 empty] | Peak14 | 30 | 6 | 3 | 1500 | 30 | 6 | 4.9325 | 200
Peak14 | 30 | 6 | 3 | 1500 | 35 | 3 | 2.4663 | 200 | [9 empty] | Peak14 | 30 | 6 | 3 | 1500 | 35 | 3 | 2.7277 | 300
Peak14 | 30 | 6 | 3 | 1500 | 40 | 1.6 | 1.3639 | 300 | [9 empty] | Peak14 | 30 | 6 | 3 | 1500 | 40 | 1.6 | 1.5109 | 450
Peak15 | 30 | 10 | 7 | 1500 | 30 | 6 | 2.9103 | 0 | [9 empty] | Peak15 | 30 | 10 | 7 | 1500 | 30 | 6 | 5.7936 | 150
Peak15 | 30 | 10 | 7 | 1500 | 35 | 3 | 2.8968 | 150 | [9 empty] | Peak15 | 30 | 10 | 7 | 1500 | 35 | 3 | 2.4718 | 300
Peak15 | 30 | 10 | 7 | 1500 | 40 | 1.6 | 1.5877 | 250 | [9 empty] | Peak15 | 30 | 10 | 7 | 1500 | 40 | 1.6 | 1.3858 | 450
Peak16 | 40 | 3 | 0 | 1500 | 30 | 6 | 4.92 | 150 | [9 empty] | Peak16 | 40 | 3 | 0 | 1500 | 30 | 6 | 4.6429 | 250
Peak16 | 40 | 3 | 0 | 1500 | 35 | 3 | 2.3215 | 250 | [9 empty] | Peak16 | 40 | 3 | 0 | 1500 | 35 | 3 | 2.8067 | 350
Peak16 | 40 | 3 | 0 | 1500 | 40 | 1.6 | 1.4033 | 350 | [9 empty] | Peak16 | 40 | 3 | 0 | 1500 | 40 | 1.6 | 1.4689 | 550
Peak17 | 40 | 6 | 3 | 1500 | 30 | 6 | 4.3683 | 150 | [9 empty] | Peak17 | 40 | 6 | 3 | 1500 | 30 | 6 | 5.971 | 200
Peak17 | 40 | 6 | 3 | 1500 | 35 | 3 | 2.9855 | 200 | [9 empty] | Peak17 | 40 | 6 | 3 | 1500 | 35 | 3 | 2.6555 | 350
Peak17 | 40 | 6 | 3 | 1500 | 40 | 1.6 | 1.3278 | 350 | [9 empty] | Peak17 | 40 | 6 | 3 | 1500 | 40 | 1.6 | 1.5889 | 500
Peak18 | 40 | 10 | 7 | 1500 | 30 | 6 | 3.2094 | 0 | [9 empty] | Peak18 | 40 | 10 | 7 | 1500 | 30 | 6 | 5.0993 | 200
Peak18 | 40 | 10 | 7 | 1500 | 35 | 3 | 2.5496 | 200 | [9 empty] | Peak18 | 40 | 10 | 7 | 1500 | 35 | 3 | 2.4359 | 350
Peak18 | 40 | 10 | 7 | 1500 | 40 | 1.6 | 1.5117 | 300 | [9 empty] | Peak18 | 40 | 10 | 7 | 1500 | 40 | 1.6 | 1.4658 | 500
Peak19 | 50 | 3 | 0 | 1500 | 30 | 6 | 5.6362 | 150 | [9 empty] | Peak19 | 50 | 3 | 0 | 1500 | 30 | 6 | 5.387 | 250
Peak19 | 50 | 3 | 0 | 1500 | 35 | 3 | 2.6935 | 250 | [9 empty] | Peak19 | 50 | 3 | 0 | 1500 | 35 | 3 | 2.6798 | 400
Peak19 | 50 | 3 | 0 | 1500 | 40 | 1.6 | 1.3399 | 400 | [9 empty] | Peak19 | 50 | 3 | 0 | 1500 | 40 | 1.6 | 1.5108 | 600
Peak20 | 50 | 6 | 3 | 1500 | 30 | 6 | 4.9802 | 150 | [9 empty] | Peak20 | 50 | 6 | 3 | 1500 | 30 | 6 | 5.041 | 250
Peak20 | 50 | 6 | 3 | 1500 | 35 | 3 | 2.5205 | 250 | [9 empty] | Peak20 | 50 | 6 | 3 | 1500 | 35 | 3 | 2.5421 | 400
Peak20 | 50 | 6 | 3 | 1500 | 40 | 1.6 | 1.5449 | 350 | [9 empty] | Peak20 | 50 | 6 | 3 | 1500 | 40 | 1.6 | 1.4322 | 600
Peak21 | 50 | 10 | 7 | 1500 | 30 | 6 | 3.4224 | 0 | [9 empty] | Peak21 | 50 | 10 | 7 | 1500 | 30 | 6 | 5.8579 | 200
Peak21 | 50 | 10 | 7 | 1500 | 35 | 3 | 2.929 | 200 | [9 empty] | Peak21 | 50 | 10 | 7 | 1500 | 35 | 3 | 2.839 | 350
Peak21 | 50 | 10 | 7 | 1500 | 40 | 1.6 | 1.4195 | 350 | [9 empty] | Peak21 | 50 | 10 | 7 | 1500 | 40 | 1.6 | 1.4974 | 550
Peak1 | 10 | 3 | 0 | 2250 | 30 | 6 | 4.2213 | 100 | [9 empty] | Peak1 | 10 | 3 | 0 | 2250 | 30 | 6 | 4.6883 | 150
Peak1 | 10 | 3 | 0 | 2250 | 35 | 3 | 2.3441 | 150 | [9 empty] | Peak1 | 10 | 3 | 0 | 2250 | 35 | 3 | 2.1572 | 250
Peak1 | 10 | 3 | 0 | 2250 | 40 | 1.6 | 1.5157 | 200 | [9 empty] | Peak1 | 10 | 3 | 0 | 2250 | 40 | 1.6 | 1.3073 | 350
Peak2 | 10 | 6 | 3 | 2250 | 30 | 6 | 5.7085 | 50 | [9 empty] | Peak2 | 10 | 6 | 3 | 2250 | 30 | 6 | 4.2072 | 150
Peak2 | 10 | 6 | 3 | 2250 | 35 | 3 | 2.1036 | 150 | [9 empty] | Peak2 | 10 | 6 | 3 | 2250 | 35 | 3 | 2.8008 | 200
Peak2 | 10 | 6 | 3 | 2250 | 40 | 1.6 | 1.4004 | 200 | [9 empty] | Peak2 | 10 | 6 | 3 | 2250 | 40 | 1.6 | 1.5358 | 300
Peak3 | 10 | 10 | 7 | 2250 | 30 | 6 | 1.9741 | 0 | [9 empty] | Peak3 | 10 | 10 | 7 | 2250 | 30 | 6 | 3.9483 | 0
Peak3 | 10 | 10 | 7 | 2250 | 35 | 3 | 1.9741 | 0 | [9 empty] | Peak3 | 10 | 10 | 7 | 2250 | 35 | 3 | 2.4072 | 200
Peak3 | 10 | 10 | 7 | 2250 | 40 | 1.6 | 1.2036 | 200 | [9 empty] | Peak3 | 10 | 10 | 7 | 2250 | 40 | 1.6 | 1.3834 | 300
Peak4 | 15 | 3 | 0 | 2250 | 30 | 6 | 5.4037 | 100 | [9 empty] | Peak4 | 15 | 3 | 0 | 2250 | 30 | 6 | 4.0201 | 200
Peak4 | 15 | 3 | 0 | 2250 | 35 | 3 | 2.01 | 200 | [9 empty] | Peak4 | 15 | 3 | 0 | 2250 | 35 | 3 | 2.8681 | 250
Peak4 | 15 | 3 | 0 | 2250 | 40 | 1.6 | 1.434 | 250 | [9 empty] | Peak4 | 15 | 3 | 0 | 2250 | 40 | 1.6 | 1.4285 | 400
Peak5 | 15 | 6 | 3 | 2250 | 30 | 6 | 4.4281 | 100 | [9 empty] | Peak5 | 15 | 6 | 3 | 2250 | 30 | 6 | 5.4996 | 150
Peak5 | 15 | 6 | 3 | 2250 | 35 | 3 | 2.7498 | 150 | [9 empty] | Peak5 | 15 | 6 | 3 | 2250 | 35 | 3 | 2.6857 | 250
Peak5 | 15 | 6 | 3 | 2250 | 40 | 1.6 | 1.3428 | 250 | [9 empty] | Peak5 | 15 | 6 | 3 | 2250 | 40 | 1.6 | 1.3449 | 400
Peak6 | 15 | 10 | 7 | 2250 | 30 | 6 | 2.2983 | 0 | [9 empty] | Peak6 | 15 | 10 | 7 | 2250 | 30 | 6 | 4.5966 | 0
Peak6 | 15 | 10 | 7 | 2250 | 35 | 3 | 2.2983 | 0 | [9 empty] | Peak6 | 15 | 10 | 7 | 2250 | 35 | 3 | 2.3859 | 250
Peak6 | 15 | 10 | 7 | 2250 | 40 | 1.6 | 1.5898 | 200 | [9 empty] | Peak6 | 15 | 10 | 7 | 2250 | 40 | 1.6 | 1.4908 | 350
Peak7 | 20 | 3 | 0 | 2250 | 30 | 6 | 3.7024 | 150 | [9 empty] | Peak7 | 20 | 3 | 0 | 2250 | 30 | 6 | 4.8801 | 200
Peak7 | 20 | 3 | 0 | 2250 | 35 | 3 | 2.4401 | 200 | [9 empty] | Peak7 | 20 | 3 | 0 | 2250 | 35 | 3 | 2.6561 | 300
Peak7 | 20 | 3 | 0 | 2250 | 40 | 1.6 | 1.3281 | 300 | [9 empty] | Peak7 | 20 | 3 | 0 | 2250 | 40 | 1.6 | 1.468 | 450
Peak8 | 20 | 6 | 3 | 2250 | 30 | 6 | 5.1858 | 100 | [9 empty] | Peak8 | 20 | 6 | 3 | 2250 | 30 | 6 | 4.4939 | 200
Peak8 | 20 | 6 | 3 | 2250 | 35 | 3 | 2.2469 | 200 | [9 empty] | Peak8 | 20 | 6 | 3 | 2250 | 35 | 3 | 2.5052 | 300
Peak8 | 20 | 6 | 3 | 2250 | 40 | 1.6 | 1.2526 | 300 | [9 empty] | Peak8 | 20 | 6 | 3 | 2250 | 40 | 1.6 | 1.3864 | 450
Peak9 | 20 | 10 | 7 | 2250 | 30 | 6 | 2.5215 | 0 | [9 empty] | Peak9 | 20 | 10 | 7 | 2250 | 30 | 6 | 5.2134 | 150
Peak9 | 20 | 10 | 7 | 2250 | 35 | 3 | 2.6067 | 150 | [9 empty] | Peak9 | 20 | 10 | 7 | 2250 | 35 | 3 | 2.9043 | 250
Peak9 | 20 | 10 | 7 | 2250 | 40 | 1.6 | 1.4521 | 250 | [9 empty] | Peak9 | 20 | 10 | 7 | 2250 | 40 | 1.6 | 1.5113 | 400
Peak10 | 25 | 3 | 0 | 2250 | 30 | 6 | 4.2412 | 150 | [9 empty] | Peak10 | 25 | 3 | 0 | 2250 | 30 | 6 | 5.637 | 200
Peak10 | 25 | 3 | 0 | 2250 | 35 | 3 | 2.8185 | 200 | [9 empty] | Peak10 | 25 | 3 | 0 | 2250 | 35 | 3 | 2.4519 | 350
Peak10 | 25 | 3 | 0 | 2250 | 40 | 1.6 | 1.5427 | 300 | [9 empty] | Peak10 | 25 | 3 | 0 | 2250 | 40 | 1.6 | 1.4661 | 500
Peak11 | 25 | 6 | 3 | 2250 | 30 | 6 | 5.8058 | 100 | [9 empty] | Peak11 | 25 | 6 | 3 | 2250 | 30 | 6 | 5.1777 | 200
Peak11 | 25 | 6 | 3 | 2250 | 35 | 3 | 2.5888 | 200 | [9 empty] | Peak11 | 25 | 6 | 3 | 2250 | 35 | 3 | 2.9118 | 300
Peak11 | 25 | 6 | 3 | 2250 | 40 | 1.6 | 1.4559 | 300 | [9 empty] | Peak11 | 25 | 6 | 3 | 2250 | 40 | 1.6 | 1.3877 | 500
Peak12 | 25 | 10 | 7 | 2250 | 30 | 6 | 2.6776 | 0 | [9 empty] | Peak12 | 25 | 10 | 7 | 2250 | 30 | 6 | 5.9192 | 150
Peak12 | 25 | 10 | 7 | 2250 | 35 | 3 | 2.9596 | 150 | [9 empty] | Peak12 | 25 | 10 | 7 | 2250 | 35 | 3 | 2.6392 | 300
Peak12 | 25 | 10 | 7 | 2250 | 40 | 1.6 | 1.3196 | 300 | [9 empty] | Peak12 | 25 | 10 | 7 | 2250 | 40 | 1.6 | 1.4915 | 450
Peak13 | 30 | 3 | 0 | 2250 | 30 | 6 | 4.0047 | 200 | [9 empty] | Peak13 | 30 | 3 | 0 | 2250 | 30 | 6 | 5.7146 | 250
Peak13 | 30 | 3 | 0 | 2250 | 35 | 3 | 2.8573 | 250 | [9 empty] | Peak13 | 30 | 3 | 0 | 2250 | 35 | 3 | 2.8474 | 400
Peak13 | 30 | 3 | 0 | 2250 | 40 | 1.6 | 1.4237 | 400 | [9 empty] | Peak13 | 30 | 3 | 0 | 2250 | 40 | 1.6 | 1.5881 | 600
Peak14 | 30 | 6 | 3 | 2250 | 30 | 6 | 5.4754 | 150 | [9 empty] | Peak14 | 30 | 6 | 3 | 2250 | 30 | 6 | 5.356 | 250
Peak14 | 30 | 6 | 3 | 2250 | 35 | 3 | 2.678 | 250 | [9 empty] | Peak14 | 30 | 6 | 3 | 2250 | 35 | 3 | 2.6838 | 400
Peak14 | 30 | 6 | 3 | 2250 | 40 | 1.6 | 1.3419 | 400 | [9 empty] | Peak14 | 30 | 6 | 3 | 2250 | 40 | 1.6 | 1.5039 | 600
Peak15 | 30 | 10 | 7 | 2250 | 30 | 6 | 4.3655 | 0 | [9 empty] | Peak15 | 30 | 10 | 7 | 2250 | 30 | 6 | 4.763 | 250
Peak15 | 30 | 10 | 7 | 2250 | 35 | 3 | 2.3815 | 250 | [9 empty] | Peak15 | 30 | 10 | 7 | 2250 | 35 | 3 | 2.9792 | 350
Peak15 | 30 | 10 | 7 | 2250 | 40 | 1.6 | 1.4896 | 350 | [9 empty] | Peak15 | 30 | 10 | 7 | 2250 | 40 | 1.6 | 1.5647 | 550
Peak16 | 40 | 3 | 0 | 2250 | 30 | 6 | 4.8623 | 200 | [9 empty] | Peak16 | 40 | 3 | 0 | 2250 | 30 | 6 | 5.2942 | 300
Peak16 | 40 | 3 | 0 | 2250 | 35 | 3 | 2.6471 | 300 | [9 empty] | Peak16 | 40 | 3 | 0 | 2250 | 35 | 3 | 2.9273 | 450
Peak16 | 40 | 3 | 0 | 2250 | 40 | 1.6 | 1.4636 | 450 | [9 empty] | Peak16 | 40 | 3 | 0 | 2250 | 40 | 1.6 | 1.5613 | 700
Peak17 | 40 | 6 | 3 | 2250 | 30 | 6 | 4.4783 | 200 | [9 empty] | Peak17 | 40 | 6 | 3 | 2250 | 30 | 6 | 4.998 | 300
Peak17 | 40 | 6 | 3 | 2250 | 35 | 3 | 2.499 | 300 | [9 empty] | Peak17 | 40 | 6 | 3 | 2250 | 35 | 3 | 2.7674 | 450
Peak17 | 40 | 6 | 3 | 2250 | 40 | 1.6 | 1.3837 | 450 | [9 empty] | Peak17 | 40 | 6 | 3 | 2250 | 40 | 1.6 | 1.4838 | 700
Peak18 | 40 | 10 | 7 | 2250 | 30 | 6 | 5.1703 | 150 | [9 empty] | Peak18 | 40 | 10 | 7 | 2250 | 30 | 6 | 5.7968 | 250
Peak18 | 40 | 10 | 7 | 2250 | 35 | 3 | 2.8984 | 250 | [9 empty] | Peak18 | 40 | 10 | 7 | 2250 | 35 | 3 | 2.553 | 450
Peak18 | 40 | 10 | 7 | 2250 | 40 | 1.6 | 1.5103 | 400 | [9 empty] | Peak18 | 40 | 10 | 7 | 2250 | 40 | 1.6 | 1.5237 | 650
Peak19 | 50 | 3 | 0 | 2250 | 30 | 6 | 5.6164 | 200 | [9 empty] | Peak19 | 50 | 3 | 0 | 2250 | 30 | 6 | 4.8888 | 350
Peak19 | 50 | 3 | 0 | 2250 | 35 | 3 | 2.4444 | 350 | [9 empty] | Peak19 | 50 | 3 | 0 | 2250 | 35 | 3 | 2.9244 | 500
Peak19 | 50 | 3 | 0 | 2250 | 40 | 1.6 | 1.4622 | 500 | [9 empty] | Peak19 | 50 | 3 | 0 | 2250 | 40 | 1.6 | 1.5092 | 800
Peak20 | 50 | 6 | 3 | 2250 | 30 | 6 | 5.1593 | 200 | [9 empty] | Peak20 | 50 | 6 | 3 | 2250 | 30 | 6 | 5.8095 | 300
Peak20 | 50 | 6 | 3 | 2250 | 35 | 3 | 2.9048 | 300 | [9 empty] | Peak20 | 50 | 6 | 3 | 2250 | 35 | 3 | 2.7706 | 500
Peak20 | 50 | 6 | 3 | 2250 | 40 | 1.6 | 1.3853 | 500 | [9 empty] | Peak20 | 50 | 6 | 3 | 2250 | 40 | 1.6 | 1.5746 | 750
Peak21 | 50 | 10 | 7 | 2250 | 30 | 6 | 5.8679 | 150 | [9 empty] | Peak21 | 50 | 10 | 7 | 2250 | 30 | 6 | 5.2711 | 300
Peak21 | 50 | 10 | 7 | 2250 | 35 | 3 | 2.6356 | 300 | [9 empty] | Peak21 | 50 | 10 | 7 | 2250 | 35 | 3 | 2.9813 | 450
Peak21 | 50 | 10 | 7 | 2250 | 40 | 1.6 | 1.4906 | 450 | [9 empty] | Peak21 | 50 | 10 | 7 | 2250 | 40 | 1.6 | 1.463 | 750

## Backup lookup matrix (hidden)
Source group | Capacity | Stack height | Clearance | Operational hours | Background | Acceptable PC | Unique NO2 PC | NO2 Screening distance | Source group | Capacity | Stack height | Clearance | Operational hours | Background | Acceptable PC | Unique NOX PC | NOX Screening distance
Back22 | 5 | 3 | 0 | 100 | 30 | 140 | 64.7822 | 50 | Back22 | 5 | 3 | 0 | 100 | N/A | 45 | 44.7995 | 100
Back23 | 5 | 6 | 3 | 100 | 30 | 140 | 37.9622 | 50 | Back23 | 5 | 6 | 3 | 100 | N/A | 45 | 39.2047 | 100
Back24 | 5 | 10 | 7 | 100 | 30 | 140 | 13.5267 | 0 | Back24 | 5 | 10 | 7 | 100 | N/A | 45 | 24.0541 | 50
Back22 | 5 | 3 | 0 | 100 | 35 | 140 | 64.7822 | 50 | Back22 | 5 | 3 | 0 | 200 | N/A | 45 | 44.7995 | 100
Back23 | 5 | 6 | 3 | 100 | 35 | 140 | 37.9622 | 50 | Back23 | 5 | 6 | 3 | 200 | N/A | 45 | 39.2047 | 100
Back24 | 5 | 10 | 7 | 100 | 35 | 140 | 13.5267 | 0 | Back24 | 5 | 10 | 7 | 200 | N/A | 45 | 24.0541 | 50
Back22 | 5 | 3 | 0 | 100 | 40 | 140 | 64.7822 | 50 | Back22 | 5 | 3 | 0 | 350 | N/A | 0.45 | 0.33682 | 200
Back23 | 5 | 6 | 3 | 100 | 40 | 140 | 37.9622 | 50 | Back23 | 5 | 6 | 3 | 350 | N/A | 0.45 | 0.3112 | 200
Back24 | 5 | 10 | 7 | 100 | 40 | 140 | 13.5267 | 0 | Back24 | 5 | 10 | 7 | 350 | N/A | 0.45 | 0.37488 | 150
Back22 | 5 | 3 | 0 | 200 | 30 | 140 | 74.2077 | 50 | Back22 | 5 | 3 | 0 | 500 | N/A | 0.45 | 0.34241 | 250
Back23 | 5 | 6 | 3 | 200 | 30 | 140 | 44.4747 | 50 | Back23 | 5 | 6 | 3 | 500 | N/A | 0.45 | 0.44457 | 200
Back24 | 5 | 10 | 7 | 200 | 30 | 140 | 16.2765 | 0 | Back24 | 5 | 10 | 7 | 500 | N/A | 0.45 | 0.38209 | 200
Back22 | 5 | 3 | 0 | 200 | 35 | 140 | 74.2077 | 50 | Back22 | 5 | 3 | 0 | 750 | N/A | 0.45 | 0.39064 | 300
Back23 | 5 | 6 | 3 | 200 | 35 | 140 | 44.4747 | 50 | Back23 | 5 | 6 | 3 | 750 | N/A | 0.45 | 0.36566 | 300
Back24 | 5 | 10 | 7 | 200 | 35 | 140 | 16.2765 | 0 | Back24 | 5 | 10 | 7 | 750 | N/A | 0.45 | 0.42579 | 250
Back22 | 5 | 3 | 0 | 200 | 40 | 140 | 74.2077 | 50 | Back1 | 10 | 3 | 0 | 100 | N/A | 45 | 41.1643 | 200
Back23 | 5 | 6 | 3 | 200 | 40 | 140 | 44.4747 | 50 | Back2 | 10 | 6 | 3 | 100 | N/A | 45 | 37.4879 | 200
Back24 | 5 | 10 | 7 | 200 | 40 | 140 | 16.2765 | 0 | Back3 | 10 | 10 | 7 | 100 | N/A | 45 | 39.5709 | 150
Back22 | 5 | 3 | 0 | 350 | 30 | 140 | 78.4602 | 50 | Back1 | 10 | 3 | 0 | 200 | N/A | 45 | 41.1643 | 200
Back23 | 5 | 6 | 3 | 350 | 30 | 140 | 46.7229 | 50 | Back2 | 10 | 6 | 3 | 200 | N/A | 45 | 37.4879 | 200
Back24 | 5 | 10 | 7 | 350 | 30 | 140 | 17.39 | 0 | Back3 | 10 | 10 | 7 | 200 | N/A | 45 | 39.5709 | 150
Back22 | 5 | 3 | 0 | 350 | 35 | 3 | 1.5421 | 50 | Back1 | 10 | 3 | 0 | 350 | N/A | 0.45 | 0.3646 | 300
Back23 | 5 | 6 | 3 | 350 | 35 | 3 | 0.88798 | 50 | Back2 | 10 | 6 | 3 | 350 | N/A | 0.45 | 0.44768 | 250
Back24 | 5 | 10 | 7 | 350 | 35 | 3 | 0.30708 | 0 | Back3 | 10 | 10 | 7 | 350 | N/A | 0.45 | 0.39741 | 250
Back22 | 5 | 3 | 0 | 350 | 40 | 1.6 | 1.5421 | 50 | Back1 | 10 | 3 | 0 | 500 | N/A | 0.45 | 0.41502 | 350
Back23 | 5 | 6 | 3 | 350 | 40 | 1.6 | 0.88798 | 50 | Back2 | 10 | 6 | 3 | 500 | N/A | 0.45 | 0.38852 | 350
Back24 | 5 | 10 | 7 | 350 | 40 | 1.6 | 0.30708 | 0 | Back3 | 10 | 10 | 7 | 500 | N/A | 0.45 | 0.43918 | 300
Back22 | 5 | 3 | 0 | 500 | 30 | 140 | 82.0262 | 50 | Back1 | 10 | 3 | 0 | 750 | N/A | 0.45 | 0.43129 | 450
Back23 | 5 | 6 | 3 | 500 | 30 | 140 | 49.8045 | 50 | Back2 | 10 | 6 | 3 | 750 | N/A | 0.45 | 0.40474 | 450
Back24 | 5 | 10 | 7 | 500 | 30 | 140 | 17.917 | 0 | Back3 | 10 | 10 | 7 | 750 | N/A | 0.45 | 0.43543 | 400
Back22 | 5 | 3 | 0 | 500 | 35 | 3 | 2.2031 | 50 | Back4 | 15 | 3 | 0 | 100 | N/A | 45 | 40.1653 | 250
Back23 | 5 | 6 | 3 | 500 | 35 | 3 | 1.2685 | 50 | Back5 | 15 | 6 | 3 | 100 | N/A | 45 | 36.9352 | 250
Back24 | 5 | 10 | 7 | 500 | 35 | 3 | 0.43869 | 0 | Back6 | 15 | 10 | 7 | 100 | N/A | 45 | 39.1737 | 200
Back22 | 5 | 3 | 0 | 500 | 40 | 1.6 | 0.93806 | 100 | Back4 | 15 | 3 | 0 | 200 | N/A | 45 | 40.1653 | 250
Back23 | 5 | 6 | 3 | 500 | 40 | 1.6 | 1.2685 | 50 | Back5 | 15 | 6 | 3 | 200 | N/A | 45 | 36.9352 | 250
Back24 | 5 | 10 | 7 | 500 | 40 | 1.6 | 0.43869 | 0 | Back6 | 15 | 10 | 7 | 200 | N/A | 45 | 39.1737 | 200
Back22 | 5 | 3 | 0 | 750 | 30 | 140 | 86.1758 | 50 | Back4 | 15 | 3 | 0 | 350 | N/A | 0.45 | 0.3854 | 350
Back23 | 5 | 6 | 3 | 750 | 30 | 140 | 51.5902 | 50 | Back5 | 15 | 6 | 3 | 350 | N/A | 0.45 | 0.36303 | 350
Back24 | 5 | 10 | 7 | 750 | 30 | 140 | 18.3703 | 0 | Back6 | 15 | 10 | 7 | 350 | N/A | 0.45 | 0.41245 | 300
Back22 | 5 | 3 | 0 | 750 | 35 | 3 | 1.4071 | 100 | Back4 | 15 | 3 | 0 | 500 | N/A | 0.45 | 0.3829 | 450
Back23 | 5 | 6 | 3 | 750 | 35 | 3 | 1.9028 | 50 | Back5 | 15 | 6 | 3 | 500 | N/A | 0.45 | 0.42695 | 400
Back24 | 5 | 10 | 7 | 750 | 35 | 3 | 0.65804 | 0 | Back6 | 15 | 10 | 7 | 500 | N/A | 0.45 | 0.39072 | 400
Back22 | 5 | 3 | 0 | 750 | 40 | 1.6 | 1.4071 | 100 | Back4 | 15 | 3 | 0 | 750 | N/A | 0.45 | 0.43037 | 550
Back23 | 5 | 6 | 3 | 750 | 40 | 1.6 | 1.1623 | 100 | Back5 | 15 | 6 | 3 | 750 | N/A | 0.45 | 0.40632 | 550
Back24 | 5 | 10 | 7 | 750 | 40 | 1.6 | 0.65804 | 0 | Back6 | 15 | 10 | 7 | 750 | N/A | 0.45 | 0.42637 | 500
Back1 | 10 | 3 | 0 | 100 | 30 | 140 | 129.5644 | 50 | Back7 | 20 | 3 | 0 | 100 | N/A | 45 | 38.136 | 300
Back2 | 10 | 6 | 3 | 100 | 30 | 140 | 75.9244 | 50 | Back8 | 20 | 6 | 3 | 100 | N/A | 45 | 43.3072 | 250
Back3 | 10 | 10 | 7 | 100 | 30 | 140 | 27.0534 | 0 | Back9 | 20 | 10 | 7 | 100 | N/A | 45 | 37.3321 | 250
Back1 | 10 | 3 | 0 | 100 | 35 | 140 | 129.5644 | 50 | Back7 | 20 | 3 | 0 | 200 | N/A | 45 | 38.136 | 300
Back2 | 10 | 6 | 3 | 100 | 35 | 140 | 75.9244 | 50 | Back8 | 20 | 6 | 3 | 200 | N/A | 45 | 43.3072 | 250
Back3 | 10 | 10 | 7 | 100 | 35 | 140 | 27.0534 | 0 | Back9 | 20 | 10 | 7 | 200 | N/A | 45 | 37.3321 | 250
Back1 | 10 | 3 | 0 | 100 | 40 | 140 | 129.5644 | 50 | Back7 | 20 | 3 | 0 | 350 | N/A | 0.45 | 0.38621 | 400
Back2 | 10 | 6 | 3 | 100 | 40 | 140 | 75.9244 | 50 | Back8 | 20 | 6 | 3 | 350 | N/A | 0.45 | 0.44357 | 350
Back3 | 10 | 10 | 7 | 100 | 40 | 140 | 27.0534 | 0 | Back9 | 20 | 10 | 7 | 350 | N/A | 0.45 | 0.40635 | 350
Back1 | 10 | 3 | 0 | 200 | 30 | 140 | 62.5394 | 100 | Back7 | 20 | 3 | 0 | 500 | N/A | 0.45 | 0.40134 | 500
Back2 | 10 | 6 | 3 | 200 | 30 | 140 | 88.9493 | 50 | Back8 | 20 | 6 | 3 | 500 | N/A | 0.45 | 0.44013 | 450
Back3 | 10 | 10 | 7 | 200 | 30 | 140 | 32.553 | 0 | Back9 | 20 | 10 | 7 | 500 | N/A | 0.45 | 0.40547 | 450
Back1 | 10 | 3 | 0 | 200 | 35 | 140 | 62.5394 | 100 | Back7 | 20 | 3 | 0 | 750 | N/A | 0.45 | 0.4146 | 650
Back2 | 10 | 6 | 3 | 200 | 35 | 140 | 88.9493 | 50 | Back8 | 20 | 6 | 3 | 750 | N/A | 0.45 | 0.43999 | 600
Back3 | 10 | 10 | 7 | 200 | 35 | 140 | 32.553 | 0 | Back9 | 20 | 10 | 7 | 750 | N/A | 0.45 | 0.40567 | 600
Back1 | 10 | 3 | 0 | 200 | 40 | 140 | 62.5394 | 100 | Back10 | 25 | 3 | 0 | 100 | N/A | 45 | 43.1975 | 300
Back2 | 10 | 6 | 3 | 200 | 40 | 140 | 88.9493 | 50 | Back11 | 25 | 6 | 3 | 100 | N/A | 45 | 39.758 | 300
Back3 | 10 | 10 | 7 | 200 | 40 | 140 | 32.553 | 0 | Back12 | 25 | 10 | 7 | 100 | N/A | 45 | 42.3814 | 250
Back1 | 10 | 3 | 0 | 350 | 30 | 140 | 65.6215 | 100 | Back10 | 25 | 3 | 0 | 200 | N/A | 45 | 43.1975 | 300
Back2 | 10 | 6 | 3 | 350 | 30 | 140 | 93.4458 | 50 | Back11 | 25 | 6 | 3 | 200 | N/A | 45 | 39.758 | 300
Back3 | 10 | 10 | 7 | 350 | 30 | 140 | 34.7801 | 0 | Back12 | 25 | 10 | 7 | 200 | N/A | 45 | 42.3814 | 250
Back1 | 10 | 3 | 0 | 350 | 35 | 3 | 1.3133 | 100 | Back10 | 25 | 3 | 0 | 350 | N/A | 0.45 | 0.44794 | 400
Back2 | 10 | 6 | 3 | 350 | 35 | 3 | 1.776 | 50 | Back11 | 25 | 6 | 3 | 350 | N/A | 0.45 | 0.42451 | 400
Back3 | 10 | 10 | 7 | 350 | 35 | 3 | 0.61417 | 0 | Back12 | 25 | 10 | 7 | 350 | N/A | 0.45 | 0.392 | 400
Back1 | 10 | 3 | 0 | 350 | 40 | 1.6 | 1.3133 | 100 | Back10 | 25 | 3 | 0 | 500 | N/A | 0.45 | 0.40724 | 550
Back2 | 10 | 6 | 3 | 350 | 40 | 1.6 | 1.0849 | 100 | Back11 | 25 | 6 | 3 | 500 | N/A | 0.45 | 0.44054 | 500
Back3 | 10 | 10 | 7 | 350 | 40 | 1.6 | 0.61417 | 0 | Back12 | 25 | 10 | 7 | 500 | N/A | 0.45 | 0.40778 | 500
Back1 | 10 | 3 | 0 | 500 | 30 | 140 | 67.2399 | 100 | Back10 | 25 | 3 | 0 | 750 | N/A | 0.45 | 0.43547 | 700
Back2 | 10 | 6 | 3 | 500 | 30 | 140 | 99.6089 | 50 | Back11 | 25 | 6 | 3 | 750 | N/A | 0.45 | 0.41349 | 700
Back3 | 10 | 10 | 7 | 500 | 30 | 140 | 35.834 | 0 | Back12 | 25 | 10 | 7 | 750 | N/A | 0.45 | 0.42438 | 650
Back1 | 10 | 3 | 0 | 500 | 35 | 3 | 1.8761 | 100 | Back13 | 30 | 3 | 0 | 100 | N/A | 45 | 43.7555 | 400
Back2 | 10 | 6 | 3 | 500 | 35 | 3 | 2.5371 | 50 | Back14 | 30 | 6 | 3 | 100 | N/A | 45 | 41.4223 | 400
Back3 | 10 | 10 | 7 | 500 | 35 | 3 | 0.87739 | 0 | Back15 | 30 | 10 | 7 | 100 | N/A | 45 | 44.0896 | 350
Back1 | 10 | 3 | 0 | 500 | 40 | 1.6 | 1.0418 | 150 | Back13 | 30 | 3 | 0 | 200 | N/A | 45 | 43.7555 | 400
Back2 | 10 | 6 | 3 | 500 | 40 | 1.6 | 1.5498 | 100 | Back14 | 30 | 6 | 3 | 200 | N/A | 45 | 41.4223 | 400
Back3 | 10 | 10 | 7 | 500 | 40 | 1.6 | 0.87739 | 0 | Back15 | 30 | 10 | 7 | 200 | N/A | 45 | 44.0896 | 350
Back1 | 10 | 3 | 0 | 750 | 30 | 140 | 68.447 | 100 | Back13 | 30 | 3 | 0 | 350 | N/A | 0.45 | 0.40049 | 550
Back2 | 10 | 6 | 3 | 750 | 30 | 140 | 103.1803 | 50 | Back14 | 30 | 6 | 3 | 350 | N/A | 0.45 | 0.43348 | 500
Back3 | 10 | 10 | 7 | 750 | 30 | 140 | 36.7405 | 0 | Back15 | 30 | 10 | 7 | 350 | N/A | 0.45 | 0.39776 | 500
Back1 | 10 | 3 | 0 | 750 | 35 | 3 | 2.8142 | 100 | Back13 | 30 | 3 | 0 | 500 | N/A | 0.45 | 0.44836 | 650
Back2 | 10 | 6 | 3 | 750 | 35 | 3 | 2.3247 | 100 | Back14 | 30 | 6 | 3 | 500 | N/A | 0.45 | 0.42541 | 650
Back3 | 10 | 10 | 7 | 750 | 35 | 3 | 1.3161 | 0 | Back15 | 30 | 10 | 7 | 500 | N/A | 0.45 | 0.43947 | 600
Back1 | 10 | 3 | 0 | 750 | 40 | 1.6 | 1.5628 | 150 | Back13 | 30 | 3 | 0 | 750 | N/A | 0.45 | 0.41467 | 900
Back2 | 10 | 6 | 3 | 750 | 40 | 1.6 | 1.4024 | 150 | Back14 | 30 | 6 | 3 | 750 | N/A | 0.45 | 0.43083 | 850
Back3 | 10 | 10 | 7 | 750 | 40 | 1.6 | 1.3161 | 0 | Back15 | 30 | 10 | 7 | 750 | N/A | 0.45 | 0.43766 | 800
Back4 | 15 | 3 | 0 | 100 | 30 | 140 | 71.2036 | 100 | Back16 | 40 | 3 | 0 | 100 | N/A | 45 | 40.243 | 500
Back5 | 15 | 6 | 3 | 100 | 30 | 140 | 92.1816 | 50 | Back17 | 40 | 6 | 3 | 100 | N/A | 45 | 43.3756 | 450
Back6 | 15 | 10 | 7 | 100 | 30 | 140 | 32.4453 | 0 | Back18 | 40 | 10 | 7 | 100 | N/A | 45 | 39.6714 | 450
Back4 | 15 | 3 | 0 | 100 | 35 | 140 | 71.2036 | 100 | Back16 | 40 | 3 | 0 | 200 | N/A | 45 | 40.243 | 500
Back5 | 15 | 6 | 3 | 100 | 35 | 140 | 92.1816 | 50 | Back17 | 40 | 6 | 3 | 200 | N/A | 45 | 43.3756 | 450
Back6 | 15 | 10 | 7 | 100 | 35 | 140 | 32.4453 | 0 | Back18 | 40 | 10 | 7 | 200 | N/A | 45 | 39.6714 | 450
Back4 | 15 | 3 | 0 | 100 | 40 | 140 | 71.2036 | 100 | Back16 | 40 | 3 | 0 | 350 | N/A | 0.45 | 0.43277 | 600
Back5 | 15 | 6 | 3 | 100 | 40 | 140 | 92.1816 | 50 | Back17 | 40 | 6 | 3 | 350 | N/A | 0.45 | 0.40996 | 600
Back6 | 15 | 10 | 7 | 100 | 40 | 140 | 32.4453 | 0 | Back18 | 40 | 10 | 7 | 350 | N/A | 0.45 | 0.42735 | 550
Back4 | 15 | 3 | 0 | 200 | 30 | 140 | 81.9539 | 100 | Back16 | 40 | 3 | 0 | 500 | N/A | 0.45 | 0.44852 | 750
Back5 | 15 | 6 | 3 | 200 | 30 | 140 | 111.5607 | 50 | Back17 | 40 | 6 | 3 | 500 | N/A | 0.45 | 0.42685 | 750
Back6 | 15 | 10 | 7 | 200 | 30 | 140 | 40.0179 | 0 | Back18 | 40 | 10 | 7 | 500 | N/A | 0.45 | 0.43626 | 700
Back4 | 15 | 3 | 0 | 200 | 35 | 140 | 81.9539 | 100 | Back16 | 40 | 3 | 0 | 750 | N/A | 0.45 | 0.44106 | 1000
Back5 | 15 | 6 | 3 | 200 | 35 | 140 | 111.5607 | 50 | Back17 | 40 | 6 | 3 | 750 | N/A | 0.45 | 0.42172 | 1000
Back6 | 15 | 10 | 7 | 200 | 35 | 140 | 40.0179 | 0 | Back18 | 40 | 10 | 7 | 750 | N/A | 0.45 | 0.42475 | 950
Back4 | 15 | 3 | 0 | 200 | 40 | 140 | 81.9539 | 100 | Back19 | 50 | 3 | 0 | 100 | N/A | 45 | 41.6624 | 550
Back5 | 15 | 6 | 3 | 200 | 40 | 140 | 111.5607 | 50 | Back20 | 50 | 6 | 3 | 100 | N/A | 45 | 44.138 | 500
Back6 | 15 | 10 | 7 | 200 | 40 | 140 | 40.0179 | 0 | Back21 | 50 | 10 | 7 | 100 | N/A | 45 | 40.4036 | 500
Back4 | 15 | 3 | 0 | 350 | 30 | 140 | 86.3222 | 100 | Back19 | 50 | 3 | 0 | 200 | N/A | 45 | 41.6624 | 550
Back5 | 15 | 6 | 3 | 350 | 30 | 140 | 119.0171 | 50 | Back20 | 50 | 6 | 3 | 200 | N/A | 45 | 44.138 | 500
Back6 | 15 | 10 | 7 | 350 | 30 | 140 | 43.4395 | 0 | Back21 | 50 | 10 | 7 | 200 | N/A | 45 | 40.4036 | 500
Back4 | 15 | 3 | 0 | 350 | 35 | 3 | 1.6811 | 100 | Back19 | 50 | 3 | 0 | 350 | N/A | 0.45 | 0.40554 | 700
Back5 | 15 | 6 | 3 | 350 | 35 | 3 | 2.098 | 50 | Back20 | 50 | 6 | 3 | 350 | N/A | 0.45 | 0.42722 | 650
Back6 | 15 | 10 | 7 | 350 | 35 | 3 | 0.71503 | 0 | Back21 | 50 | 10 | 7 | 350 | N/A | 0.45 | 0.44224 | 600
Back4 | 15 | 3 | 0 | 350 | 40 | 1.6 | 0.95782 | 150 | Back19 | 50 | 3 | 0 | 500 | N/A | 0.45 | 0.43918 | 850
Back5 | 15 | 6 | 3 | 350 | 40 | 1.6 | 1.3776 | 100 | Back20 | 50 | 6 | 3 | 500 | N/A | 0.45 | 0.41889 | 850
Back6 | 15 | 10 | 7 | 350 | 40 | 1.6 | 0.71503 | 0 | Back21 | 50 | 10 | 7 | 500 | N/A | 0.45 | 0.42476 | 800
Back4 | 15 | 3 | 0 | 500 | 30 | 140 | 88.0572 | 100 | Back19 | 50 | 3 | 0 | 750 | N/A | 0.45 | 0.39806 | 1200
Back5 | 15 | 6 | 3 | 500 | 30 | 140 | 121.5557 | 50 | Back20 | 50 | 6 | 3 | 750 | N/A | 0.45 | 0.43336 | 1100
Back6 | 15 | 10 | 7 | 500 | 30 | 140 | 44.8634 | 0 | Back21 | 50 | 10 | 7 | 750 | N/A | 0.45 | 0.40672 | 1100
Back4 | 15 | 3 | 0 | 500 | 35 | 3 | 2.4016 | 100
Back5 | 15 | 6 | 3 | 500 | 35 | 3 | 2.9971 | 50
Back6 | 15 | 10 | 7 | 500 | 35 | 3 | 1.0215 | 0
Back4 | 15 | 3 | 0 | 500 | 40 | 1.6 | 1.3683 | 150
Back5 | 15 | 6 | 3 | 500 | 40 | 1.6 | 1.2221 | 150
Back6 | 15 | 10 | 7 | 500 | 40 | 1.6 | 1.0215 | 0
Back4 | 15 | 3 | 0 | 750 | 30 | 140 | 89.6175 | 100
Back5 | 15 | 6 | 3 | 750 | 30 | 140 | 127.8319 | 50
Back6 | 15 | 10 | 7 | 750 | 30 | 140 | 46.2357 | 0
Back4 | 15 | 3 | 0 | 750 | 35 | 3 | 2.0525 | 150
Back5 | 15 | 6 | 3 | 750 | 35 | 3 | 2.9521 | 100
Back6 | 15 | 10 | 7 | 750 | 35 | 3 | 1.5322 | 0
Back4 | 15 | 3 | 0 | 750 | 40 | 1.6 | 1.34 | 200
Back5 | 15 | 6 | 3 | 750 | 40 | 1.6 | 1.2373 | 200
Back6 | 15 | 10 | 7 | 750 | 40 | 1.6 | 1.4597 | 150
Back7 | 20 | 3 | 0 | 100 | 30 | 140 | 86.1256 | 100
Back8 | 20 | 6 | 3 | 100 | 30 | 140 | 103.6511 | 50
Back9 | 20 | 10 | 7 | 100 | 30 | 140 | 36.1767 | 0
Back7 | 20 | 3 | 0 | 100 | 35 | 140 | 86.1256 | 100
Back8 | 20 | 6 | 3 | 100 | 35 | 140 | 103.6511 | 50
Back9 | 20 | 10 | 7 | 100 | 35 | 140 | 36.1767 | 0
Back7 | 20 | 3 | 0 | 100 | 40 | 140 | 86.1256 | 100
Back8 | 20 | 6 | 3 | 100 | 40 | 140 | 103.6511 | 50
Back9 | 20 | 10 | 7 | 100 | 40 | 140 | 36.1767 | 0
Back7 | 20 | 3 | 0 | 200 | 30 | 140 | 99.3157 | 100
Back8 | 20 | 6 | 3 | 200 | 30 | 140 | 128.6274 | 50
Back9 | 20 | 10 | 7 | 200 | 30 | 140 | 45.4394 | 0
Back7 | 20 | 3 | 0 | 200 | 35 | 140 | 99.3157 | 100
Back8 | 20 | 6 | 3 | 200 | 35 | 140 | 128.6274 | 50
Back9 | 20 | 10 | 7 | 200 | 35 | 140 | 45.4394 | 0
Back7 | 20 | 3 | 0 | 200 | 40 | 140 | 99.3157 | 100
Back8 | 20 | 6 | 3 | 200 | 40 | 140 | 128.6274 | 50
Back9 | 20 | 10 | 7 | 200 | 40 | 140 | 45.4394 | 0
Back7 | 20 | 3 | 0 | 350 | 30 | 140 | 104.063 | 100
Back8 | 20 | 6 | 3 | 350 | 30 | 140 | 89.9129 | 100
Back9 | 20 | 10 | 7 | 350 | 30 | 140 | 50.1476 | 0
Back7 | 20 | 3 | 0 | 350 | 35 | 3 | 1.9819 | 100
Back8 | 20 | 6 | 3 | 350 | 35 | 3 | 2.3281 | 100
Back9 | 20 | 10 | 7 | 350 | 35 | 3 | 0.78448 | 0
Back7 | 20 | 3 | 0 | 350 | 40 | 1.6 | 1.1519 | 150
Back8 | 20 | 6 | 3 | 350 | 40 | 1.6 | 1.0241 | 150
Back9 | 20 | 10 | 7 | 350 | 40 | 1.6 | 0.78448 | 0
Back7 | 20 | 3 | 0 | 500 | 30 | 140 | 106.6908 | 100
Back8 | 20 | 6 | 3 | 500 | 30 | 140 | 91.9159 | 100
Back9 | 20 | 10 | 7 | 500 | 30 | 140 | 52.5735 | 0
Back7 | 20 | 3 | 0 | 500 | 35 | 3 | 2.8313 | 100
Back8 | 20 | 6 | 3 | 500 | 35 | 3 | 2.3048 | 100
Back9 | 20 | 10 | 7 | 500 | 35 | 3 | 1.1207 | 0
Back7 | 20 | 3 | 0 | 500 | 40 | 1.6 | 1.0845 | 200
Back8 | 20 | 6 | 3 | 500 | 40 | 1.6 | 1.463 | 150
Back9 | 20 | 10 | 7 | 500 | 40 | 1.6 | 1.1207 | 0
Back7 | 20 | 3 | 0 | 750 | 30 | 140 | 108.2959 | 100
Back8 | 20 | 6 | 3 | 750 | 30 | 140 | 93.2736 | 100
Back9 | 20 | 10 | 7 | 750 | 30 | 140 | 54.4547 | 0
Back7 | 20 | 3 | 0 | 750 | 35 | 3 | 2.4683 | 150
Back8 | 20 | 6 | 3 | 750 | 35 | 3 | 2.1945 | 150
Back9 | 20 | 10 | 7 | 750 | 35 | 3 | 1.681 | 0
Back7 | 20 | 3 | 0 | 750 | 40 | 1.6 | 1.1649 | 250
Back8 | 20 | 6 | 3 | 750 | 40 | 1.6 | 1.498 | 200
Back9 | 20 | 10 | 7 | 750 | 40 | 1.6 | 1.2795 | 200
Back10 | 25 | 3 | 0 | 100 | 30 | 140 | 98.5561 | 100
Back11 | 25 | 6 | 3 | 100 | 30 | 140 | 112.3447 | 50
Back12 | 25 | 10 | 7 | 100 | 30 | 140 | 38.2875 | 0
Back10 | 25 | 3 | 0 | 100 | 35 | 140 | 98.5561 | 100
Back11 | 25 | 6 | 3 | 100 | 35 | 140 | 112.3447 | 50
Back12 | 25 | 10 | 7 | 100 | 35 | 140 | 38.2875 | 0
Back10 | 25 | 3 | 0 | 100 | 40 | 140 | 98.5561 | 100
Back11 | 25 | 6 | 3 | 100 | 40 | 140 | 112.3447 | 50
Back12 | 25 | 10 | 7 | 100 | 40 | 140 | 38.2875 | 0
Back10 | 25 | 3 | 0 | 200 | 30 | 140 | 114.5224 | 100
Back11 | 25 | 6 | 3 | 200 | 30 | 140 | 98.0108 | 100
Back12 | 25 | 10 | 7 | 200 | 30 | 140 | 49.5337 | 0
Back10 | 25 | 3 | 0 | 200 | 35 | 140 | 114.5224 | 100
Back11 | 25 | 6 | 3 | 200 | 35 | 140 | 98.0108 | 100
Back12 | 25 | 10 | 7 | 200 | 35 | 140 | 49.5337 | 0
Back10 | 25 | 3 | 0 | 200 | 40 | 140 | 114.5224 | 100
Back11 | 25 | 6 | 3 | 200 | 40 | 140 | 98.0108 | 100
Back12 | 25 | 10 | 7 | 200 | 40 | 140 | 49.5337 | 0
Back10 | 25 | 3 | 0 | 350 | 30 | 140 | 120.5057 | 100
Back11 | 25 | 6 | 3 | 350 | 30 | 140 | 103.4526 | 100
Back12 | 25 | 10 | 7 | 350 | 30 | 140 | 55.7574 | 0
Back10 | 25 | 3 | 0 | 350 | 35 | 3 | 2.234 | 100
Back11 | 25 | 6 | 3 | 350 | 35 | 3 | 2.4954 | 100
Back12 | 25 | 10 | 7 | 350 | 35 | 3 | 0.83303 | 0
Back10 | 25 | 3 | 0 | 350 | 40 | 1.6 | 1.3195 | 150
Back11 | 25 | 6 | 3 | 350 | 40 | 1.6 | 1.168 | 150
Back12 | 25 | 10 | 7 | 350 | 40 | 1.6 | 0.83303 | 0
Back10 | 25 | 3 | 0 | 500 | 30 | 140 | 123.1853 | 100
Back11 | 25 | 6 | 3 | 500 | 30 | 140 | 106.3199 | 100
Back12 | 25 | 10 | 7 | 500 | 30 | 140 | 58.8301 | 0
Back10 | 25 | 3 | 0 | 500 | 35 | 3 | 1.885 | 150
Back11 | 25 | 6 | 3 | 500 | 35 | 3 | 2.5804 | 100
Back12 | 25 | 10 | 7 | 500 | 35 | 3 | 1.19 | 0
Back10 | 25 | 3 | 0 | 500 | 40 | 1.6 | 1.2527 | 200
Back11 | 25 | 6 | 3 | 500 | 40 | 1.6 | 1.1506 | 200
Back12 | 25 | 10 | 7 | 500 | 40 | 1.6 | 1.3154 | 150
Back10 | 25 | 3 | 0 | 750 | 30 | 140 | 125.3766 | 100
Back11 | 25 | 6 | 3 | 750 | 30 | 140 | 107.997 | 100
Back12 | 25 | 10 | 7 | 750 | 30 | 140 | 61.4183 | 0
Back10 | 25 | 3 | 0 | 750 | 35 | 3 | 2.8275 | 150
Back11 | 25 | 6 | 3 | 750 | 35 | 3 | 2.503 | 150
Back12 | 25 | 10 | 7 | 750 | 35 | 3 | 1.7851 | 0
Back10 | 25 | 3 | 0 | 750 | 40 | 1.6 | 1.3514 | 250
Back11 | 25 | 6 | 3 | 750 | 40 | 1.6 | 1.2639 | 250
Back12 | 25 | 10 | 7 | 750 | 40 | 1.6 | 1.4702 | 200
Back13 | 30 | 3 | 0 | 100 | 30 | 140 | 82.4285 | 150
Back14 | 30 | 6 | 3 | 100 | 30 | 140 | 120.4584 | 100
Back15 | 30 | 10 | 7 | 100 | 30 | 140 | 58.0639 | 0
Back13 | 30 | 3 | 0 | 100 | 35 | 140 | 82.4285 | 150
Back14 | 30 | 6 | 3 | 100 | 35 | 140 | 120.4584 | 100
Back15 | 30 | 10 | 7 | 100 | 35 | 140 | 58.0639 | 0
Back13 | 30 | 3 | 0 | 100 | 40 | 140 | 82.4285 | 150
Back14 | 30 | 6 | 3 | 100 | 40 | 140 | 120.4584 | 100
Back15 | 30 | 10 | 7 | 100 | 40 | 140 | 58.0639 | 0
Back13 | 30 | 3 | 0 | 200 | 30 | 140 | 96.7319 | 150
Back14 | 30 | 6 | 3 | 200 | 30 | 140 | 138.9945 | 100
Back15 | 30 | 10 | 7 | 200 | 30 | 140 | 70.3164 | 0
Back13 | 30 | 3 | 0 | 200 | 35 | 140 | 96.7319 | 150
Back14 | 30 | 6 | 3 | 200 | 35 | 140 | 138.9945 | 100
Back15 | 30 | 10 | 7 | 200 | 35 | 140 | 70.3164 | 0
Back13 | 30 | 3 | 0 | 200 | 40 | 140 | 96.7319 | 150
Back14 | 30 | 6 | 3 | 200 | 40 | 140 | 138.9945 | 100
Back15 | 30 | 10 | 7 | 200 | 40 | 140 | 70.3164 | 0
Back13 | 30 | 3 | 0 | 350 | 30 | 140 | 103.5482 | 150
Back14 | 30 | 6 | 3 | 350 | 30 | 140 | 94.3954 | 150
Back15 | 30 | 10 | 7 | 350 | 30 | 140 | 75.334 | 0
Back13 | 30 | 3 | 0 | 350 | 35 | 3 | 1.9093 | 150
Back14 | 30 | 6 | 3 | 350 | 35 | 3 | 2.7327 | 150
Back15 | 30 | 10 | 7 | 350 | 35 | 3 | 1.3581 | 0
Back13 | 30 | 3 | 0 | 350 | 40 | 1.6 | 1.2459 | 200
Back14 | 30 | 6 | 3 | 350 | 40 | 1.6 | 1.1509 | 200
Back15 | 30 | 10 | 7 | 350 | 40 | 1.6 | 1.3518 | 150
Back13 | 30 | 3 | 0 | 500 | 30 | 140 | 106.9999 | 150
Back14 | 30 | 6 | 3 | 500 | 30 | 140 | 96.2762 | 150
Back15 | 30 | 10 | 7 | 500 | 30 | 140 | 78.114 | 0
Back13 | 30 | 3 | 0 | 500 | 35 | 3 | 2.7276 | 150
Back14 | 30 | 6 | 3 | 500 | 35 | 3 | 2.4335 | 150
Back15 | 30 | 10 | 7 | 500 | 35 | 3 | 1.9402 | 0
Back13 | 30 | 3 | 0 | 500 | 40 | 1.6 | 1.2699 | 250
Back14 | 30 | 6 | 3 | 500 | 40 | 1.6 | 1.1902 | 250
Back15 | 30 | 10 | 7 | 500 | 40 | 1.6 | 1.4083 | 200
Back13 | 30 | 3 | 0 | 750 | 30 | 140 | 109.5955 | 150
Back14 | 30 | 6 | 3 | 750 | 30 | 140 | 98.391 | 150
Back15 | 30 | 10 | 7 | 750 | 30 | 140 | 79.5777 | 0
Back13 | 30 | 3 | 0 | 750 | 35 | 3 | 2.6698 | 200
Back14 | 30 | 6 | 3 | 750 | 35 | 3 | 2.4663 | 200
Back15 | 30 | 10 | 7 | 750 | 35 | 3 | 2.8968 | 150
Back13 | 30 | 3 | 0 | 750 | 40 | 1.6 | 1.4474 | 300
Back14 | 30 | 6 | 3 | 750 | 40 | 1.6 | 1.3639 | 300
Back15 | 30 | 10 | 7 | 750 | 40 | 1.6 | 1.5877 | 250
Back16 | 40 | 3 | 0 | 100 | 30 | 140 | 101.1871 | 150
Back17 | 40 | 6 | 3 | 100 | 30 | 140 | 93.1063 | 150
Back18 | 40 | 10 | 7 | 100 | 30 | 140 | 64.4007 | 0
Back16 | 40 | 3 | 0 | 100 | 35 | 140 | 101.1871 | 150
Back17 | 40 | 6 | 3 | 100 | 35 | 140 | 93.1063 | 150
Back18 | 40 | 10 | 7 | 100 | 35 | 140 | 64.4007 | 0
Back16 | 40 | 3 | 0 | 100 | 40 | 140 | 101.1871 | 150
Back17 | 40 | 6 | 3 | 100 | 40 | 140 | 93.1063 | 150
Back18 | 40 | 10 | 7 | 100 | 40 | 140 | 64.4007 | 0
Back16 | 40 | 3 | 0 | 200 | 30 | 140 | 118.5432 | 150
Back17 | 40 | 6 | 3 | 200 | 30 | 140 | 107.9638 | 150
Back18 | 40 | 10 | 7 | 200 | 30 | 140 | 80.2004 | 0
Back16 | 40 | 3 | 0 | 200 | 35 | 140 | 118.5432 | 150
Back17 | 40 | 6 | 3 | 200 | 35 | 140 | 107.9638 | 150
Back18 | 40 | 10 | 7 | 200 | 35 | 140 | 80.2004 | 0
Back16 | 40 | 3 | 0 | 200 | 40 | 140 | 118.5432 | 150
Back17 | 40 | 6 | 3 | 200 | 40 | 140 | 107.9638 | 150
Back18 | 40 | 10 | 7 | 200 | 40 | 140 | 80.2004 | 0
Back16 | 40 | 3 | 0 | 350 | 30 | 140 | 125.5506 | 150
Back17 | 40 | 6 | 3 | 350 | 30 | 140 | 114.3576 | 150
Back18 | 40 | 10 | 7 | 350 | 30 | 140 | 87.0677 | 0
Back16 | 40 | 3 | 0 | 350 | 35 | 3 | 2.296 | 150
Back17 | 40 | 6 | 3 | 350 | 35 | 3 | 2.0385 | 150
Back18 | 40 | 10 | 7 | 350 | 35 | 3 | 1.4977 | 0
Back16 | 40 | 3 | 0 | 350 | 40 | 1.6 | 1.5127 | 200
Back17 | 40 | 6 | 3 | 350 | 40 | 1.6 | 1.3932 | 200
Back18 | 40 | 10 | 7 | 350 | 40 | 1.6 | 1.1898 | 200
Back16 | 40 | 3 | 0 | 500 | 30 | 140 | 128.0818 | 150
Back17 | 40 | 6 | 3 | 500 | 30 | 140 | 116.9031 | 150
Back18 | 40 | 10 | 7 | 500 | 30 | 140 | 91.2198 | 0
Back16 | 40 | 3 | 0 | 500 | 35 | 3 | 2.161 | 200
Back17 | 40 | 6 | 3 | 500 | 35 | 3 | 2.9122 | 150
Back18 | 40 | 10 | 7 | 500 | 35 | 3 | 2.1396 | 0
Back16 | 40 | 3 | 0 | 500 | 40 | 1.6 | 1.5476 | 250
Back17 | 40 | 6 | 3 | 500 | 40 | 1.6 | 1.4502 | 250
Back18 | 40 | 10 | 7 | 500 | 40 | 1.6 | 1.2882 | 250
Back16 | 40 | 3 | 0 | 750 | 30 | 140 | 131.3007 | 150
Back17 | 40 | 6 | 3 | 750 | 30 | 140 | 118.9367 | 150
Back18 | 40 | 10 | 7 | 750 | 30 | 140 | 94.3929 | 0
Back16 | 40 | 3 | 0 | 750 | 35 | 3 | 2.3215 | 250
Back17 | 40 | 6 | 3 | 750 | 35 | 3 | 2.9855 | 200
Back18 | 40 | 10 | 7 | 750 | 35 | 3 | 2.5496 | 200
Back16 | 40 | 3 | 0 | 750 | 40 | 1.6 | 1.4033 | 350
Back17 | 40 | 6 | 3 | 750 | 40 | 1.6 | 1.3278 | 350
Back18 | 40 | 10 | 7 | 750 | 40 | 1.6 | 1.5117 | 300
Back19 | 50 | 3 | 0 | 100 | 30 | 140 | 117.4908 | 150
Back20 | 50 | 6 | 3 | 100 | 30 | 140 | 107.4483 | 150
Back21 | 50 | 10 | 7 | 100 | 30 | 140 | 69.2083 | 0
Back19 | 50 | 3 | 0 | 100 | 35 | 140 | 117.4908 | 150
Back20 | 50 | 6 | 3 | 100 | 35 | 140 | 107.4483 | 150
Back21 | 50 | 10 | 7 | 100 | 35 | 140 | 69.2083 | 0
Back19 | 50 | 3 | 0 | 100 | 40 | 140 | 117.4908 | 150
Back20 | 50 | 6 | 3 | 100 | 40 | 140 | 107.4483 | 150
Back21 | 50 | 10 | 7 | 100 | 40 | 140 | 69.2083 | 0
Back19 | 50 | 3 | 0 | 200 | 30 | 140 | 136.9732 | 150
Back20 | 50 | 6 | 3 | 200 | 30 | 140 | 125.9076 | 150
Back21 | 50 | 10 | 7 | 200 | 30 | 140 | 88.6921 | 0
Back19 | 50 | 3 | 0 | 200 | 35 | 140 | 136.9732 | 150
Back20 | 50 | 6 | 3 | 200 | 35 | 140 | 125.9076 | 150
Back21 | 50 | 10 | 7 | 200 | 35 | 140 | 88.6921 | 0
Back19 | 50 | 3 | 0 | 200 | 40 | 140 | 136.9732 | 150
Back20 | 50 | 6 | 3 | 200 | 40 | 140 | 125.9076 | 150
Back21 | 50 | 10 | 7 | 200 | 40 | 140 | 88.6921 | 0
Back19 | 50 | 3 | 0 | 350 | 30 | 140 | 101.6767 | 200
Back20 | 50 | 6 | 3 | 350 | 30 | 140 | 132.3707 | 150
Back21 | 50 | 10 | 7 | 350 | 30 | 140 | 109.7022 | 150
Back19 | 50 | 3 | 0 | 350 | 35 | 3 | 2.6302 | 200
Back20 | 50 | 6 | 3 | 350 | 35 | 3 | 2.3241 | 150
Back21 | 50 | 10 | 7 | 350 | 35 | 3 | 1.5971 | 150
Back19 | 50 | 3 | 0 | 350 | 40 | 1.6 | 1.257 | 250
Back20 | 50 | 6 | 3 | 350 | 40 | 1.6 | 1.1762 | 250
Back21 | 50 | 10 | 7 | 350 | 40 | 1.6 | 1.3668 | 200
Back19 | 50 | 3 | 0 | 500 | 30 | 140 | 104.5657 | 200
Back20 | 50 | 6 | 3 | 500 | 30 | 140 | 134.898 | 150
Back21 | 50 | 10 | 7 | 500 | 30 | 140 | 111.5404 | 150
Back19 | 50 | 3 | 0 | 500 | 35 | 3 | 2.4962 | 200
Back20 | 50 | 6 | 3 | 500 | 35 | 3 | 2.293 | 200
Back21 | 50 | 10 | 7 | 500 | 35 | 3 | 2.608 | 150
Back19 | 50 | 3 | 0 | 500 | 40 | 1.6 | 1.3668 | 300
Back20 | 50 | 6 | 3 | 500 | 40 | 1.6 | 1.291 | 300
Back21 | 50 | 10 | 7 | 500 | 40 | 1.6 | 1.4906 | 250
Back19 | 50 | 3 | 0 | 750 | 30 | 140 | 106.6131 | 200
Back20 | 50 | 6 | 3 | 750 | 30 | 140 | 137.4222 | 150
Back21 | 50 | 10 | 7 | 750 | 30 | 140 | 113.3685 | 150
Back19 | 50 | 3 | 0 | 750 | 35 | 3 | 2.6935 | 250
Back20 | 50 | 6 | 3 | 750 | 35 | 3 | 2.5205 | 250
Back21 | 50 | 10 | 7 | 750 | 35 | 3 | 2.929 | 200
Back19 | 50 | 3 | 0 | 750 | 40 | 1.6 | 1.3399 | 400
Back20 | 50 | 6 | 3 | 750 | 40 | 1.6 | 1.5449 | 350
Back21 | 50 | 10 | 7 | 750 | 40 | 1.6 | 1.4195 | 350

## Help
BUILDINGS THAT COULD AFFECT DISPERSION
All buildings that could affect dispersion need to be considered during screening. This includes the building on which the stack is located. Buildings that could affect dispersion from a stack are any building that is both: • within 5L of the stack • has a height more than 40% of the stack height For each building 'L' is the lowest of either: • the height of the building • the maximum projected width, which is the greatest width between 2 points (for example opposing corners of a roof) Where there are multiple buildings that could affect dispersion, they should be combined into a simplified block. The height of the simplified block should be set to the tallest building.
Example 1
A 20m stack is located on a 17m building (Building A). There is another 19m high building nearby, 14m from the stack (Building B).
| Building A | Building B
Height (m) | 17 | 19
Length (m) | 20 | 30
Width (m) | 10 | 20
Max projected width (m) | 22.3607 | 36.0555
L (m) | 17 | 19
5L (m) | 85 | 95
Distance from stack (m) | 0 | 14
Building height/stack height | 85% | 95%
Figure 1 - Building A and B affect dispersion from 20m stack (edited screenshot from BREEZE Downwash Analyst)
The stack is located on Building A and the building height is more than 40% of the stack height. Building A will affect dispersion from the stack. Building B is within 5L and has height more than 40% of the stack height. Building B will also affect dispersion from the stack. Building A and B need to be combined into a simplified block with a height equal to Building B, since this is the tallest of the two buildings that affect dispersion from the stack.
Combined simplified block building
Height (m) | 19
Length (m) | 53
Width (m) | 20
Example 2
A 20m stack is located on a 17m building (Building A). There is another 7m high building nearby, 14m from the stack (Building B).
| Building A | Building B
Height (m) | 17 | 7
Length (m) | 20 | 30
Width (m) | 10 | 20
Max projected width (m) | 22.3607 | 36.0555
L (m) | 17 | 7
5L (m) | 85 | 35
Distance from stack (m) | 0 | 14
Building height/stack height | 85% | 35%
Figure 2 - Building B too low to affect dispersion from 20m stack (edited screenshot from BREEZE Downwash Analyst)
The stack is located on Building A and the building height is more than 40% of the stack height. Building A will affect dispersion from the stack. Building B is within 5L, however its height is less than 40% of the stack height. Building B will not affect dispersion from the stack and can be ignored. Building A dimensions need to be used for screening.
Example 3
A 20m stack is located on a 17m building (Building A). There is another 19m high building nearby, 99m from the stack (Building B).
| Building A | Building B
Height (m) | 17 | 19
Length (m) | 20 | 30
Width (m) | 10 | 20
Max projected width (m) | 22.3607 | 36.0555
L (m) | 17 | 19
5L (m) | 85 | 95
Distance from stack (m) | 0 | 99
Building height/stack height | 85% | 95%
Figure 3 - Building B too far away to affect dispersion from 20m stack (edited screenshot from BREEZE Downwash Analyst)
The stack is located on Building A and the building height is more than 40% of the stack height. Building A will affect dispersion from the stack. Building B is beyond 5L, despite its height being more than 40% of the stack height. Building B will not affect dispersion from the stack and can be ignored. Building A dimensions need to be used for screening.
RELEVANT PUBLIC EXPOSURE
Sensitive human health receptors are located where there is relevant public exposure. Relevant public exposure are locations where members of the public have access, are regularly present and can be exposed for a significant portion of the averaging time of the standard. The nitrogen dioxide standards are 40µg/m3 as an annual mean, and 200µg/m3 as an hourly mean, not to be exceeded more than 18 times (hours) per calendar year. These standards do not apply where health and safety at work provisions exist and where members of the public do not have access.
Annual mean exposure
Example locations of annual mean public exposure include, but are not limited to: residential properties, schools, hospitals and cares homes.
Hourly mean exposure
Example locations of hourly mean public exposure include, but are not limited to: residential properties, schools, hospitals, cares homes, busy shopping streets, bus stations and railway stations that are not fully enclosed, and car parks where the public are reasonably expected to spend an hour or more.
Roadside locations
Public exposure can occur at roadside and non-roadside locations. At roadside locations road traffic sources lead increased backgrounds compared to the baseline backgrounds away from busy roads. Examples of roadside locations and public exposure within 15m of the road include: • Narrow congested streets with residential properties close to the kerbs (5,000 vehicles/day) • Busy streets where people may spend 1 hour or more close to traffic (10,000 vehicles/day) • Junctions (10,000 vehicles/day) • Bus and coach stations, not fully enclosed (2,500 movements/day) Traffic flow data should be available for the major road networks in urban areas from the relevant local authority, as this data is needed to conduct their Local Air Quality Management Assessments.