## Blue Haze IBA BAT
Blue haze IBA Treatment Facility BAT Assessment based on BAT Conclusions for Waste Incineration dated 3 December 2019 and the supporting UK Interpretation Document V0.28 dated 30/09/21
Permit no. | EPR/BU5208IJ | Operator: Veolia ES Landfill Ltd | Facility name: Blue haze IBA Treatment Facility
BAT No. | Topic | Brief Description | BAT | Relevant to IBA treatment? | Extent to which the installation currently complies with requirement of the BAT conclusion | Any further supporting information | Text for drop down boxes - these will be hidden in the final version
1 | EMS | Improve overall performance via use of a compliant EMS. | Implement and adhere to an EMS that incorporates key features identified. | Yes | There is an EMS in place that complies with all the points listed in BAT 1 | Yes we have an EMS, summary provided as a seperate document in the application | Select option and/or add site specific text | There is an EMS in place that complies with all the points listed in BAT 1 | The EMS meets the requirements of BAT 1 with the exception of [list elements] and the EMS will be updated by 03/12/23 to ensure that it meets BAT 1
2 | Energy efficiency | Determine gross electrical efficiency, gross energy efficiency or boiler efficiency (depending on plant type). | Original performance test results should remain valid provided no major modifications which could affect the energy efficiency of the plant e.g. boiler or steam turbine replacement (periodic maintenance including replacement of boiler tubes does not count as major modification). Otherwise if modified or original tests results not available, energy efficiency can be calculated using long-term data (e.g. using the methodology set out in the Ricardo R1 guidance on 5-year boiler efficiency reassessments). | No | Select option and/or add site specific text |  | Select option and/or add site specific text | Original performance test dated […………….] is still valid | Energy efficiency has been calculated using long term data derived using Ricardo R1 guidance on 5-year boiler efficiency reassessment. | Energy efficiency has been calculated using [insert brief description of method used] and report describing how it was calculated is attached [insert document reference]. | Energy efficiency has not been calculated. A test will be carried out before 03/12/23 using long term data derived using Ricardo R1 guidance on 5-year boiler efficiency reassessment. | Energy efficiency has not been calculated. A test will be carried out before 03/12/23 using [insert brief description of method to be used] and report describing how it will be calculated is attached [insert document reference].
3 | Process Monitoring | Monitor key process parameters for emissions to air and water specified in the corresponding table. | Monitoring of specified process parameters. | Yes | Process monitoring is carried out in line with BAT 3 requirements for the following relevant parameters flow, pH and conductivity | Excess rainwater run-off only. Periodic sampling before tankering off site will be conducted of relevant parameters. Volume exported by tanker will be recorded. | Select option and/or add site specific text | Process monitoring is carried out in line with BAT 3 requirements for the following relevant parameters [list parameters] | Process monitoring is carried out in line with BAT 3 requirements for the following relevant parameters [list parameters] except for [list parameters] which will be in place by 03/12/23.
4 | Air emissions monitoring | Monitor emissions to air with at least the frequency in the corresponding table and in accordance with the EN standards. | Monitor emissions to air with at least the frequency in the corresponding table and in accordance with the EN standards. | No | Select option and/or add site specific text |  | Select option and/or add site specific text | Monitoring is carried out in line with BAT 4 requirements | Monitoring is carried out in line with BAT 4 requirements except for [list parameters] which will be in place by 03/12/23
| PBDD/F | Monitor emissions to air of brominated dioxins and furans periodically if required. | Monitor PBDD/F if waste streams known to contain brominated flame retardants are burned. | No | Select option and/or add site specific text |  | Select option and/or add site specific text | PBDD/F monitoring is not required as no waste containing brominated flame retardants are/will be burned | The plant burns municipal waste or similar and therefore PBDD/F monitoring will be carried out from 01/01/23 where possible. | The following waste types could contain brominated flame retardants: {list waste types] and so PBDD/F monitoring will be carried out from 01/01/23 where possible. | The plant may burn wastes containing brominated flame retardants in future, in which case PBDD/F monitoring will be carried out if necessary from 01/01/23 where possible.
| PCDD/F | Monitor emissions to air of dioxins and furans using a continuous sampler if required. | Monitor emissions to air of dioxins and furans using a continuous sampler if required, unless emissions are sufficiently stable (see PCDD/F monitoring protocol). | No | Select option and/or add site specific text |  | Select option and/or add site specific text | Continuous PCDD/F sampling (long term monitoring) is already installed and is operational | No attempt will be made to demonstrate that emissions of PCDD/F are sufficiently stable, and continuous sampling (long-term monitoring) will be installed by 03/12/23. | Attempts will be made to demonstrate via the PCCD/F Monitoring Protocol that emissions to air of PCDD/F are sufficiently stable and that a continuous sampler (long-term monitoring) is not required by 03/12/23; if these are unsuccessful, continuous sampling will be installed as soon as reasonably practical.
| Mercury | Monitor emissions to air of mercury using continuous monitoring if required. | Monitor emissions to air of mercury using continuous monitoring, unless emissions can be proven to be low and stable (see Mercury monitoring protocol). | No | Select option and/or add site specific text |  | Select option and/or add site specific text | Continuous mercury monitoring is already installed and is operational | No attempt will be made to demonstrate that emissions of mercury are low and stable, and continuous monitoring will be installed by 03/12/23. | Attempts will be made to demonstrate via the Mercury Monitoring Protocol that emissions to air of mercury are low and stable and that a continuous sampler is not required by 03/12/23; if these are unsuccessful, continuous monitoring will be installed as soon as reasonably practical.
5 | OTNOC monitoring | Appropriately monitor emissions during OTNOC. | Monitor PCCD/F and dioxin-like PCB mass emissions during a planned start-up and shut-down following the successful commissioning of the plant; already-operational plants must carry out this monitoring every 3 years; emissions profiles of continuously monitored pollutants must also be established following successful commissioning and for existing plants; consider further monitoring for plants that use abatement-system bypasses during start-up and/or shut-down. | No | Select option and/or add site specific text |  | Select option and/or add site specific text | Plant has been successfully commissioned, or is likely to be before 03/12/23. Emissions profiles of continuously monitored pollutants have been established during start-up and shut-down or will be established by 03/12/23. Monitoring of PCCD/F and dioxin-like PCB mass emissions during a planned start-up and shut-down will be carried within 3 years of 03/12/23. [Delete the following if not applicable] The plant is also fitted with an abatement bypass for start-up and the following monitoring is proposed during start-up [provide detail]. | Plant is likely to be commissioned after 03/12/23. Emissions profiles for continuously monitored pollutants will be established during start-up and shut-down following successful commissioning. Monitoring of PCCD/F and dioxin-like PCB mass emissions during a planned start-up and shut-down will also be carried out following the successful commissioning of the plant. [Delete the following if not applicable] The plant is also fitted with an abatement bypass for start-up [and shut down] and the following monitoring is proposed during start-up [and shut-down] [list parameters].
6 | Water emissions monitoring | Monitor emissions from FGC and/or bottom ash treatment. | Monitor to frequencies and standards in corresponding table. | Yes | Monitoring is carried out in line with BAT 6 requirements for bottom ash treatment | No emissions to water. Emissions to sewer only via tanker. Sampling monthly when exporting water via tanker from site. No samples will be taken during months when no water is removed from site. | Select option and/or add site specific text | Not applicable as no emissions to water from FGC or bottom ash treatment. | Monitoring is carried out in line with BAT 6 requirements for [FGC/bottom ash treatment] | Monitoring is carried out in line with BAT 6 requirements for [FGC/bottom ash treatment] except for [list parameters] which will be in place by 03/12/23
|  |  | Reduced monitoring frequency permitted if emissions can be shown to be sufficiently stable. | Yes | Not applicable as no data currently available. Applicablilty will be reviewed following initial test results. |  | Select option and/or add site specific text | Not applicable as no emissions to water from FGC or bottom ash treatment. | Emissions are sufficiently stable based on historic monitoring data and will be monitored at reduced frequency - see monitoring data attached [insert document reference] | Emissions not sufficiently stable based on historic monitoring data and will be monitored at reduced frequency.
7 | Ash monitoring | Monitor LOI or TOI content of bottom ash. | To frequencies and standards in corresponding table. | No | Select option and/or add site specific text |  | Select option and/or add site specific text | Monitoring carried out for LOI | Monitoring carried out for TOC
8 | POP monitoring | For hazardous waste containing POPs, monitor POP content of waste streams (applicable to dedicated hazardous waste incinerators only). | After commissioning and then after significant change that could affect POP content. | No | Select option and/or add site specific text |  | Select option and/or add site specific text | Not applicable - plant is not a dedicated hazardous waste incinerator | Not applicable - plant is a dedicated hazardous waste incinerator, but POP content determination is not required because of the criteria listed under BAT 8 (see attached evidence). | Applicable - necessary POP content determination will be carried out after 03/12/23
9 | Waste input controls | Pre-acceptance / acceptance procedures | Use all techniques (a) to (c) in corresponding table, and where relevant (d), (e) and (f). | No | Select option and/or add site specific text |  | Select option and/or add site specific text | Techniques set out in BAT 9 (a)-(c) are in place. Techniques (d)-(f) are not relevant. | Techniques set out in BAT 9 (a)-(c) will be place by 03/12/23. Techniques (d)-(f) are not relevant. | Techniques set out in BAT 9 (a)-(c) are in place. Additionally, the following relevant techniques are in place: [list technique reference letters] | Techniques set out in BAT 9 (a)-(c) will be in place by 03/12/23. [Additionally, the following relevant techniques will be in place by 03/12/23: [list technique reference letters].
10 | Bottom ash treatment | Quality output management system | Quality output management system part of EMS where bottom ash treatment is carried out. | Yes | A quality management system is in place. |  | Select option and/or add site specific text | Not applicable - bottom ash treatment is not carried out. | A quality management system is in place. | A quality management system will be implemented by 03/12/23.
11 | Waste delivery, storage and handling | Monitor waste deliveries | Monitor in line with corresponding table, depending on the risk posed by the waste type. | No | Select option and/or add site specific text |  | Select option and/or add site specific text | Measures in line with BAT 10 are in place | Measures in line with BAT 10 will be in place by 03/12/23
|  | Radioactivity detection | Radioactivity detection not required unless site-specific risk assessment dictates otherwise. | No | Select option and/or add site specific text |  | Select option and/or add site specific text | Not required - no increased risk identified | Radioactivity detection is carried out due to site-specific reasons as set out as follows: [specify reasons] | Radioactivity detection will be carried out from 03/12/23 due to site-specific reasons as set out as follows: [specify reasons]
12 |  | Storage and handling | Use both techniques listed in corresponding table. Technique (a) (Impermeable surfaces with adequate drainage infrastructure) must be used for all types of IBA treatment and storage. | Yes | Not applicable. In line with UK regulators WI BREF Interpretation Document | According to interpretation document not applicable to IBA treatment. | Select option and/or add site specific text | Measures in line with BAT 12 are in place | Measures in line with BAT 12 will be in place by 03/12/23
13 |  | Storage and handling of clinical waste | Combination of techniques listed in corresponding table. | No | Select option and/or add site specific text |  | Select option and/or add site specific text | Not applicable as clinical waste not received at the installation | The following techniques are used in line with BAT 13: [list technique reference letters] | The following techniques in line with BAT 13 will be in place by 03/12/23: [list technique reference letters]
14 | Overall environment performance | Reduce unburnt substances in slags / bottom ash and reduce emissions. | Combination of techniques listed in corresponding table | No | Select option and/or add site specific text |  | Select option and/or add site specific text | The following measures listed in the table of BAT 14 are used: [list technique reference letters] | The following measures listed in the table of BAT 14 will be implemented by 03/12/23: [list technique reference letters]
|  |  | BAT-AEPL for TOC or LOI | No | Select option and/or add site specific text |  | Select option and/or add site specific text | The installation meets the BAT-AEPL for [TOC or LOI] as shown by historic monitoring data | The installation does not currently meet the he BAT-AEPL for [TOC or LOI] but measures will be implemented to ensure that it meets it by 03/12/23.
15 |  | Control plant settings to reduce emissions to air. | Use techniques such as an advanced control system. | No | Select option and/or add site specific text |  | Select option and/or add site specific text | An advanced control system is in place to achieve the requirements of BAT 15. | Alternative measures are in place to achieve the requirements of BAT 15 [provide detail]
16 |  | Procedures to limit shutdown and start-up | Set up and implement procedures such as continuous rather than batch operation. | No | Select option and/or add site specific text |  | Select option and/or add site specific text | Start-up and shut-down is minimised by [describe measures such as continuous supply chain, continuous process] | Measures listed below will be in place by 03/12/23 [list measures]
17 | Emission to air and water | Design of FGC system and waste water treatment plant. | Appropriate design, operated in design range, maintained to ensure optimal availability. | No | Select option and/or add site specific text |  | Select option and/or add site specific text | Flue gas system [and waste water treatment plant] is designed appropriately and is operated within those design parameters | Improvements are required and will be implemented by 03/12/23.
18 | OTNOC | Reduce frequency of OTNOC | Set up and implement an OTNOC management plan. | No | Select option and/or add site specific text | Reference to supporting document describing how critical equipment has been designed to minimise occurrence of abnormal operation (AO) and minimise impacts from AO and start-up and shut-down periods: XXXXXX | Select option and/or add site specific text | An OTNOC management plan which meets the requirements of BAT 18 has been implemented. A description of how critical equipment has been designed to minimise occurrence of abnormal operation (AO) and minimise impacts from AO and start-up and shut-down periods is included with this submission (see reference to supporting document in column G). | An OTNOC management plan which meets the requirements of BAT 18 will be implemented by 03/12/23. A description of how critical equipment has been designed to minimise occurrence of abnormal operation (AO) and minimise impacts from AO and start-up and shut-down periods is included with this submission (see reference to supporting document in column G).
19 | Energy efficiency | Increase efficiency | Use a heat recovery boiler. | No | Select option and/or add site specific text |  | Select option and/or add site specific text | A heat recovery boiler is used to [generate electricity and/or steam and/or hot water] | A heat recovery boiler is not applicable because. [provide justification]
20 |  | Increase efficiency | Combination of techniques listed in corresponding table. | No | Select option and/or add site specific text |  | Select option and/or add site specific text | The following measures listed in the table of BAT 20 are used: [list technique reference letters] | The following measures listed in the table of BAT 20 will be implemented by 03/12/23: [list technique reference letters]
|  | BAT-AEEL | Within relevant BAT-AEEL range. | No | Select option and/or add site specific text |  | Select option and/or add site specific text | The [gross electrical efficiency / gross energy efficiency / boiler efficiency] is [x} % . | The gross [electrical efficiency / gross energy efficiency / boiler efficiency] has not yet been calculated. See response to BAT 2 above
21 | Diffuse emissions to air | Prevent or reduce diffuse emissions (including odour). | Use techniques listed. | No | Select option and/or add site specific text |  | Select option and/or add site specific text | Measures in line with BAT 21 are in place | Measures in line with BAT 21 will be in place by 03/12/23
22 |  | Prevent diffuse emissions of VOCs from gaseous and liquid wastes. | Direct feed to furnace. | No | Select option and/or add site specific text |  | Select option and/or add site specific text | Not applicable - gaseous or liquid waste are not accepted | Measures in line with BAT 22 are in place | Measures in line with BAT 22 will be in place by 03/12/23
23 |  | Prevent or reduce diffuse emissions to air from treatment of slags and bottom ashes. | Include listed measures in EMS. | Yes | The EMS includes the features listed under BAT 23. | See dust management plant attached to the application. | Select option and/or add site specific text | Not applicable - bottom ash treatment is not carried out. | The EMS includes the features listed under BAT 23. | The EMS will be updated to include the features listed under BAT 23 by 03/12/23.
24 |  | Prevent or reduce diffuse emissions to air from treatment of slags and bottom ashes. | Use one or a combination of techniques in corresponding table. | Yes | The following measures listed in the table of BAT 24 are used: [list technique reference letters] The following measures listed in the table of BAT 24 are not used [list technique reference letters and in Column G justify why they are not necessary, including any equivalent measures used] | (a) Enclosed and covered equipment (b) Height of discharge limited (low only) (d) Water Sprays installed (External rain guns for stockpiles and internal misters) (e) moisture content managed when processing (visual check and moisture dosing as required) (f) not applicable as IBA not dry NOT APPLIED (c) protect stockpiles against prevailing winds (continuous damping down of stockpile and surrounding areas manages dust emission. The site is situated in a depression below the tree line and is sheltered from the wind). | Select option and/or add site specific text | Not applicable - bottom ash treatment is not carried out. | The following measures listed in the table of BAT 24 are used: [list technique reference letters] The following measures listed in the table of BAT 24 are not used [list technique reference letters and in Column G justify why they are not necessary, including any equivalent measures used] | The following measures listed in the table of BAT 24 are used: [list technique reference letters] The following measures listed in the table of BAT 24 are not used [list technique reference letters and in Column G justify why they are not necessary, including any equivalent measures used] The following measures listed in the table of BAT 24 will be implemented by 03/12/23: [list technique reference letters]
25 | Channelled emissions to air | Reduce emissions of metals and metalloids from incineration of waste. | Use one or a combination of techniques in corresponding table. | No | Select option and/or add site specific text |  | Select option and/or add site specific text | The following measures listed in the table of BAT 25 are used: [list technique reference letters] | The following measures listed in the table of BAT 25 will be implemented by 03/12/23: [list technique reference letters] | The following alternative measures are in place to meet the requirements of BAT 25 [list measures e.g. ceramic filters]
|  | BAT-AELs for dust and metals | Emissions below top end of BAT-AEL range | No | Select option and/or add site specific text |  | Select option and/or add site specific text | The plant is currently able to achieve an emission limit value set at the top end of the BAT-AEL range. | The plant will be able to achieve an emission limit value set at the top end of the BAT-AEL range by 03/12/23. | A derogation from the BAT-AEL for [insert which BAT AEL(s)] will be requested.
26 |  | Reduce emissions of dust from treatment of slags and bottom ashes. | Use a bag filter if treating air from treatment of IBA under sub-atmospheric conditions. | Yes | Not applicable as IBA is not treated under sub-atmospheric conditions. |  | Select option and/or add site specific text | Not applicable - bottom ash treatment is not carried out. | Not applicable as IBA is not treated under sub-atmospheric conditions. | Bag filter in place. | Bag filter will be in place by 03/12/23
|  | BAT-AEL for dust from IBA treatment | Emissions below top end of BAT-AEL range if using a bag filter to treat air from treatment of IBA under sub-atmospheric conditions | Yes | Not applicable as IBA is not treated under sub-atmospheric conditions. |  | Select option and/or add site specific text | Not applicable - bottom ash treatment is not carried out. | Not applicable as IBA is not treated under sub-atmospheric conditions. | The plant is currently able to achieve an emission limit value set at the top end of the BAT-AEL range. | The plant will be able to achieve an emission limit value set at the top end of the BAT-AEL range by 03/12/23. | A derogation from the BAT-AEL will be requested.
27 |  | Reduce emissions of HCl, HF and SO2 | Use one or a combination of techniques in corresponding table. | No | Select option and/or add site specific text |  | Select option and/or add site specific text | The following measures listed in the table of BAT 27 are used: [list technique reference letters] | The following measures listed in the table of BAT 27 will be implemented by 03/12/23: [list technique reference letters]
28 |  | Reduce peak emissions of HCl, HF and SO2 and amount of residue produced. | Use technique (a) or both techniques in corresponding table. | No | Select option and/or add site specific text |  | Select option and/or add site specific text | The following measures listed in the table of BAT 28 are used: [list technique reference letters] | The following measures listed in the table of BAT 28 will be implemented by 03/12/23: [list technique reference letters]
|  | BAT-AELs for HCl, HF and SO2 | Emissions below top end of BAT-AEL range. | No | Select option and/or add site specific text |  | Select option and/or add site specific text | The plant is currently able to achieve an emission limit value set at the top end of the BAT-AEL range. | The plant will be able to achieve an emission limit value set at the top end of the BAT-AEL range by 03/12/23. | A derogation from the BAT-AEL for [insert which BAT AEL(s)] will be requested.
29 |  | Reduce emissions of NOx while limiting emissions of CO, N2O and NH3 | Use appropriate combination of techniques in corresponding table. | No | Select option and/or add site specific text |  | Select option and/or add site specific text | The following measures listed in the table of BAT 29 are used: [list technique reference letters] | The following measures listed in the table of BAT 29 will be implemented by 03/12/23: [list technique reference letters]
|  | BAT-AELs for NOx, CO and NH3 | Emissions below top end of BAT-AEL range. | No | Select option and/or add site specific text |  | Select option and/or add site specific text | The plant is currently able to achieve an emission limit value set at the top end of the BAT-AEL range. | The plant will be able to achieve an emission limit value set at the top end of the BAT-AEL range by 03/12/23. | A derogation from the BAT-AEL for [insert which BAT AEL(s)] will be requested.
30 |  | Reduce emissions of organic compounds including PCDD/F and PCBs | Use techniques (a), (b), (c), (d) and one or a combination of techniques (e) to (i) in corresponding table | No | Select option and/or add site specific text |  | Select option and/or add site specific text | The following measures listed in the table of BAT 30 are used: [list technique reference letters] | The following measures listed in the table of BAT 30 will be implemented by 03/12/23: [list technique reference letters]
|  | BAT-AELs for PCDD/F | Emissions below top end of BAT-AEL range. | No | Select option and/or add site specific text |  | Select option and/or add site specific text | The plant is currently able to achieve an emission limit value set at the top end of the BAT-AEL range. | The plant will be able to achieve an emission limit value set at the top end of the BAT-AEL range by 03/12/23. | A derogation from the BAT-AEL will be requested.
31 |  | Reduce mercury emissions | Using one or a combination of techniques in the corresponding table. | No | Select option and/or add site specific text |  | Select option and/or add site specific text | The following measures listed in the table of BAT 31 are used: [list technique reference letters] | The following measures listed in the table of BAT 31 will be implemented by 03/12/23: [list technique reference letters]
|  | BAT-AEL for mercury | Emissions below top end of BAT-AEL range. | No | Select option and/or add site specific text |  | Select option and/or add site specific text | The plant is currently able to achieve an emission limit value set at the top end of the BAT-AEL range. | The plant will be able to achieve an emission limit value set at the top end of the BAT-AEL range by 03/12/23. | A derogation from the BAT-AEL will be requested.
32 | Emissions to water | Reduce contamination of uncontaminated water, reduce emissions to water and increase resource efficiency. | Segregate waste water streams and treat them separately. | Yes | The measures listed under BAT 32 are used. | There is only a single type of waste water produced on site which is the surface run-off from the operation. This is collected in the storage lagoon and is kept separate from the clean surface run-off collected from the rest of the site. The waste water is removed from site for disposal by tanker as required. | Select option and/or add site specific text | The measures listed under BAT 32 are used. | The measures listed under BAT 32 will be in place by 03/12/23. | The following measures listed under BAT 32 are used [list measures] but the following measures are not used [list measures and provide justification why they are not applicable]
33 | Water usage | Reduce water usage, prevent waste water generation. | Using one or a combination of techniques in the corresponding table | No | Select option and/or add site specific text |  | Select option and/or add site specific text | The following measures listed in the table of BAT 33 are used: [list technique reference letters] | The following measures listed in the table of BAT 33 will be implemented by 03/12/23: [list technique reference letters]
34 | Emissions to water | Reduce emissions to water from FGC and/or from storage and treatment of slags and bottom ashes. | Using one or a combination of techniques in the corresponding table and use secondary techniques as close to source as possible. For IBA, this should include specific consideration of abatement of metals prior to discharge to water or sewer (e.g. via precipitation followed by solids removal) to prevent transfer of pollutants from one medium to another. | Yes | The following measures listed in the table of BAT 34 will be implemented by 03/12/23. None - no treatment is required to comply with the limits. |  | Select option and/or add site specific text | Not applicable - no direct or indirect emissions to water from FGC or bottom ash treatment | The following measures listed in the table of BAT 34 are used: [list technique reference letters] | The following measures listed in the table of BAT 34 will be implemented by 03/12/23: [list technique reference letters]
|  | BAT-AELs | Emissions below top end of BAT-AEL range. | Yes | The plant is currently able to achieve an emission limit value set at the top end of the BAT-AEL range. |  | Select option and/or add site specific text | Not applicable - no direct or indirect emissions to water from FGC or bottom ash treatment | The plant is currently able to achieve an emission limit value set at the top end of the BAT-AEL range. | The plant will be able to achieve an emission limit value set at the top end of the BAT-AEL range by 03/12/23. | A derogation from the BAT-AEL for [insert which BAT AEL(s)] will be requested.
35 | Resource efficiency | Resource efficiency | Handle and treat bottom ashes separately from FGC residues. | No | Select option and/or add site specific text |  | Select option and/or add site specific text | Bottom ashes are handled and treated separately from FGC residues. | Bottom ashes will be handled and treated separately from FGC residues by 03/12/23.
36 |  | Resource efficiency for treatment of slags and bottom ashes. | Use appropriate combination of techniques in corresponding table depending on hazardous properties of the slags and bottom ashes. | Yes | The following measures listed in the table of BAT 36 are used: [list technique reference letters] | (a) screening and sieving, (c) aeraulic separation, (d). recovery of ferrous and non-ferrous, (e) ageing | Select option and/or add site specific text | Not applicable - bottom ash treatment is not carried out. | The following measures listed in the table of BAT 36 are used: [list technique reference letters] | The following measures listed in the table of BAT 36 will be implemented by 03/12/23: [list technique reference letters]
37 | Noise | Reduce noise emissions | Using one or a combination of techniques in the corresponding table. | Yes | The following measures listed in the table of BAT 37 are used: [list technique reference letters] | (c) operational measures, (c) low-noise equipment, (d) noise attenuation by location in a deprression/elevated banks, (e) noise-control equipment | Select option and/or add site specific text | The following measures listed in the table of BAT 37 are used: [list technique reference letters] | The following measures listed in the table of BAT 37 will be implemented by 03/12/23: [list technique reference letters]