All defects or problems found during checks and inspections must be recorded on this form. The completed form must be handed to the Plant Manager who must enter remedial action taken. All records of plant repair and maintenance will be kept for a minimum of two years. Use a √ or X followed by your initials or numeric readings where applicable.

| Plant | Task detail | Mon | Tue | Wed | Thu | Fri |
| --- | --- | --- | --- | --- | --- | --- |
| Autoclave | Check for leaks or damage to vessel and pipework |  |  |  |  |  |
|  | Check PLC for unusual traces and any abnormalities. |  |  |  |  |  |
|  | Lubricate the doors |  |  |  |  |  |
|  | Check and operate all manual shut off valves |  |  |  |  |  |
| Boiler | Inspect area for leaks. |  |  |  |  |  |
|  | Blow-down of boiler water level glasses 1 & 2 |  |  |  |  |  |
|  | Manual blow-down of boiler (min 10 seconds) |  |  |  |  |  |
|  | Check and record boiler TDS |  |  |  |  |  |
|  | Check & record gauge pressure |  |  |  |  |  |
|  | Boiler fuel tanks, check for leaks & store locked |  |  |  |  |  |
|  | Check boiler burner & pump operation |  |  |  |  |  |
| Test boiler safety: | 1 Turn off feed pump |  |  |  |  |  |
|  | Low water alarm rings |  |  |  |  |  |
|  | Burner stops |  |  |  |  |  |
|  | Low water light lit |  |  |  |  |  |
|  | 2 Slowly open blow-down valve |  |  |  |  |  |
|  | Extra low water alarm rings |  |  |  |  |  |
|  | Burner goes to lock-out |  |  |  |  |  |
|  | Extra low light is lit |  |  |  |  |  |
| Plant Manager to initial | 3 Close blow-down valve |  |  |  |  |  |
| here to | 4 Start feed pump. Re set extra low alarm |  |  |  |  |  |
| Confirm completion | Low alarm auto resets |  |  |  |  |  |
|  | Burner restarts |  |  |  |  |  |
|  | Boiler high water test passed |  |  |  |  |  |
| Date | NB If NO to any of the above, shut down immediately and rectify fault |  |  |  |  |  |
| Water Treatment, Hotwell & Blowdown Vessel | Record Hot-well water level daily and softness on Friday |  |  |  |  |  |
|  | Record Hot-well water temperature |  |  |  |  |  |
|  | Check function of water treatment system and water softness daily |  |  |  |  |  |
| Boiler Chemicals | Treatment tank check/top up with chemicals if required |  |  |  |  |  |
|  | Brine tank check/top up with salt if required |  |  |  |  |  |
|  | Salt tablets, number of bags in stock |  |  |  |  |  |
|  | Sodium Bisulphite, number of drums in stock |  |  |  |  |  |
|  | Sulphite test reading (acceptable range 100 - 200) |  |  |  |  |  |
| Heat Exchanger Cooling | Check pipe-work for leaks |  |  |  |  |  |
| System | Check Fan operation |  |  |  |  |  |
|  | Check Primary pump 1 & 2 operation |  |  |  |  |  |
|  | Check Secondary Pump 1 & 2 operation |  |  |  |  |  |

| Shredder and Cart Tipper | Check hydraulic rams & pumps for leaks |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Check condition of lifter chains & rollers |  |  |  |  |  |  |  |  |  |
|  | Check condition of cutters |  |  |  |  |  |  |  |  |  |
|  | Check coolant level |  |  |  |  |  |  |  |  |  |
|  | Check coolant fan operation |  |  |  |  |  |  |  |  |  |
| Shredder and Cart Tipper | Grease all bearings on Shredder and Lifter |  |  |  |  |  |  |  |  |  |
|  | Clean inside of ram housing |  |  |  |  |  |  |  |  |  |
| Shredder fire suppression | Check condition of pipework for leaks |  |  |  |  |  |  |  |  |  |
|  | High level sprinklers working |  |  |  |  |  |  |  |  |  |
|  | Low level sprinklers working |  |  |  |  |  |  |  |  |  |
| Bin Tipper | Check Hydraulic rams & pipework for leaks |  |  |  |  |  |  |  |  |  |
|  | Check condition of tipper bolts & pivot pins |  |  |  |  |  |  |  |  |  |
|  | Grease all bearings |  |  |  |  |  |  |  |  |  |
|  | Wash and disinfect unit and installation floor |  |  |  |  |  |  |  |  |  |
| Bin Washer | Check operation of washer & pumps |  |  |  |  |  |  |  |  |  |
|  | Check & record cleaning chemical level |  |  |  |  |  |  |  |  |  |
|  | Check system for leaks |  |  |  |  |  |  |  |  |  |
| Air Compressor | Drain air receiver |  |  |  |  |  |  |  |  |  |
|  | Check function of compressor |  |  |  |  |  |  |  |  |  |
| Site General | Waste storage bin lids secure |  |  |  |  |  |  |  |  |  |
|  | Weather conditions (Dry, Wet, Windy, Frosty) |  |  |  |  |  |  |  |  |  |
|  | Drainage system clear & pumps working |  |  |  |  |  |  |  |  |  |
|  | Odour check intensity (See E007.11.1) Scale: 0-5 |  |  |  |  |  |  |  |  |  |
|  | Site signage, security fencing & gates in good order |  |  |  |  |  |  |  |  |  |
|  | Floors, steps, gantries and exits (including fire exits) clear |  |  |  |  |  |  |  |  |  |
|  | Check Ladders (See H007) |  |  |  |  |  |  |  |  |  |
|  | Remove litter or weeds on site |  |  |  |  |  |  |  |  |  |
|  | Evidence of pests |  |  |  |  |  |  |  |  |  |
|  | Spill Kits and drain mats complete & in place |  |  |  |  |  |  |  |  |  |
|  | PPE being worn |  |  |  |  |  |  |  |  |  |
|  | Fire alarm bell test. Record call point ID |  |  |  |  |  |  |  |  |  |
|  | Number of complaints received |  |  |  |  |  |  |  |  |  |
|  | Check site for containers on top of bins or the floor |  |  |  |  |  |  |  |  |  |
|  | Check/clean weighbridge stations |  |  |  |  |  |  |  |  |  |
|  | Check for littler around the building |  |  |  |  |  |  |  |  |  |
|  | Check all bunded areas are free from spills |  |  |  |  |  |  |  |  |  |

| Meter Readings (Start of week) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Plant Electricity R1 | kWh |  | Boiler Fuel Oil | litres |  |
| Plant Electricity R2 | kWh |  | Boiler water feed | m3 |  |
| EV Charging point | kWh |  | Water | m3 |  |
|  |  |  | Gas | m3 |  |

Rectifications made (use reverse of sheet if necessary)

Rectifications checked and this record filed by…………………………………………….(Plant Manager)	Date:………………………..