## Standard Permit GRA1
Temporary Waste Storage Facility: |  |  |  | Temporary Waste Storage Facility - Less than 15,000 Ltrs
Location: |  |  |  | Refuels Storage Tank at OnRoute Truckstop, Third Way, Avonmouth
Location of environmentally sensitive sites (km / m): |  |  |  | Greater than 200 metres (see below)
Risk assessment carried out by: |  |  |  | Refuels Ltd
Date: |  |  |  | 2025-05-27
The scope of the permit and associated rules is defined by the following risk criteria:
| Parameter 1 | Permitted activities - The storage of waste prior to recovery or disposal elsewhere (R13 or D15)
| Parameter 2 | Permitted waste types - Hazardous Waste (Petroleum Distillates), UN1268 Waste/Mixed Fuels EWC 130703
| Parameter 3 | Quantity of waste accepted at the facility: less than 30,000Ltrs per annum.
| Parameter 4 | Quantity of waste stored at any one time: 15,000Ltrs
| Parameter 5 | All waste shall be stored on an impermeable surface within a bunded tank
| Parameter 6 | The only point source discharges to controlled waters are surface water from the landlords control area (off site via interceptor)
| Parameter 7 | a groundwater source protection zone 1, or if a source protection zone has not been defined then within
50 metres of any well, spring or borehole used for the supply of water for human consumption . This must include private water supplies.
| Parameter 8 | The activities shall not be carried out within 200 metres of a European Site (candidate or Special Area of Conservation,
proposed or Special Protection Area or Ramsar site) or a Site of Special Scientific Interest (SSSI).
| Abbreviations: | SR - standard rule
Data and information |  |  |  |  | Judgement |  |  | Action (by permitting)
Receptor | Source | Harm | Pathway | Probability of exposure | Consequence | Magnitude of risk | Justification for magnitude | Risk management | Residual risk
What is at risk? What do I wish to protect? | What is the agent or process with potential to cause harm? | What are the harmful consequences if things go wrong? | How might the receptor come into contact with the source? | How likely is this contact? | How severe will the consequences be if this occurs? | What is the overall magnitude of the risk? | On what did I base my judgement? | How can I best manage the risk to reduce the magnitude? | What is the magnitude of the risk after management? (This residual risk will be controlled by Compliance Assessment).
Onsite Workers & Local human population. | Waste, litter and mud on local roads. | Nuisance, loss of amenity, road traffic accidents. | Vehicles entering and leaving site. | Low | Low | Low | Activities unlikely to give rise to litter, debris or mud. | SR (Standard Rule) (emissions of substances not controlled by emission limits) requires emissions management plan where necessary. | Low
Onsite Workers & Local human population. | Odour of product | Nuisance, loss of amenity. | During decanting & uplifting product between vehicle and storage tank | Low | Low | Low | Vapour recovery system inplace to support uplifting operations. Dry brake user couplings. | SR odour condition requires emissions to be free from odour at levels likely to cause pollution outside the site - an odour management plan is required in the unlikely event of an odour problem. | Low
Onsite Workers & Local human population. | Noise and vibration. | Nuisance, loss of amenity, loss of sleep or harm. | Noise through the air and vibration through the ground. | Low | Low | Low | Minimal operation 3-4 movements per week. Operation is not intrusive (65Db(A)) for 30 min period. Operation is mainly carried out 09.00-17.00Hrs | SR - emissions shall be free from noise and vibration and a noise and vibration management plan is required where necessary. | Low
Local human population and local environment. | Flooding of site. | If waste is washed off site it may contaminate buildings / gardens / natural habitats downstream. | Flood waters. | Low | Low | Low | Waste is potentially polluting but stored inside sealed and bunded storage tank. | SR - management system required to identify and minimise risks including those from accidents. | Low
Onsite Workers, Local human population and local environment. | Fire risk from stockpiles,arson and / or vandalism causing the release of polluting materials to air (smoke or fumes), water or land. | Respiratory irritation, illness and nuisance to local population. Injury to staff, firefighters or arsonists/vandals. Pollution of air,water or land. | Air transport of smoke. Spillages and contaminated firewater by direct run-off from site and via surface water drains and ditches. | Low | Medium | medium | On site security (fence & CCTV). Real time tank content volume and temperature monitoring. User specific security and access control. Earth circuit continuity. No mains electric connection, power supply via PV panel and battery. Annual PPM regime in place. Tank is subject to 4-Hour, 2000º F Fire Test, Internal temperature increased only 165º F, Immediately after the Fire Test the hot tank is exposed to a Hose Stream Test | SR - management system required to identify and minimise risks from operations - to include fire and security. | Low
On Site Workers, Local human population after gaining unauthorised access to the waste operation. | All on-site hazards: wastes | Bodily injury. | Direct physical contact. | Low | Low | Low | Permitted waste types are hazardous but stored in sealed tanks therefore only a medium magnitude risk is estimated. On site security (fencing and CCTV) | SR - management system required to identify and minimise risks from operations - to include security. | Low
Local human population and local environment. | Accidental fire causing the release of polluting materials to air (smoke or fumes), water or land. | Respiratory irritation, illness and nuisance to local population. Injury to staff or firefighters. Pollution of water or land. | As above. | Low | Medium | Medium | On site security (fence & CCTV). Real time tank content volume and temperature monitoring. User specific security and access control. Earth circuit continuity. No mains electric connection, power supply via PV panel and battery. Annual PPM regime in place. Tank is subject to 4-Hour, 2000º F Fire Test, Internal temperature increased only 165º F, Immediately after the Fire Test the hot tank is exposed to a Hose Stream Test | SR - management system required to identify and minimise risks from operations - to include fire. | Low
All surface waters close to and downstream of site. | Spillage of liquids, contaminated rainwater run-off. | Acute effects; oxygen depletion, fish kill and algal blooms. | Direct run-off from site across ground surface, via surface water drains, ditches etc. Product could be spilled during transfer | Low | Medium | Medium | HLCO High level cut-off alarm system. Real time tank content volume and temperature monitoring. Dry brake user couplings. Integral self bunding. Tank sited on concrete base. All site drainage is via interceptor | SR - All areas of the site used for storage of oil in drums or tanks of oil shall be provided with an impermeable surface and bunding SR - no point source emissions to water. SR - require emissions management plan if activities give rise to pollution. | Low
All surface waters close to and downstream of site. | As above | Chronic effects; deterioration of water quality. | As above. Indirect run-off via the soil layer. | Low | Medium | Medium | Oils could be spilled during transfer/bulking operations leading to direct contmaination of surface waters or by run-off becoming contaminated. | As above | Low
Abstraction from watercourse downstream of facility (for agricultural or potable use). | As above | Acute effects, closure of abstraction intakes. | Direct run-off from site across ground surface, via surface water drains, ditches etc. Product could be spilled during transfer | Low | Medium | Medium | HLCO High level cut-off alarm system. Real time tank content volume and temperature monitoring. Dry brake user couplings. Integral self bunding. Tank sited on concrete base. All site drainage is via interceptor | As above | Low
Groundwater | As above | Chronic effects: contamination of groundwater, requiring treatment of water or closure of borehole. | Transport through soil/groundwater then extraction at borehole. | Low | High | Medium | HLCO High level cut-off alarm system. Real time tank content volume and temperature monitoring. Dry brake user couplings. Integral self bunding. Tank sited on concrete base. All site drainage is via interceptor | SR - the activities must be outside a groundwater source protection zone 1, or if a source protection zone has not been defined then within 50 metres of any well, spring or borehole used for the supply of water for human consumption. This must include private water supplies. Other conditions as above. | Low
Local human population. | Contaminated waters used for recreational purposes. | Harm to human health - skin damage or gastro-intestinal illness. | Direct contact or ingestion. | Low | Medium | Medium | Unlikely to occur, but might restrict recreational use. | SR (emissions of substances not controlled by emission limits). SR (if required) - emissions management plan. Sanitisation temperatures will be reached to allow pasteurization of material. | Low
Protected sites - European sites and SSSIs protected species/habitats and other nature conservation sites. | Any | Harm to protected site through toxic contamination and disturbance. | Any | Low | Medium | Medium | Most likely a a result of surface water contamination. | SR - activities shall not be carried out within 200 metres of a European Site or SSSI. | Low
Notes: | Red triangle indicates comment containing supporting information
Yellow columns contain drop down menus that allow automatic evaluation of risk in green column
| Very low | Low | Medium | High
High | 4 | 8 | 12 | 16
Medium | 3 | 6 | 9 | 12
Low | 2 | 4 | 6 | 8
Very low | 1 | 2 | 3 | 4
|  |  |  | Very low |  | 2 | 3 | 6 | Medium
|  |  |  | Low |  | 2 | 3 | 6 | Medium
|  |  |  | Medium |  | #REF! | #REF! | #REF! | #REF!
|  |  |  | High |  | #REF! | #REF! | #REF! | #REF!
[6 empty] | #REF! | #REF! | #REF! | #REF!
[6 empty] | #REF! | #REF! | #REF! | #REF!
[6 empty] | 2 | 2 | 4 | Low
[6 empty] | 2 | 2 | 4 | Low
| Very low | Low | Medium | High |  | #REF! | #REF! | #REF! | #REF!
Very low | 1 | 2 | 3 | 4 |  | #REF! | #REF! | #REF! | #REF!
Low | 2 | 4 | 6 | 8 |  | #REF! | #REF! | #REF! | #REF!
Medium | 3 | 6 | 9 | 12 |  | #REF! | #REF! | #REF! | #REF!
High | 4 | 8 | 12 | 16 |  | #REF! | #REF! | #REF! | #REF!
[6 empty] | #REF! | #REF! | #REF! | #REF!
[6 empty] | #REF! | #REF! | #REF! | #REF!
[6 empty] | #REF! | #REF! | #REF! | #REF!
[6 empty] | #REF! | #REF! | #REF! | #REF!
[6 empty] | #REF! | #REF! | #REF! | #REF!
[6 empty] | #REF! | #REF! | #REF! | #REF!
[6 empty] | #REF! | #REF! | #REF! | #REF!
Note on B31: Receptors to consider should include: atmosphere, land, surface waters, groundwater, humans, wildlife and their habitats. A single receptor may be at risk from several different sources and all must be addressed.
Note on C31: The Source of hazard will be the activity or operation taking place for which a particular hazard may arise.
Note on D31: Harm may arise when a specific hazard is realised.
Note on E31: Pathways are the routes or means by which defined hazards may potentially realise their consequences at the receptors.
Note on F31: Probability of exposure is the likelihood of the receptors being exposed to the hazard. Example definitions: High – exposure is probable: direct exposure likely with no / few barriers between hazard source and receptor; Medium – exposure is fairly probable: feasible exposure possible - barriers to exposure less controllable; Low – exposure is unlikely: several barriers exist between hazards source and receptors to mitigate against exposure: Very Low – exposure is very unlikely: effective, multiple barriers in place to mitigate against exposure.
Note on G31: The consequences of a hazard being realised may be actual or potential harm. This will include be on a high/medium/low/very low score using attributes and scaling to consider 'harm'.
Note on H31: Magnitude of the risk is determined by combining the probability with the magnitude of the potential consequences High risks require additional assessment and active management Medium risks require additional assessment and may require active management/monitoring Low and very low risks require periodic review.
Note on J31: Risk management involves breaking or limiting the source-pathway-receptor linkage to reduce risk.