## Proposed Mitigation
RECOMMENDATIONS FROM STANTEC REPORT | New Flood Extents |  | ESTIMATING SCOPE
Figure 10: Ellesmere Port STC Predicted Flow Paths following Mesophilic Digester Burst
Figure 12: Ellesmere Port STC Predicted Flow Paths following Post Digestion Tank Burst
[6 empty] | Section 1 | Section 2 |  |  |  | Total
|  |  |  | CONTAINMENT KERB 300mm | mm | 30000 | 130000
[5 empty] | m | 30 | 130 |  |  |  | 160 | See sheet 'Kerbing Detail'
[6 empty] | Section 4 | Section 5 |  | Total
|  |  |  | CONTAINMENT KERB 150mm | mm | 140000
[5 empty] | m | 140 | 0 |  | 140
[6 empty] | Section 6 | Section 7 |  | Total
|  |  |  | CONTAINMENT WALL 1500mm | mm | 82000 | 213000
[5 empty] | m | 82 | 213 |  | 295 | See sheet 'Containment Wall'
Figure 14: Ellesmere Post STC Predicted Flow Paths following Centrate Tank Burst
[6 empty] | Section 9 |  | Total
|  |  |  | CONTAINMENT WALL 1000mm | mm | 110000
[5 empty] | m | 110 |  | 110
[6 empty] | Section 11 |  | Total
|  |  |  | CONTAINMENT WALL 500mm | mm | 40000
[5 empty] | m | 40 |  | 40
|  |  |  | SACRIFICIAL AREA | m2 | 12000
|  |  |  | SACRIFICIAL AREA DRAINAGE | m | 570
|  |  |  | 150mm SPEED BUMP | m | 16
Figure 16: Ellesmere Port STC Predicted Flow Paths following Thickened SAS Tank Burst
WORKS ASSOCIATED WITH NEW SAS PLANT
[6 empty] | Section 8 | Section 3 |  | Total
|  |  |  | CONTAINMENT WALL 1500mm(h) | mm | 100000 | 110000
[5 empty] | m | 100 | 110 |  | 210
|  |  |  | AUTOMATED FLOOD GATES (MINIMUM 1500mm HIGH) | m | 6
[6 empty] | Section 10 |  |  | Total
|  |  |  | CONTAINMENT WALL 1000mm(h) | mm | 165000
[5 empty] | m | 165 |  |  | 165
|  |  |  | SACRIFICIAL AREA | m2 | 3000
|  |  |  | SACRIFICIAL AREA DRAINAGE | m | 60
Section 1
Section 2
Section 7
Section 6
Section 9
Section 11
Section 4
Section 10
Section 8
Section 3

## Kerbing Detail
Proposed Mitigation
| Total length on Trief kerbing required (m) | 160
| Total length on standard kerbing required (m) | 140
| Allowance for 0.5m wide strip of bitmac resurfacing (m2) | 150
(Trief Cadet or Titan Compact)

## Opt A - Containment Wall (hidden)
|  |  | CONTAINMENT WALL | #REF! | m
C30 strength RC
|  |  | CONTAINMENT WALL + RETAINNG WALL | #REF! | m
Additional items to consider:
| Vegetation removal | 180m x 10m
| Compensatory planting (shrubbed area including allowance for small trees) | 3600m2
| Existing fence removal & replacement | 150m
| Access & working platform | 250m x 7m x 0.4 (Terram and MOT1 fill)
▲ESTIMATING SCOPE▲
▼ Jetting Calc ▼
Jetting distance
Assumed values
Thermophillic Digesters
|  |  | H | 13.6 | m
|  |  | h | 1.5 | m
|  |  | Imax | 12.1 | m
Post Digestion Tank
|  |  | H | 7 | m
|  |  | h | 1.5 | m
|  |  | Imax | 5.5 | m
Typical Section Containment and retaining wall
Typical Section (Existing) Containment and retaining wall
Typical Section (Proposed) Containment and retaining wall
Sheet pile wall
12m long AU16 Grade 390N/mm2
(Approx Spons Mass 95kg/m 305 x 305)
Capping beam detail as per Containment wall detail above
Working area
Vegetation removal & compenstory planting
Working area
Existing fence at toe of slope
For capping beam detail to sheet pile walls assume depth of base increase by 200mm i.e. total depth 450mm
OPTION A

## Containment Wall
|  |  |  | CONTAINMENT WALL 1.5m HIGH | 295 | m
|  |  |  | CONTAINMENT WALL 1.0m HIGH | 110 | m
|  |  |  | CONTAINMENT WALL 0.5m HIGH | 40 | m
CONTAINMENT WALL ASSOCIATED WITH SAS PLANT
|  |  |  | CONTAINMENT WALL 1.5m HIGH | 210 | m
|  |  |  | CONTAINMENT WALL 1.0m HIGH | 165 | m
C30 strength RC
Additional items to consider:
| Vegetation removal | 180m x 10m
| Compensatory planting (shrubbed area including allowance for small trees) | 3600m2 | m2
▲ESTIMATING SCOPE▲
Section A
Vegetation removal (trees to boundary) & compenstory planting
Typical Section A (Proposed)
Containment wall
(to match EGL)
OPTION B1
Section B
Section C
Section A
Section A
Section B
Typical Section B (Proposed)
Containment wall
Typical Section C (Proposed)
Containment wall

## SACRIFICIAL AREA DRAINAGE
ONLY REQUIRED FOR OPTION B1
Impermeable membrane area Strip existing surfacing (assume gravel), prep surface, lay membrane, reinstate surfacing | 12000 | m2
Length of French drains | 570 | m
No. of existing manhole connections | 10 | No.
Impermeable membrane area (SAS PLANT) Strip existing surfacing (assume gravel), prep surface, lay membrane, reinstate surfacing | 3000 | m2
Length of French drains (SAS PLANT) | 60 | m
https://uusp/engdel/Standards/engineering%20standards/Standard%20Details/STND_00%20Miscellaneous/Current%20Versions/STND-00-001_B.pdf
|  |  |  | ID | Area | Area | Connecting Manhole | CL | IL | EGL | Start IL | Gradient | DN | Length | End IL | Check
[5 empty] | mm2 | m2 | [10 empty] | https://www.uksuds.com/tools/members/surface-water-storage-volume-estimation-members
|  |  |  | A | 3526189813 | 3526.1898 | 342544.5261, 374320.4825 | 5.21 | 3.99 | 5.21 | 4.51 | 0.5% | 150 | 100 | 4.01 | OK | Using this online tool to give inidcation of surface water capacity needed
[7 empty] | MH003 | 5.53 | 3.92 | 5.53 | 4.83 | 0.5% | 150 | 70 | 4.48 | OK |  | Notes for WwTW | Ellesmere Port
|  |  |  | B | 3551680000 | 3551.68 | 342487.3926, 374299.8179 | 5.59 | 1.09 | 5.59 | 4.89 | 0.5% | 150 | 135 | 4.215 | OK | Site latitude | Use map zoom and drop pin on location | 53.26267° N
|  |  |  | C | 627236926.9 | 627.2369 | 342372.5156, 374289.9174 | 5.29 | 3.63 | 5.29 | 4.59 | 0.5% | 150 | 40 | 4.39 | OK | Site longitude | Use map zoom and drop pin on location | 53.26267° N
|  |  |  | D | 543978330.8 | 543.9783 | MH024 | 5.28 | 2.31 | 5.28 | 4.58 | 0.5% | 150 | 55 | 4.305 | OK | Total site area (m2) | Total additional impermeable area created by option | 12000
|  |  |  | E | 1073523610.8 | 1073.5236 | MH024 | 5.28 | 2.31 | 5.28 | 4.58 | 0.5% | 150 | 55 | 4.305 | OK | Total site area (ha) |  | 1.2
|  |  |  | F | 2329000000 | 2329 | MH024 | 5.28 | 2.31 | 5.28 | 4.58 | 0.5% | 150 | 75 | 4.205 | OK | Significant public open space (ha) |  | 0
|  |  |  | H | 300000000 | 300 | MH024 | 5.28 | 2.31 | 5.28 | 4.58 | 0.5% | 150 | 40 | 4.38 | OK
[5 empty] | TOTAL (EXCL SAS) | 11951.6087 | [6 empty] | TOTAL (EXCL SAS) | 570 |  |  | Area positively drained (ha) |  | 1.2
|  |  | AREA RELATED TO NEW SAS PLANT | G | 2230140000 | 2230.14 | MH341 | 5.95 | 4.75 | 5.95 | 5.25 | 0.5% | 150 | 60 | 4.95 | OK | Impermeable area (ha) |  | 1.2
[17 empty] | Drained area that is impermeable (%) |  | 100%
[17 empty] | Impervious area drained via infiltration (ha) |  | 0
[17 empty] | Return period for infiltration system design (years) |  | 100
[17 empty] | Impervious area drained to rainwater harvesting systems (ha) | Assume zero | 0
[17 empty] | Return period for rainwater harvesting system design (years) | Default | 10
[17 empty] | Compliance factor for rainwater harvesting system design (%) | Default | 66%
[17 empty] | Net site area for storage volume design (ha) | Calculated | 1.2
[17 empty] | Net impermeable area for storage volume design (ha) | Calculated | 1.2
[17 empty] | Pervious area contribution (%) | Default | 30
[17 empty] | Rainfall 100yrs 6hrs (mm) | Results using the IH24 method | 63
[17 empty] | Rainfall 100yrs 12hrs (mm) | Results using the IH24 method | 81.62
[17 empty] | Qbar (l/s) |  | 5.83
[17 empty] | 1 in 1 year (l/s) |  | 5.1
[17 empty] | 1 in 30 year (l/s) |  | 9.9
[17 empty] | 1 in 100 years (l/s) |  | 12.1
[17 empty] | Attenuation storage (m3) |  | 792
[17 empty] | Long term storage (m3) |  | 249
[17 empty] | Total storage (m3) |  | 1042
[17 empty] | 1 in 30 year area rate (l/s/m2) |  | 0.000825
[17 empty] | DN150 Proposal capacity (@1 in 200 ks=1.5mm) | l/s | 10.9052
[17 empty] | AREA PER PIPE( DN150) | m2 | 13218.4548
Area G
Area F
Area D
Area E
Area C
Area B
Area A
Area E
Area H