## Rev Table
Site Name | Camberley STW Containment Classification Assessment
Revision | Date | Description | Author | Checked | Reviewed | Approved
1.0 | 2022-02-08 | Draft | C.Sfynia | S.Georgaki | S.Georgaki

## Introduction
Although this tool works as a standalone tool, we recommend you read this first: ADBA CIRIA736 Bud Classification Assessment.
There are 5 steps to follow:
1) | Identify the hazard posed to the environment by the inventory of meterials held on the site and the location of the site
a. Categorise the source
b. Identify the pathways
c. Identify the receptor
2) | The Site Hazard Rating is derived by this tool from the cobination of the hazards assessed above
3) | Calculate the likeihood of a loss of primary containment event occuring
4) | The combination of the Site Hazard Rating and the likelihood of a loss of containment occuring gives the site risk rating and requied secondary containment classification
5) | From the class of containment needed, Identify suitable designs from the 'Standard Containment Designs' Sheet
These cells are drop down menus to selected the risk category
Additional Guidance
The spreadsheets in this workbook have been created based on a protected version which did not allow for complete functionality

## 1) a) Source
| Material | Physical properties | Quantity | units | Storage | Flammability | Corrosive | Ecotoxicity (based on LD and quantity) | Environmental hazard rating | Justification
Feedstock
| Barley | Solid | 1000 | tonnes | Covered clamp | Not flammable | No | Low | L
| Chicken manure | Solid | <1500 | tonnes | Covered clamp | Not flammable | Possibly | Low | M
|  | Solid | > 1500 | tonnes | Covered clamp | Not flammable | Possibly | Low | M
| Cow manure | Liquid | < 10000 | tonnes | Covered tank | Not flammable | No | Low | H
|  | Liquid | > 10000 | tonnes | Covered tank | Not flammable | No | Low | H
| Potatoes | Solid | 2000 | tonnes | Covered | Not flammable | No | Low | L
| Clamp Leachate | Liquid | 1000 | m3 | Collected by drainage | Not flammable | Possibly | Moderate | H
| Condensate from gas line | Liquid | 1 | m3 | condensate trap | Not flammable | No | Low | L
| Slurry | Liquid | <= 1000 | tonnes | Covered tank | Not flammable | No |  | H
| Slurry | Liquid | > 1000 | tonnes | Covered tank | Not flammable | No | Medium | H
| Energy Crops | Solid | < 50000 | tonnes |  | Not flammable | No |  | L
| Energy Crop silage | Solid |  | tonnes | Pad | Not flammable | No |  | M
| Energy crop silage effluent | Liquid |  | m3 | Covered tank | Not flammable | No |  | H
| Food waste | Solid |  | tonnes | Pad | Not flammable | No |  | H
| Green waste | Solid |  | tonnes | Pad | Possibly | No |  | L
[8 empty] | Feedstock Overall Rating | L | Section not relevant
Process
| Digestate (fermenter) | Liquid | < 1000 | m3 | Covered Tank or lagoon |  |  |  | H | Based on latest aquatic toxicity results from REA
|  | Liquid | 1000 < X < 5000 | m3 | Covered Tank or lagoon |  |  |  | H | Based on latest aquatic toxicity results from REA
| Separated digestate solids | Cake |  |  | Concrete pad |  |  |  | M | Largely immobile therefore presents only a medium risk.
| Separated digestate liquid | Liquid |  |  | Covered tank |  |  |  | H
[8 empty] | Process Overall Rating | H | Justification: Digestate is stored within the tanks
Additives and site chemicals
| Ferric Chloride | Liquid | 1 | IVC | IVC | Not flammable | No | Low | L
| Glycol | Liquid | 1 | IVC | IVC | Not flammable | No | Low | L
| Cleaning products | Liquid | 1 | IVC | Consumables container | Not flammable | No | Low | L
| Lab consumables | Liquid | 20 | litres | Consumables container | Not flammable | No | Low | L
[8 empty] | Chemicals Overall Rating | L | Section not relevant
Fire fighting agents and cooling water spillages
| Fire Fighting Agents harmful in their own right or contaminated by inventory | Liquid | >25 | m3 | NA | Not flammable | No | Low | L
| Fire fighting and cooling water contaminated by inventory | Liquid | >25 | m3 | NA | Not flammable | No | Low | L
[8 empty] | Spillages Overall Rating | L | All the hazards are "Low" therefore the overall rating is low
[8 empty] | Sources Overall Hazard Rating | H
H
M
L
Note on G4: Amaya: Flammability is the ability of a substance to burn or ignite, causing fire or combustion. The degree of difficulty required to cause the combustion of a substance is quantified through fire testing.
Note on H4: Amaya: A corrosive substance is one that will destroy and damage other substances with which it comes into contact. It may attack a great variety of materials, including metals and various organic compounds, but people are mostly concerned with its effects on living tissue: it causes chemical burns on contact.
The table below is partially completed to show what needs to be considered and its suggested Hazard Rating. Complete this table for your site to act as a reference and then use your judgement to assign hazard ratings in the yellow boxes. The tool then combines these to calculate the overall source hazard rating.

## 1) b) Pathway
| Pathway - the route from primary containment to receptor |  | Environmental hazard rating | Notes
Site layout and drainage
| If any of the site inventory has a runoff time of a few minutes… |  | H | Runoff time is an estimate of how long it would take to flow to the nearest receptor
| If any of the site inventory has a runoff time of a few hours.… |  | H
| If any of the site inventory has a runoff time of a few days… |  | M
| If any of the site inventory has a runoff time of a few weeks… |  | L | during failure of digester the sludge does not leave site
Topography, geology and hydrology
| Site is raised above a nearby receptor |  | M | Receptors include watercourses and the underlying geology
| Chalk |  | H
| Fractured chalk |  | H
| Principal Aquifer |  | H
| Groundwater protection zone 1 |  | H
etc
Mitigation - do these apply?
| If a secondary containment system is present… |  | L
| If the rain water drainage system in the secondary containment fails safe… |  | L
|  | Path & Mitigation Overall Rating | L | Justification: Solution incorporates containment and control of interface with drainage
Climatic conditions
| Annual rainfall < 1000 mm |  | L
| Annual rainfall > 1000 mm |  | M
| Snow accumulation is possible |  | M
Fire Fighting Water
| Inflammable materials normally present on site in large quantities? |  | M
Location
| Site is in a flood plain |  | H | Site is protected by flood defences
| Site is at bottom of a hill |  | M
| Site is connected to a sewage treatment works |  | M | Shares same site as STW - but containment isolates from the site
|  | Site Considerations Overall Rating | M | Justification: The site is not part of the flood plain however it is close to it.
|  | Pathway Overall Hazard Rating | M
H
M
L
The table shows what needs to be considered and its suggested Hazard Rating. Complete this table for your site to act as a reference and then use your judgement to assign hazard ratings in the yellow boxes. The tool then combines these to calculate the overall pathway hazard rating.

## 1) c) Receptors
| Receptors | Within | units |  | Environmental hazard rating | Notes
Watercourses and bodies
| Rivers above potable water supplies | 100 | m |  | H
| Aquifers used for public supply | 150 | m |  | H
| High quality waters | 1000 | m |  | H
| Agricultural abstraction points | 50 | m |  | M
| High value ecosystems | 1000 | m |  | M
| Recreational waters | 50 | m |  | M
| Small treatment works | 50 | m |  | M
| None of the above |  |  |  | L
|  |  |  | Water Overall Rating | L | Justification: None of the above apply
Habitation
| Dwelling | 250 | m |  | M | No dense dwelling around.
| Workplace | 250 | m |  | L | next to warehouses
| None of the above |  |  |  | L
|  |  |  | Habitation Overall Rating | M | Justification: Adjacent to warehouses and near residential area
Other
| SSSI/SPA/SAC | 1000 |  |  | L
| RAMSAR Site | 1000 |  |  | L
| None of the above |  |  |  | L
|  |  |  | Other Overall Rating | L | Justification: None of the above apply
|  |  |  | Receptors Overall Hazard Rating | M
H
M
L
Input from specialists required.
Use of Energy Institute Tool?
If receptor is uphill from source
then it does not need to be
included.
The table shows what needs to be considered and its suggested Hazard Rating. Complete this table for your site to act as a reference and then use your judgement to assign hazard ratings in the yellow boxes. The tool then combines these to calculate the overall receptors hazard rating.

## 2) Site Hazard Rating
Calculated hazard ratings:
Source | Pathway | Receptor | Site Hazard Rating
H | M | M | High
Possible Combination |  |  | Site Hazard Rating
L | L | L | Low
M | M | L | Low
H | L | L | Low
M | M | M | Medium
H | M | L | Medium
H | H | L | Medium
H | M | M | High
H | H | M | High
H | H | H | High
Rating lookup table
L | 1
M | 2
H | 3
This assesment score
3 | 2 | 2 | 12
The table below is filled in based on your inputs in the "hazard" worksheets 1a, 1b and 1c. The tool then combines these to calculate the overall site hazard rating.
The table below shows the various combinations and their consequent overall site hazards taken from CIRIA 736 and is only provided here for your information.

## 3) Likelihood
| Risk # | Description of Risk | UNMITIGATED LIKELIHOOD | Mitigation applied | MITIGATED LIKELIHOOD |  | Low | Site Overall Likelihood
| 1 | Operational failures, such as failure of plant, or human failure by operators | H | Annual HAZOPs and operator training | L
| 2 | Shortfalls in design – lack of alarms and fail-safe devices | M | Pre-construction HAZOP identified measures - see P&ID ref XXX-YY-123 | L
| 3 | Structural failure – materials, components, detailing, corrosion or when exposed to heat and flame | M
| 4 | Abuse – inappropriate change of use or other misuse | L
| 5 | Impact, eg from a vehicle | M | Armco barriers and concrete bollards installed | L
| 6 | Vandalism, terrorism, force majeure etc | L
| 7 | Fire or explosion | L
| 8 | Geological factors -subsidence etc | L
| 9 | Ageing or deteriorating assets/sub-components. | M
| 10 | Lightning strike | L
| 11 | Additional risk #1 | L
| 12 | Additional risk #2 | M | HAZOP mitigation measure abc | L
| 13 | Additional risk #3 | M | HAZOP mitigation measure xyz | L
| 14 | etc
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
| Risk | Examples of mitigation options | Reduction in likelihood | Detail of measures
| 1 | Operational Failures
|  | The team will carry out periodic design reviews and a comprehensive HAZOP involving all the designers (process, civil, drainage, electrical) to ensure primary containment failure risk is very low. In addition operator training will be strenghthened with detailed standard operating procedures. | -2 | (Taken from consultant's HAZOP report, for example)
|  | Maintenance programme in place | -1
|  | Audit process in place | -1
| 2 | Shortfalls in design
|  | Plant control will be assessed at the HAZOP stage | -2
|  | No outlets below normal liquid level | -1
| 3 | Structural failure – materials, components, detailing, corrosion or when exposed to heat and flame
|  | Pre-cast concrete tank | -2
|  | Tank design has no history of failure | -1
|  | Tank failure risk assessment completed? | -1
|  | Steel valves | -1
|  | Structures will be built to British Standards with contractors that work under ISO9000 | -1
| 4 | Abuse – inappropriate change of use or other misuse
|  | Change control procedure in place with sign off from competent personnel in applicable disciplines | -2
| 5 | Vehicle impact
|  | Armco crash barriers around tank | -2
|  | Tanks in bund not accessible by vehicles | -2
|  | Restricted vehicular access to site | -1
| 6 | Vandalism, terrorism, force majeure etc
|  | lockable valves on outlets (that are locked when not in use by procedure) | -1
|  | automatic and manual shut off valves | -1
|  | The site will include fencing where access is open to public | -1
|  | Passive CCTV system | -1
|  | Monitored CCTV with motion detection and warning signs | -2
| 7 | Fire or explosion
|  | DSEAR assesment completed | -2
|  | Control of ignition sources on site | -1
| 8 | Geological factors -subsidence etc
|  | Site investigatons will be provided to the civil contractor for the desing of the foundations | -1
| 9 | Ageing or deteriorating assets/sub-components.
|  | Ageing/deterioration factored into plant design | -1
| 10 | Lightning strike
|  | Catenary or multiple lightning conductors supplied by specialists | -1
High
Medium
Low
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
In terms of likelihood of a loss of containment, CIRIA 736 provides these guidelines on quantifying the likelihood...
To derive the likelihood for your site, firstly, using the completed risk descriptions and any additional risks identified at your site ask yourself how often will the risk occur and cause a loss of primary containment.
Secondly, consider any mitigation (see the examples provided in the table starting below row 50 for guidance) and apply the reduced likelihood.
Finally, select the likelihood by applying the fact that the highest likelihood gives the site's overall likelihood.

## 4) Site Risk and Classification
| Site Hazard Rating | Likelihood | Overall Site Risk Rating | Indicated Class of Secondary Containment Required
| High | Low | Medium | Class 2
Rating lookup table
Low | 1
Medium | 2
High | 3
This assesment score
3 | 1 |  | 3
The table below is filled in based on your inputs in the "Site Hazard Rating" worksheet and "Likelihood" worksheet. The tool then combines these to calculate the overall site hazard rating and the consequent class of secondary containment required.

## 5) Standard Containment Designs
Your site needs a design based on this diagram
# | Material | When used | How | Why
A | Clay | If plentiful on site | 1m thick, sheepsfoot roller etc. | Low cost & effective.
B | Stabilised soil | If soil tested and is suitable | Sample and test to determine amount of lime, cement and depth. | Low cost & effective when no clay on site.
C | Bentonite matting | If A or B not suitable | Prepare sub, roll out and cover. | Moderate cost. Quick & easy to lay. Tolerant of damage.
D | Landfill liner type foil | If A, B or C not suitable | Prepare sub, roll out, weld and cover.
E | Concrete | Small areas only | Shutter, place mesh and pour fibre reinforced. | Only if A, B, C or D not suitable.
The text and diagrams below are intended to provide an introduction to the design requirements of secondary containment systems. All this text should be read in order to gain a useful understanding of containment construction prior to commencing procurement.