## Sheet1
Noise Source | Sound Power Level LWA dB (A) | Height (m) | Number | Information Source
Stack(s) | 103 | 60 | 2 | Sound power level equivalent to the stack for Riverside 2, excludes the Absorber Column(s). Height of the Absorber Column(s) and Stack(s) is 113m. A precautionary height of 60m was used for the Stack(s) to represent a worst-case assessment in terms of noise propagation from this component to the nearest noise sensitive receptors.
Flue Gas Fan | 85 | 9.8 | 2 | Based on similar development (professional judgement).
Pumps | 104 | 1 | 14 | WKC Group Pump Noise Calculator, 450kW rich solution pump, assumed worst-case speed range.
Pumps associated with solvent/waste tanks | 96 | 1 | 3 | WKC Group Pump Noise Calculator, 100kW pump, assumed 1500rpm speed range.
Back Pressure turbines | 85 | 6 | 2 | Based on similar development (professional judgement).
33/11kV Transformers | 78 | 6 | 2 | Based on NEMA TR1 and IEEE standards for specifying sound pressure and converting to sound power.
132/33kV Transformers | 86 | 6 | 2 | Based on NEMA TR1 and IEEE standards for specifying sound pressure and converting to sound power.
CO2 Vents | 110 | 11.6 | 2 | Based on similar development (professional judgement).
CO2 Compressors | 90 | 11 |  | The CO2 compressors are a part of the Compression Plant.
2
Refrigeration Package | 98 | 1 | 2 | Based on similar development (professional judgement).
Cooling Solution | 93 | 15 | 20 | Assumed as part of design based on similar developments.
Heat Transfer Station Cooling Fans | 98 | 7.75 | 6 | Assumed as part of design based on similar developments, height assumed to be 2.5m above the roof of building as a worst case.