## Provided Noise Source Code
Noise Source Code | Unit/ Area | Sound Pressure Level (dBA) @ 1m
NS02 | warehouse, telpher | 89
NS03 | steam / boiler room | 69
NS04 | compressed air, LP | 86
NS05 | process technology, general | 63
NS06 | process technology, CIP | 69
NS07 | process technolgy, valve island | 85
NS08 | pulver solution | 63
NS09 | water house | 68
NS10 | incoming warehouse, raw auxiliary operating materials | 70
NS11 | filling and packing line, mixer & flash pasteurizer | 85
NS12 | sugar dissolver | 80
NS13 | low voltage distribution | 80
NS14 | warehouse, general | 63
NS15 | filling and packing line, general | 85
NS16 | sugar delivery | 89
NS17 | ventilating systems | 60
NS20 | compressed air, hp | 85
NS23 | chiller | 90
NS25 | filling and packing line, preform supply | 79
NS26 | workshop, general | 80
NS27 | filling and packing line, filling unit | 90
NS28 | filling and packing line, foil shrinking unit | 83
NS29 | filling and packing line, blowing station | 87
NS31 | water treatment | 84
Old Site Layout
Proposed Phase 1 & 2, used in report

## Indoor Noise Level Prediction
Room's Name | Lw |  | Cumulative Sound Pressure Level | Resultant Sound Power Level | Total Floor Area | Total Assumed Ceiling Area | Assumed Ceiling Height | Total Room's Wall Area | Total Room's Surface Area (S) | Assumed Room's Absorption Coeficient Alfa (reflective) | Total sound absorbtion (A=S * αavg) | Room's Volume | Assumed Distance to Receiver (Worst Case) | Q Factor (Directivity) | Sound Power within Room | Equivalent Absoprtion Area (A) | Room Constant (A/(1-(αavg) | Direct sound pressure level | Reverberant sound pressure level | Indoor Sound Pressure Level
| Type | Noise Source(s) Code | dB(A) |  | (m²) | (m²) | (m) | (m²) | (m²) | α | (m²) | (m3) | (m) |  | dB(A) | (m²) |  | (dBA) | (dBA) | (dBA)
Warehouse & Logistics | Lw | NS14++NS02 | 89.0109 | 97.0109 | 30336.37 | 30336.37 | 20.5 | 14282.218 | 74954.958 | 0.1 | 7495.4958 | 621895.585 | 10.25 | 2 | 97.0109 | 7495.4958 | 8328.3287 | 68.8146 | 63.8259 | 70.0106
Conveyor Loop + Outgoing Goods | Lw | NS14 | 63 | 71 | 17779.58 | 17779.58 | 10.2 | 5440.2757 | 40999.4357 | 0.1 | 4099.9436 | 181351.716 | 5.1 | 2 | 71 | 4099.9436 | 4555.4929 | 48.8668 | 40.4352 | 49.4492
NS26-Workshop | Lw | NS26 | 80 | 88 | 238.96 | 238.96 | 10.2 | 630.6999 | 1108.6199 | 0.1 | 110.862 | 2437.392 | 5.1 | 2 | 88 | 110.862 | 123.18 | 65.8668 | 73.1152 | 73.865
NS06 - CIP | Lw | NS06 | 69 | 77 | 191.66 | 191.66 | 10.2 | 564.8406 | 948.1606 | 0.1 | 94.8161 | 1954.932 | 5.1 | 2 | 77 | 94.8161 | 105.3512 | 54.8668 | 62.7942 | 63.4431
Syrup & Control Room | Lw | NS12++NS05 | 80.0858 | 88.0858 | 548.22 | 548.22 | 10.2 | 955.2952 | 2051.7352 | 0.1 | 205.1735 | 5591.844 | 5.1 | 2 | 88.0858 | 205.1735 | 227.9706 | 65.9526 | 70.5276 | 71.8269
Raw Auxiliary Operating | Lw | NS25++NS10 | 79.515 | 87.515 | 1485.75 | 1485.75 | 10.2 | 1572.6535 | 4544.1535 | 0.1 | 454.4153 | 15154.65 | 5.1 | 2 | 87.515 | 454.4153 | 504.9059 | 65.3818 | 66.5035 | 68.989
Water Treatment | Lw | NS31++NS09 | 84.1077 | 92.1077 | 611.71 | 611.71 | 10.2 | 1009.0971 | 2232.5171 | 0.1 | 223.2517 | 6239.442 | 5.1 | 2 | 92.1077 | 223.2517 | 248.0575 | 69.9745 | 74.1828 | 75.5799
Water Treatment | Lw | NS31++NS09 | 84.1077 | 92.1077 | 314.3 | 314.3 | 10.2 | 723.3231 | 1351.9231 | 0.1 | 135.1923 | 3205.86 | 5.1 | 2 | 92.1077 | 135.1923 | 150.2137 | 69.9745 | 76.3612 | 77.2596
Concrete Powder / Raw Materials | Lw | NS08++NS05 | 66.0103 | 74.0103 | 486.81 | 486.81 | 10.2 | 900.2019 | 1873.8219 | 0.1 | 187.3822 | 4965.462 | 5.1 | 2 | 74.0103 | 187.3822 | 208.2024 | 51.8771 | 56.846 | 58.0468
Folls & Labels + Raw Aux Operating Materials | Lw | NS10++NS25 | 79.515 | 87.515 | 1485.75 | 1485.75 | 10.2 | 1572.6535 | 4544.1535 | 0.1 | 454.4153 | 15154.65 | 5.1 | 2 | 87.515 | 454.4153 | 504.9059 | 65.3818 | 66.5035 | 68.989
Incoming Goods | Lw | NS10 | 70 | 78 | 299.68 | 299.68 | 10.2 | 706.2997 | 1305.6597 | 0.1 | 130.566 | 3056.736 | 5.1 | 2 | 78 | 130.566 | 145.0733 | 55.8668 | 62.4047 | 63.2752
Sugar Dissolver | Lw | NS12 | 80 | 88 | 84.5 | 84.5 | 10.2 | 375.0494 | 544.0494 | 0.1 | 54.4049 | 861.9 | 5.1 | 2 | 88 | 54.4049 | 60.4499 | 65.8668 | 76.2066 | 76.5907
Compressed Air LP/HP | Lw | NS20++NS04 | 88.539 | 96.539 | 301.36 | 301.36 | 6.8 | 472.1845 | 1074.9045 | 0.1 | 107.4904 | 2049.248 | 3.4 | 2 | 96.539 | 107.4904 | 119.4338 | 77.9276 | 81.7883 | 83.2839
Compressed Air LP/HP | Lw | NS20++NS04 | 88.539 | 96.539 | 255.52 | 255.52 | 6.8 | 434.7918 | 945.8318 | 0.1 | 94.5832 | 1737.536 | 3.4 | 2 | 96.539 | 94.5832 | 105.0924 | 77.9276 | 82.3439 | 83.6848
Filling / Emptying Zone | Lw | NS07 | 85 | 93 | 207.54 | 207.54 | 12.65 | 728.9562 | 1144.0362 | 0.1 | 114.4036 | 2625.381 | 6.325 | 2 | 93 | 114.4036 | 127.1151 | 68.997 | 77.9786 | 78.4957
Boiler Room | Lw | NS03 | 69 | 77 | 209.28 | 209.28 | 6.8 | 393.4892 | 812.0492 | 0.1 | 81.2049 | 1423.104 | 3.4 | 2 | 77 | 81.2049 | 90.2277 | 58.3886 | 63.4672 | 64.6418
Cooling Central | Lw | NS23 | 90 | 98 | 300.18 | 300.18 | 6.8 | 471.2591 | 1071.6191 | 0.1 | 107.1619 | 2041.224 | 3.4 | 2 | 98 | 107.1619 | 119.0688 | 79.3886 | 83.2626 | 84.7543
Server Room (wall only) | Lw | NS13 | 80 | 88 | 132.24 | 132.24 | 6.8 | 312.7882 | 577.2682 | 0.1 | 57.7268 | 899.232 | 3.4 | 2 | 88 | 57.7268 | 64.1409 | 69.3886 | 75.9492 | 76.8156
AVT 1+AVT 2 | Lw | NS11 (x4)++NS15 (X4)++NS27 (x4)++NS29 (X4) | 99.7001 | 107.7001 | 5680.47 | 5680.47 | 10.2 | 3075.0508 | 14435.9908 | 0.1 | 1443.5991 | 57940.794 | 5.1 | 2 | 107.7001 | 1443.5991 | 1603.999 | 85.5669 | 81.6686 | 87.0515
AVT 3 +AVT 4 | Lw | NS11 (x4)++NS15 (X4)++NS27 (x4)++NS29 (X4) | 99.7001 | 107.7001 | 6391.32 | 6391.32 | 10.2 | 3261.7858 | 16044.4258 | 0.1 | 1604.4426 | 65191.464 | 5.1 | 2 | 107.7001 | 1604.4426 | 1782.714 | 85.5669 | 81.2098 | 86.9236

## Noise Sources
Name | ID | Type | 1/3 Oktave Spectrum (dB) | [29 empty] | Source
|  |  | Weight. | 25 | 31.5 | 40 | 50 | 63 | 80 | 100 | 125 | 160 | 200 | 250 | 315 | 400 | 500 | 630 | 800 | 1000 | 1250 | 1600 | 2000 | 2500 | 3150 | 4000 | 5000 | 6300 | 8000 | 10000 | A | lin
NS17 - Ventilating System (AHU) | AHU | Lw | A |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 60 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 60 | 63.2
NS16- Sugar Delivery | Sugar | Lw | A |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 89 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 89 | 92.2
NS23 - Chiller | CHILLER | Lw | A |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 85 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 85 | 88.2
NS14-Warehouse, General | Warehouse | Lw | A |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 63 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 63 | 66.2
NS02 - Warehouse, telpher | Telpher | Lw | A |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 89 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 89 | 92.2
NS26 - Workshop | Workshop | Lw | A |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 80 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 80 | 83.2
NS06 - Process Technology, CIP | CIP | Lw | A |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 69 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 69 | 72.2
NS05 - Process Technology, General | NS05 | Lw | A |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 63 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 63 | 66.2
NS12 - Sugar Dissolver | NS12 | Lw | A |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 80 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 80 | 83.2
NS10 - Incoming Warehouse, Raw materials | NS10 | Lw | A |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 70 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 70 | 73.2
NS25 - Filling and packing line, perform supply | NS25 | Lw | A |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 79 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 79 | 82.2
NS09 - Water House | NS09 | Lw | A |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 68 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 68 | 71.2
NS31 - Water Treatment | NS31 | Lw | A |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 84 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 84 | 87.2
NS08 - Pulver Solution | NS08 | Lw | A |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 63 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 63 | 66.2
NS04 - Compressed Air | NS04 | Lw | A |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 86 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 86 | 89.2
NS20 - Compressed Air, Hp | NS20 | Lw | A |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 85 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 85 | 88.2
NS07 - Process technolgy, valve island | NS07 | Lw | A |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 85 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 85 | 88.2
Ns03 - Boiler Room | NS03 | Lw | A |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 69 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 69 | 72.2
NS23 - Chiller | NS23 | Lw | A |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 85 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 85 | 88.2
NS13 - Low Voltage distribution | NS13 | Lw | A |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 80 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 80 | 83.2
AHU-01-Casing | AHU_01_Casing | Lw (c) |  |  | 8 |  |  | 67 |  |  | 74 |  |  | 62 |  |  | 63 |  |  | 54 |  |  | 48 |  |  | 40 |  |  | 49 |  | 63.4 | 75.3 | Dalair Ltd
AHU-01-ATMOSPHERIC-supply-fan | AHU_01_ATMOSPHERIC_supply_fan | Lw |  |  | 0 |  |  | 74 |  |  | 77 |  |  | 76 |  |  | 73 |  |  | 68 |  |  | 66 |  |  | 64 |  |  | 62 |  | 75.1 | 81.7 | Dalair Ltd
AHU-01-ATMOSPHERIC-extract-fan | AHU_01_ATMOSPHERIC_extract_fan | Lw |  |  | 0 |  |  | 75 |  |  | 85 |  |  | 82 |  |  | 81 |  |  | 80 |  |  | 79 |  |  | 76 |  |  | 71 |  | 85.5 | 89.4 | Dalair Ltd
AHU-02-Casing | AHU_02_Casing | Lw (c) |  |  | 8 |  |  | 68 |  |  | 73 |  |  | 65 |  |  | 64 |  |  | 58 |  |  | 54 |  |  | 48 |  |  | 54 |  | 65.3 | 75.2 | Dalair Ltd
AHU-02-ATMOSPHERIC-supply-fan | AHU_02_ATMOSPHERIC_supply_fan | Lw |  |  | 0 |  |  | 70 |  |  | 81 |  |  | 77 |  |  | 73 |  |  | 70 |  |  | 67 |  |  | 63 |  |  | 61 |  | 76 | 83.5 | Dalair Ltd
AHU-02-ATMOSPHERIC-extract-fan | AHU_02_ATMOSPHERIC_extract_fan | Lw |  |  | 0 |  |  | 77 |  |  | 85 |  |  | 82 |  |  | 81 |  |  | 81 |  |  | 79 |  |  | 77 |  |  | 72 |  | 86 | 89.6 | Dalair Ltd
AHU-03-Casing | AHU_03_Casing | Lw (c) |  |  | 8 |  |  | 66 |  |  | 75 |  |  | 63 |  |  | 64 |  |  | 56 |  |  | 49 |  |  | 40 |  |  | 48 |  | 64.5 | 76.1 | Dalair Ltd
AHU-03-ATMOSPHERIC-supply-fan | AHU_03_ATMOSPHERIC_supply_fan | Lw |  |  | 0 |  |  | 69 |  |  | 83 |  |  | 77 |  |  | 73 |  |  | 70 |  |  | 67 |  |  | 63 |  |  | 60 |  | 76.2 | 84.7 | Dalair Ltd
AHU-03-ATMOSPHERIC-extract-fan | AHU_03_ATMOSPHERIC_extract_fan | Lw |  |  | 0 |  |  | 76 |  |  | 86 |  |  | 79 |  |  | 80 |  |  | 77 |  |  | 73 |  |  | 69 |  |  | 66 |  | 82 | 88.4 | Dalair Ltd
AHU-04-Casing | AHU_04_Casing | Lw (c) |  |  | 8 |  |  | 81 |  |  | 84 |  |  | 77 |  |  | 81 |  |  | 74 |  |  | 70 |  |  | 60 |  |  | 66 |  | 80.6 | 87.7 | Dalair Ltd
AHU-04-ATMOSPHERIC-supply-fan | AHU_04_ATMOSPHERIC_supply_fan | Lw |  |  | 0 |  |  | 78 |  |  | 90 |  |  | 85 |  |  | 84 |  |  | 88 |  |  | 87 |  |  | 83 |  |  | 79 |  | 92.5 | 94.8 | Dalair Ltd
AHU-04-ATMOSPHERIC-extract-fan | AHU_04_ATMOSPHERIC_extract_fan | Lw |  |  | 0 |  |  | 83 |  |  | 91 |  |  | 89 |  |  | 93 |  |  | 92 |  |  | 90 |  |  | 84 |  |  | 79 |  | 96.4 | 98.6 | Dalair Ltd
AHU-05-Casing | AHU_05_Casing | Lw (c) |  |  | 8 |  |  | 82 |  |  | 82 |  |  | 80 |  |  | 81 |  |  | 73 |  |  | 69 |  |  | 60 |  |  | 65 |  | 80.5 | 87.6 | Dalair Ltd
AHU-05-ATMOSPHERIC-supply-fan | AHU_05_ATMOSPHERIC_supply_fan | Lw |  |  | 0 |  |  | 79 |  |  | 88 |  |  | 89 |  |  | 85 |  |  | 87 |  |  | 86 |  |  | 82 |  |  | 79 |  | 91.9 | 94.7 | Dalair Ltd
AHU-05-ATMOSPHERIC-extract-fan | AHU_05_ATMOSPHERIC_extract_fan | Lw |  |  | 0 |  |  | 84 |  |  | 91 |  |  | 91 |  |  | 94 |  |  | 91 |  |  | 89 |  |  | 84 |  |  | 79 |  | 96.1 | 98.8 | Dalair Ltd
AHU-06-Casing | AHU_06_Casing | Lw (c) |  |  | 8 |  |  | 76 |  |  | 75 |  |  | 75 |  |  | 78 |  |  | 72 |  |  | 68 |  |  | 60 |  |  | 65 |  | 78 | 82.8 | Dalair Ltd
AHU-06-ATMOSPHERIC-supply-fan | AHU_06_ATMOSPHERIC_supply_fan | Lw |  |  | 0 |  |  | 73 |  |  | 80 |  |  | 87 |  |  | 82 |  |  | 85 |  |  | 85 |  |  | 81 |  |  | 78 |  | 90.4 | 92 | Dalair Ltd
AHU-06-ATMOSPHERIC-extract-fan | AHU_06_ATMOSPHERIC_extract_fan | Lw |  |  | 0 |  |  | 80 |  |  | 88 |  |  | 91 |  |  | 91 |  |  | 88 |  |  | 86 |  |  | 80 |  |  | 74 |  | 93.2 | 96.4 | Dalair Ltd
AHU-07-Casing | AHU_07_Casing | Lw (c) |  |  | 8 |  |  | 78 |  |  | 81 |  |  | 77 |  |  | 80 |  |  | 71 |  |  | 67 |  |  | 57 |  |  | 64 |  | 79 | 85.5 | Dalair Ltd
AHU-07-ATMOSPHERIC-supply-fan | AHU_07_ATMOSPHERIC_supply_fan | Lw |  |  | 0 |  |  | 76 |  |  | 88 |  |  | 86 |  |  | 84 |  |  | 85 |  |  | 83 |  |  | 79 |  |  | 77 |  | 89.6 | 92.9 | Dalair Ltd
AHU-07-ATMOSPHERIC-extract-fan | AHU_07_ATMOSPHERIC_extract_fan | Lw |  |  | 0 |  |  | 80 |  |  | 88 |  |  | 91 |  |  | 91 |  |  | 88 |  |  | 87 |  |  | 81 |  |  | 76 |  | 93.6 | 96.6 | Dalair Ltd
AHU-08-Casing | AHU_08_Casing | Lw (c) |  |  | 8 |  |  | 75 |  |  | 80 |  |  | 75 |  |  | 80 |  |  | 72 |  |  | 69 |  |  | 57 |  |  | 64 |  | 79.2 | 84.6 | Dalair Ltd
AHU-08-ATMOSPHERIC-supply-fan | AHU_08_ATMOSPHERIC_supply_fan | Lw |  |  | 0 |  |  | 73 |  |  | 84 |  |  | 82 |  |  | 84 |  |  | 86 |  |  | 85 |  |  | 79 |  |  | 77 |  | 90.4 | 91.8 | Dalair Ltd
AHU-08-ATMOSPHERIC-extract-fan | AHU_08_ATMOSPHERIC_extract_fan | Lw |  |  | 0 |  |  | 79 |  |  | 89 |  |  | 92 |  |  | 92 |  |  | 87 |  |  | 86 |  |  | 79 |  |  | 76 |  | 93.3 | 97 | Dalair Ltd
AHU-09-Casing | AHU_09_Casing | Lw (c) |  |  | 8 |  |  | 74 |  |  | 76 |  |  | 72 |  |  | 76 |  |  | 69 |  |  | 65 |  |  | 56 |  |  | 62 |  | 75.6 | 81.2 | Dalair Ltd
AHU-09-ATMOSPHERIC-supply-fan | AHU_09_ATMOSPHERIC_supply_fan | Lw |  |  | 0 |  |  | 72 |  |  | 83 |  |  | 84 |  |  | 80 |  |  | 83 |  |  | 82 |  |  | 78 |  |  | 75 |  | 87.8 | 90.1 | Dalair Ltd
AHU-09-ATMOSPHERIC-extract-fan | AHU_09_ATMOSPHERIC_extract_fan | Lw |  |  | 0 |  |  | 76 |  |  | 85 |  |  | 85 |  |  | 88 |  |  | 88 |  |  | 86 |  |  | 80 |  |  | 76 |  | 92.2 | 93.9 | Dalair Ltd
SF-01-Casing | SF_01_Casing | Lw (c) |  |  | 8 |  |  | 70 |  |  | 70 |  |  | 71 |  |  | 72 |  |  | 65 |  |  | 57 |  |  | 49 |  |  | 57 |  | 71.4 | 77.2 | Dalair Ltd
SF-01-ATMOSPHERIC-supply-fan | SF_01_ATMOSPHERIC_supply_fan | Lw |  |  | 0 |  |  | 74 |  |  | 80 |  |  | 87 |  |  | 82 |  |  | 82 |  |  | 80 |  |  | 76 |  |  | 75 |  | 87.1 | 90.5 | Dalair Ltd
EF-01-Casing | EF_01_Casing | Lw (c) |  |  | 8 |  |  | 67 |  |  | 73 |  |  | 69 |  |  | 70 |  |  | 64 |  |  | 56 |  |  | 48 |  |  | 56 |  | 69.9 | 76.6 | Dalair Ltd
EF-01-ATMOSPHERIC-extract-fan | EF_01_ATMOSPHERIC_extract_fan | Lw |  |  | 0 |  |  | 79 |  |  | 88 |  |  | 89 |  |  | 90 |  |  | 90 |  |  | 84 |  |  | 80 |  |  | 77 |  | 93.2 | 95.9 | Dalair Ltd
SF-02-Casing | SF_02_Casing | Lw (c) |  |  | 8 |  |  | 70 |  |  | 74 |  |  | 71 |  |  | 73 |  |  | 64 |  |  | 59 |  |  | 50 |  |  | 56 |  | 72 | 78.5 | Dalair Ltd
SF-02-ATMOSPHERIC-supply-fan | SF_02_ATMOSPHERIC_supply_fan | Lw |  |  | 0 |  |  | 75 |  |  | 86 |  |  | 86 |  |  | 82 |  |  | 84 |  |  | 82 |  |  | 78 |  |  | 75 |  | 88.5 | 91.7 | Dalair Ltd
EF-02-Casing | EF_02_Casing | Lw (c) |  |  | 8 |  |  | 68 |  |  | 73 |  |  | 72 |  |  | 70 |  |  | 61 |  |  | 57 |  |  | 47 |  |  | 53 |  | 69.8 | 77.3 | Dalair Ltd
EF-02-ATMOSPHERIC-extract-fan | EF_02_ATMOSPHERIC_extract_fan | Lw |  |  | 0 |  |  | 80 |  |  | 88 |  |  | 92 |  |  | 90 |  |  | 87 |  |  | 85 |  |  | 79 |  |  | 74 |  | 92.4 | 96.3 | Dalair Ltd
EF-03-Casing | EF_03_Casing | Lw (c) |  |  | 8 |  |  | 68 |  |  | 73 |  |  | 72 |  |  | 70 |  |  | 61 |  |  | 57 |  |  | 47 |  |  | 53 |  | 69.8 | 77.3 | Dalair Ltd
EF-03-ATMOSPHERIC-extract-fan | EF_03_ATMOSPHERIC_extract_fan | Lw |  |  | 0 |  |  | 80 |  |  | 88 |  |  | 92 |  |  | 90 |  |  | 87 |  |  | 85 |  |  | 79 |  |  | 74 |  | 92.4 | 96.3 | Dalair Ltd
EF-04-Casing | EF_04_Casing | Lw (c) |  |  | 8 |  |  | 68 |  |  | 73 |  |  | 72 |  |  | 70 |  |  | 61 |  |  | 57 |  |  | 47 |  |  | 53 |  | 69.8 | 77.3 | Dalair Ltd
EF-04-ATMOSPHERIC-extract-fan | EF_04_ATMOSPHERIC_extract_fan | Lw |  |  | 0 |  |  | 80 |  |  | 88 |  |  | 92 |  |  | 90 |  |  | 87 |  |  | 85 |  |  | 79 |  |  | 74 |  | 92.4 | 96.3 | Dalair Ltd
EF-05-Casing | EF_05_Casing | Lw (c) |  |  | 8 |  |  | 68 |  |  | 73 |  |  | 72 |  |  | 70 |  |  | 61 |  |  | 57 |  |  | 47 |  |  | 53 |  | 69.8 | 77.3 | Dalair Ltd
EF-05-ATMOSPHERIC-extract-fan | EF_05_ATMOSPHERIC_extract_fan | Lw |  |  | 0 |  |  | 80 |  |  | 88 |  |  | 92 |  |  | 90 |  |  | 87 |  |  | 85 |  |  | 79 |  |  | 74 |  | 92.4 | 96.3 | Dalair Ltd
COND-01-Northern-Offices-Condenser-Compound | COND_01 | Lw | A |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 86.3 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 86.3 | 89.5 | Daikin-REYQ24U (REYQ16U)+(REYQ8U)
COND-02-Western-Condenser-Compound | COND_02 | Lw | A |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 83.8 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 83.8 | 87 | Daikin-REYQ18U
COND-03-Office | COND_03 | Lw | A |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 62 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 62 | 65.2 | Daikin-RXM
COND-04-Server Room | COND_04 | Lw | A |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 70 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 70 | 73.2 | Daikin-RZAG
COND-05-Server Room | COND_05 | Lw | A |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 70 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 70 | 73.2 | Daikin-RZAG
COND-06-IT Storage | COND_06 | Lw | A |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 70 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 70 | 73.2 | Daikin-RZAG
COND-07-IT Storage | COND_07 | Lw | A |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 70 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 70 | 73.2 | Daikin-RZAG
COND-08-UPS Room | COND_08 | Lw | A |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 62 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 62 | 65.2 | DMOUCD021E
COND-09-Server Room | COND_09 | Lw | A |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 70 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 70 | 73.2 | DMOUCD021
COND-10-Server Room | COND_10 | Lw | A |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 70 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 70 | 73.2 | DMOUCD021
REF-01-Chilled-Concentrate-Storage | REF-01 | Lw (c) | A |  | 28 |  |  | 28 |  |  | 28 |  |  | 28 |  |  | 72 |  |  | 28 |  |  | 28 |  |  | 28 |  |  | 28 |  | 72 | 75.9 | Mastair
Lidl Depart | Depart | Lw (c) | [5 empty] | 104 |  |  | 94 |  |  | 92 |  |  | 93 |  |  | 93 |  |  | 90 |  |  | 83 |  |  | 74 |  | 96.9 | 105.4
Lidl Arrive | Arrive | Lw (c) | [5 empty] | 111 |  |  | 97 |  |  | 91 |  |  | 92 |  |  | 92 |  |  | 89 |  |  | 83 |  |  | 73 |  | 96.3 | 111.3
Lidl Unloading | Unloading | Lw (c) | [5 empty] | 91 |  |  | 85 |  |  | 79 |  |  | 79 |  |  | 77 |  |  | 75 |  |  | 71 |  |  | 53 |  | 82.2 | 92.6

## Line Sources - Vehicle movement
Name | M. | ID | Result. PWL |  |  | Result. PWL' |  |  | Lw / Li |  |  | Correction |  |  | Sound Reduction |  | Attenuation | Operating Time |  |  | K0 | Freq. | Direct. | Moving Pt. Src
|  |  | Day | Evening | Night | Day | Evening | Night | Type | Value | norm. | Day | Evening | Night | R | Area |  | Day | Special | Night |  |  |  | Number |  |  | Speed
|  |  | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) |  |  | dB(A) | dB(A) | dB(A) | dB(A) |  | (m²) |  | (min) | (min) | (min) | (dB) | (Hz) |  | Day | Evening | Night | (km/h)
In going Goods |  |  | 93.3 | -15.7 | 87.3 | 65.3 | -43.7 | 59.3 | PWL-Pt | Arrive |  | 41 | 0 | 10 | [6 empty] | 0 |  | (none) | 8 | 0 | 2 | 10
Incoming Goods |  |  | 88.6 | -17.5 | 82.5 | 62.3 | -43.7 | 56.3 | PWL-Pt | Arrive |  | 41 | 0 | 10 | [6 empty] | 0 |  | (none) | 4 | 0 | 1 | 10
CO2/N2 H2O Vehicle Supply |  |  | 85.9 | -14.1 | 85.9 | 56.3 | -43.7 | 56.3 | PWL-Pt | Arrive |  | 41 | 0 | 10 | [6 empty] | 0 |  | (none) | 1 | 0 | 1 | 10
Out going Goods |  |  | 96.7 | -17.1 | 93.7 | 70.7 | -43.1 | 67.7 | PWL-Pt | Depart |  | 41 | 0 | 10 | [6 empty] | 0 |  | (none) | 24 | 0 | 12 | 10
In going Goods |  |  | 93.6 | -15.5 | 87.5 | 65.3 | -43.7 | 59.3 | PWL-Pt | Arrive |  | 41 | 0 | 10 | [6 empty] | 0 |  | (none) | 8 | 0 | 2 | 10
In going Goods |  |  | 93.3 | -15.7 | 87.3 | 65.3 | -43.7 | 59.3 | PWL-Pt | Arrive |  | 41 | 0 | 10 | [6 empty] | 0 |  | (none) | 8 | 0 | 2 | 10

## Buildings Heights
Name | M. | ID | RB | Residents | Absorption | Height
Begin
(m)
|  | Existing Industrial Building | x | 0 | 0.21 | 15 | r | 420033 | 332288
|  | Existing Industrial Building | x | 0 | 0.21 | 15 | r | 419916 | 332446
|  | Existing Industrial Building | x | 0 | 0.21 | 7 | r | 419832 | 332475
|  | Existing Industrial Building | x | 0 | 0.21 | 7 | r | 419880 | 332519
|  | Existing Industrial Building | x | 0 | 0.21 | 7 | r | 419884 | 332543
|  | Existing Industrial Building | x | 0 | 0.21 | 7 | r | 419802 | 332383
|  | Existing Industrial Building | x | 0 | 0.21 | 7 | r | 420376 | 332204
|  | Existing Industrial Building | x | 0 | 0.37 | 7 | r | 420264 | 332806
Receiver 2 |  | Nearest Residential | x | 0 | 0.37 | 7 | r | 420236 | 332796
Receiver 1 |  | Existing Industrial Building | x | 0 | 0.37 | 8 | r | 420148 | 332823
|  | Existing Industrial Building | x | 0 | 0.21 | 7 | r | 420586 | 332270
|  | Existing Industrial Building | x | 0 | 0.21 | 7 | r | 420601 | 332249
|  | Existing Industrial Building | x | 0 | 0.21 | 7 | r | 420660 | 332324
|  | ACL_Proposed Industry Silos | x | 0 | 0.21 | 12.5 | r | 420061 | 332659
|  | ACL_Proposed Industry Silos | x | 0 | 0.21 | 12.5 | r | 420056 | 332647
|  | ACL_Existing Buildings | x | 0 | 0.21 | 15 | r | 420401 | 332377
|  | ACL_Existing Buildings | x | 0 | 0.21 | 15 | r | 420390 | 332341
|  | ACL_Existing Buildings | x | 0 | 0.21 | 15 | r | 420360 | 332310
|  | ACL_Existing Buildings | x | 0 | 0.21 | 7 | r | 419933 | 332581
|  | ACL_Existing Buildings | x | 0 | 0.21 | 7 | r | 419944 | 332606
|  | ACL_Existing Buildings | x | 0 | 0.21 | 7 | r | 419950 | 332631
|  | ACL_Existing Buildings | x | 0 | 0.21 | 7 | r | 419972 | 332701
|  | ACL_Existing Buildings | x | 0 | 0.21 | 7 | r | 419980 | 332737
|  | ACL_Existing Buildings | x | 0 | 0.21 | 7 | r | 419966 | 332671
Receiver 3 |  | Nearest Residential | x | 0 | 0.21 | 7 | r | 420252 | 332784
|  | ACL_Proposed Industry | x | 0 | 0.21 |  |  | 420097 | 332511
|  | ACL_Proposed Industry | x | 0 | 0.21 |  |  | 420159 | 332601
|  | ACL_Proposed Industry | x | 0 | 0.21 |  |  | 420212 | 332690
|  | ACL_Proposed Industry | x | 0 | 0.21 |  |  | 420253 | 332683
Receiver 4 |  | Woodland Farm | x | 0 | 0.21 | 7 | r | 419950 | 332535

## Area Noise Sources - Roof & Chi
Name | M. | ID | Result. PWL |  |  | Result. PWL'' |  |  | Lw / Li |  |  | Correction |  |  | Sound Reduction |  | Attenuation | Operating Time |  |  | K0 | Freq. | Direct. | Moving Pt. Src
|  |  | Day | Evening | Night | Day | Evening | Night | Type | Value | norm. | Day | Evening | Night | R | Area |  | Day | Special | Night |  |  |  | Number
|  |  | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) |  |  | dB(A) | dB(A) | dB(A) | dB(A) |  | (m²) |  | (min) | (min) | (min) | (dB) | (Hz) |  | Day | Evening | Night
Warehouse & Logistics |  |  | 76.6 | 76.6 | 76.6 | 35 | 35 | 35 | Li | 70 |  | 0 | 0 | 0 | 31 | 14327.18 |  |  |  |  | 0 | 500 | (none)
NS26-Workshop |  |  | 62.5 | 62.5 | 62.5 | 39 | 39 | 39 | Li | 74 |  | 0 | 0 | 0 | 31 | 222.85 |  |  |  |  | 0 | 500 | (none)
Syrup & Control Room |  |  | 64.3 | 64.3 | 64.3 | 37 | 37 | 37 | Li | 72 |  | 0 | 0 | 0 | 31 | 536.32 |  |  |  |  | 0 | 500 | (none)
Folls & LAbels _Raw Aux Operating Materials |  |  | 66.6 | 66.6 | 66.6 | 34 | 34 | 34 | Li | 69 |  | 0 | 0 | 0 | 31 | 1809.69 |  |  |  |  | 0 | 500 | (none)
Water Treatment |  |  | 66.8 | 66.8 | 66.8 | 42 | 42 | 42 | Li | 77 |  | 0 | 0 | 0 | 31 | 304.55 |  |  |  |  | 0 | 500 | (none)
Water Treatment |  |  | 68.8 | 68.8 | 68.8 | 41 | 41 | 41 | Li | 76 |  | 0 | 0 | 0 | 31 | 602.34 |  |  |  |  | 0 | 500 | (none)
Concrete Powder / Raw Materials |  |  | 49.8 | 49.8 | 49.8 | 23 | 23 | 23 | Li | 58 |  | 0 | 0 | 0 | 31 | 477.55 |  |  |  |  | 0 | 500 | (none)
Raw Auxiliary Operating |  |  | 65.6 | 65.6 | 65.6 | 34 | 34 | 34 | Li | 69 |  | 0 | 0 | 0 | 31 | 1460.03 |  |  |  |  | 0 | 500 | (none)
Incoming Goods |  |  | 52.8 | 52.8 | 52.8 | 28 | 28 | 28 | Li | 63 |  | 0 | 0 | 0 | 31 | 299.45 |  |  |  |  | 0 | 500 | (none)
Sugar Dissolver |  |  | 61.2 | 61.2 | 61.2 | 42 | 42 | 42 | Li | 77 |  | 0 | 0 | 0 | 31 | 83.76 |  |  |  |  | 0 | 500 | (none)
Compressed Air LP/HP |  |  | 73 | 73 | 73 | 49 | 49 | 49 | Li | 84 |  | 0 | 0 | 0 | 31 | 251.11 |  |  |  |  | 0 | 500 | (none)
Compressed Air LP/HP |  |  | 72.7 | 72.7 | 72.7 | 48 | 48 | 48 | Li | 83 |  | 0 | 0 | 0 | 31 | 295.46 |  |  |  |  | 0 | 500 | (none)
Boiler Room |  |  | 51.6 | 51.6 | 51.6 | 30 | 30 | 30 | Li | 65 |  | 0 | 0 | 0 | 31 | 145.8 |  |  |  |  | 0 | 500 | (none)
Cooling Central |  |  | 74.7 | 74.7 | 74.7 | 50 | 50 | 50 | Li | 85 |  | 0 | 0 | 0 | 31 | 292.09 |  |  |  |  | 0 | 500 | (none)
AVT 1+AVT 2 |  |  | 89.8 | 89.8 | 89.8 | 52 | 52 | 52 | Li | 87 |  | 0 | 0 | 0 | 31 | 6017.45 |  |  |  |  | 0 | 500 | (none)
AVT 3 +AVT 4 |  |  | 90.5 | 90.5 | 90.5 | 52 | 52 | 52 | Li | 87 |  | 0 | 0 | 0 | 31 | 7040.21 |  |  |  |  | 0 | 500 | (none)
NS06 - CIP |  |  | 50.6 | 50.6 | 50.6 | 28 | 28 | 28 | Li | 63 |  | 0 | 0 | 0 | 31 | 183.4 |  |  |  |  | 0 | 500 | (none)
Conveyor Loop + Outgoing Goods |  |  | 49.8 | 49.8 | 49.8 | 14 | 14 | 14 | Li | 49 |  | 0 | 0 | 0 | 31 | 3823.49 |  |  |  |  | 0 | 500 | (none)
Chillers Area N23 at 32 oC & Attenuation |  |  | 82.2 | 90.2 | 82.2 | 67.4 | 75.4 | 67.4 | Lw | 90.2 |  | -8 | 0 | -8 | [6 empty] | 0 | 500 | (none)

## Vertical Noise Sources - Walls
Name | M. | ID | Result. PWL |  |  | Result. PWL'' |  |  | Lw / Li |  |  | Correction |  |  | Sound Reduction |  | Attenuation | Operating Time |  |  | K0 | Freq. | Direct.
|  |  | Day | Evening | Night | Day | Evening | Night | Type | Value | norm. | Day | Evening | Night | R | Area |  | Day | Special | Night
|  |  | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) |  |  | dB(A) | dB(A) | dB(A) | dB(A) |  | (m²) |  | (min) | (min) | (min) | (dB) | (Hz)
AVT 1+AVT 2 |  |  | 81.3 | 81.3 | 81.3 | 52 | 52 | 52 | Li | 87 |  | 0 | 0 | 0 | 31 | 848.7 |  | 60 | 0 | 60 | 3 | 500 | (none)
AVT 3 +AVT 4 |  |  | 81.7 | 81.7 | 81.7 | 52 | 52 | 52 | Li | 87 |  | 0 | 0 | 0 | 31 | 943.27 |  | 60 | 0 | 60 | 3 | 500 | (none)
Warehouse & Logistics |  |  | 69.5 | 69.5 | 69.5 | 35 | 35 | 35 | Li | 70 |  | 0 | 0 | 0 | 31 | 2803.09 |  | 60 | 0 | 60 | 3 | 500 | (none)
Warehouse & Logistics |  |  | 68.3 | 68.3 | 68.3 | 35 | 35 | 35 | Li | 70 |  | 0 | 0 | 0 | 31 | 2160.64 |  | 60 | 0 | 60 | 3 | 500 | (none)
Warehouse & Logistics |  |  | 60.3 | 60.3 | 60.3 | 35 | 35 | 35 | Li | 70 |  | 0 | 0 | 0 | 31 | 338.64 |  | 60 | 0 | 60 | 3 | 500 | (none)
Warehouse & Logistics |  |  | 54.5 | 54.5 | 54.5 | 35 | 35 | 35 | Li | 70 |  | 0 | 0 | 0 | 31 | 88.84 |  | 60 | 0 | 60 | 3 | 500 | (none)
Sugar Dissolver |  |  | 60.5 | 60.5 | 60.5 | 42 | 42 | 42 | Li | 77 |  | 0 | 0 | 0 | 31 | 71.52 |  | 60 | 0 | 60 | 3 | 500 | (none)
Incoming Goods |  |  | 51.5 | 51.5 | 51.5 | 28 | 28 | 28 | Li | 63 |  | 0 | 0 | 0 | 31 | 223.88 |  | 60 | 0 | 60 | 3 | 500 | (none)
Boiler Room |  |  | 49.2 | 49.2 | 49.2 | 30 | 30 | 30 | Li | 65 |  | 0 | 0 | 0 | 31 | 82.42 |  | 60 | 0 | 60 | 3 | 500 | (none)
Boiler Room |  |  | 46 | 46 | 46 | 30 | 30 | 30 | Li | 65 |  | 0 | 0 | 0 | 31 | 40.15 |  | 60 | 0 | 60 | 3 | 500 | (none)
Compressed Air LP/HP |  |  | 68.4 | 68.4 | 68.4 | 49 | 49 | 49 | Li | 84 |  | 0 | 0 | 0 | 31 | 87.62 |  | 60 | 0 | 60 | 3 | 500 | (none)
Compressed Air LP/HP |  |  | 66.4 | 66.4 | 66.4 | 48 | 48 | 48 | Li | 83 |  | 0 | 0 | 0 | 31 | 68.44 |  | 60 | 0 | 60 | 3 | 500 | (none)
Folls & LAbels _Raw Aux Operating Materials |  |  | 59.8 | 59.8 | 59.8 | 34 | 34 | 34 | Li | 69 |  | 0 | 0 | 0 | 31 | 383.54 |  | 60 | 0 | 60 | 3 | 500 | (none)
Warehouse & Logistics |  |  | 65.7 | 65.7 | 65.7 | 35 | 35 | 35 | Li | 70 |  | 0 | 0 | 0 | 31 | 1170.81 |  | 60 | 0 | 60 | 3 | 500 | (none)
Warehouse & Logistics |  |  | 65.1 | 65.1 | 65.1 | 35 | 35 | 35 | Li | 70 |  | 0 | 0 | 0 | 31 | 1020.05 |  | 60 | 0 | 60 | 3 | 500 | (none)
Loading Dock 1 |  |  | 74.9 | 74.9 | 74.9 | 66 | 66 | 66 | Li | 70 |  | 0 | 0 | 0 | 0 | 7.7 |  | 60 | 0 | 60 | 3 | 500 | (none)
Loading Dock 2 |  |  | 74.7 | 74.7 | 74.7 | 66 | 66 | 66 | Li | 70 |  | 0 | 0 | 0 | 0 | 7.46 |  | 60 | 0 | 60 | 3 | 500 | (none)
Loading Dock 3 |  |  | 74.8 | 74.8 | 74.8 | 66 | 66 | 66 | Li | 70 |  | 0 | 0 | 0 | 0 | 7.57 |  | 60 | 0 | 60 | 3 | 500 | (none)
Loading Dock 4 |  |  | 75 | 75 | 75 | 66 | 66 | 66 | Li | 70 |  | 0 | 0 | 0 | 0 | 7.86 |  | 60 | 0 | 60 | 3 | 500 | (none)
Loading Dock 5 |  |  | 74.8 | 74.8 | 74.8 | 66 | 66 | 66 | Li | 70 |  | 0 | 0 | 0 | 0 | 7.61 |  | 60 | 0 | 60 | 3 | 500 | (none)
Loading Dock 6 |  |  | 74.7 | 74.7 | 74.7 | 66 | 66 | 66 | Li | 70 |  | 0 | 0 | 0 | 0 | 7.43 |  | 60 | 0 | 60 | 3 | 500 | (none)
Loading Dock 7 |  |  | 74.8 | 74.8 | 74.8 | 66 | 66 | 66 | Li | 70 |  | 0 | 0 | 0 | 0 | 7.58 |  | 60 | 0 | 60 | 3 | 500 | (none)
Loading Dock 8 |  |  | 74.7 | 74.7 | 74.7 | 66 | 66 | 66 | Li | 70 |  | 0 | 0 | 0 | 0 | 7.45 |  | 60 | 0 | 60 | 3 | 500 | (none)
Loading Dock 9 |  |  | 74.8 | 74.8 | 74.8 | 66 | 66 | 66 | Li | 70 |  | 0 | 0 | 0 | 0 | 7.53 |  | 60 | 0 | 60 | 3 | 500 | (none)
Loading Dock 10 |  |  | 74.8 | 74.8 | 74.8 | 66 | 66 | 66 | Li | 70 |  | 0 | 0 | 0 | 0 | 7.58 |  | 60 | 0 | 60 | 3 | 500 | (none)
Loading Dock 11 |  |  | 74.8 | 74.8 | 74.8 | 66 | 66 | 66 | Li | 70 |  | 0 | 0 | 0 | 0 | 7.58 |  | 60 | 0 | 60 | 3 | 500 | (none)
Loading Dock 12 |  |  | 74.8 | 74.8 | 74.8 | 66 | 66 | 66 | Li | 70 |  | 0 | 0 | 0 | 0 | 7.56 |  | 60 | 0 | 60 | 3 | 500 | (none)
Loading Dock 13 |  |  | 74.8 | 74.8 | 74.8 | 66 | 66 | 66 | Li | 70 |  | 0 | 0 | 0 | 0 | 7.58 |  | 60 | 0 | 60 | 3 | 500 | (none)
Loading Dock 14 |  |  | 74.8 | 74.8 | 74.8 | 66 | 66 | 66 | Li | 70 |  | 0 | 0 | 0 | 0 | 7.62 |  | 60 | 0 | 60 | 3 | 500 | (none)
Loading Dock 15 |  |  | 74.8 | 74.8 | 74.8 | 66 | 66 | 66 | Li | 70 |  | 0 | 0 | 0 | 0 | 7.56 |  | 60 | 0 | 60 | 3 | 500 | (none)
Loading Dock 16 |  |  | 74.7 | 74.7 | 74.7 | 66 | 66 | 66 | Li | 70 |  | 0 | 0 | 0 | 0 | 7.37 |  | 60 | 0 | 60 | 3 | 500 | (none)
Loading Dock 17 |  |  | 74.7 | 74.7 | 74.7 | 66 | 66 | 66 | Li | 70 |  | 0 | 0 | 0 | 0 | 7.41 |  | 60 | 0 | 60 | 3 | 500 | (none)
Loading Dock 18 |  |  | 74.8 | 74.8 | 74.8 | 66 | 66 | 66 | Li | 70 |  | 0 | 0 | 0 | 0 | 7.64 |  | 60 | 0 | 60 | 3 | 500 | (none)
Loading Dock 19 |  |  | 74.8 | 74.8 | 74.8 | 66 | 66 | 66 | Li | 70 |  | 0 | 0 | 0 | 0 | 7.54 |  | 60 | 0 | 60 | 3 | 500 | (none)
Loading Dock 20 |  |  | 74.8 | 74.8 | 74.8 | 66 | 66 | 66 | Li | 70 |  | 0 | 0 | 0 | 0 | 7.62 |  | 60 | 0 | 60 | 3 | 500 | (none)
Loading Dock 21 |  |  | 74.8 | 74.8 | 74.8 | 66 | 66 | 66 | Li | 70 |  | 0 | 0 | 0 | 0 | 7.54 |  | 60 | 0 | 60 | 3 | 500 | (none)
Loading Dock 22 |  |  | 77.2 | 77.2 | 77.2 | 66 | 66 | 66 | Li | 70 |  | 0 | 0 | 0 | 0 | 13.21 |  | 60 | 0 | 60 | 3 | 500 | (none)
Loading Dock 23 |  |  | 77.1 | 77.1 | 77.1 | 66 | 66 | 66 | Li | 70 |  | 0 | 0 | 0 | 0 | 13.01 |  | 60 | 0 | 60 | 3 | 500 | (none)
Warehouse & Logistics |  |  | 66.8 | 66.8 | 66.8 | 35 | 35 | 35 | Li | 70 |  | 0 | 0 | 0 | 31 | 1516.81 |  | 60 | 0 | 60 | 3 | 500 | (none)

## Point Sources
Name | M. | ID | Result. PWL |  |  | Lw / Li |  |  | Correction |  |  | Sound Reduction |  | Attenuation | Operating Time |  |  | K0 | Freq. | Direct. | Height |  | Coordinates
|  |  | Day | Evening | Night | Type | Value | norm. | Day | Evening | Night | R | Area |  | Day | Special | Night | [5 empty] | X | Y | Z
|  |  | (dBA) | (dBA) | (dBA) |  |  | dB(A) | dB(A) | dB(A) | dB(A) |  | (m²) |  | (min) | (min) | (min) | (dB) | (Hz) |  | (m) |  | (m) | (m) | (m)
AHU-01-ATMOSPHERIC-extract-fan |  |  | 61.9 | 61.9 | 61.9 | Lw | AHU_01_ATMOSPHERIC_supply_fan |  | 0 | 0 | 0 |  |  | NC40 |  |  |  | 0 |  | (none) | 1.1 | g | 420266.61 | 332677.24 | 79.4
AHU-01-ATMOSPHERIC-supply-fan |  |  | 61.9 | 61.9 | 61.9 | Lw | AHU_01_ATMOSPHERIC_supply_fan |  | 0 | 0 | 0 |  |  | NC40 |  |  |  | 0 |  | (none) | 1.1 | g | 420271.15 | 332673.47 | 79.4
AHU-01-Casing |  |  | 63.4 | 63.4 | 63.4 | Lw | AHU_01_Casing |  | 0 | 0 | 0 | [6 empty] | 0 |  | (none) | 1.7 | g | 420264.62 | 332670.13 | 80
AHU-02-ATMOSPHERIC-extract-fan |  |  | 71.4 | 71.4 | 71.4 | Lw | AHU_02_ATMOSPHERIC_extract_fan |  | 0 | 0 | 0 |  |  | NC40 |  |  |  | 0 |  | (none) | 1.1 | g | 420258.48 | 332687.81 | 79.4
AHU-02-ATMOSPHERIC-supply-fan |  |  | 63.3 | 63.3 | 63.3 | Lw | AHU_02_ATMOSPHERIC_supply_fan |  | 0 | 0 | 0 |  |  | NC40 |  |  |  | 0 |  | (none) | 1.1 | g | 420254.06 | 332682.87 | 79.4
AHU-02-Casing |  |  | 65.3 | 65.3 | 65.3 | Lw | AHU_02_Casing |  | 0 | 0 | 0 | [6 empty] | 0 |  | (none) | 1.7 | g | 420250.16 | 332689.81 | 80
AHU-03-ATMOSPHERIC-extract-fan |  |  | 68.1 | 68.1 | 68.1 | Lw | AHU_03_ATMOSPHERIC_extract_fan |  | 0 | 0 | 0 |  |  | NC40 |  |  |  | 0 |  | (none) | 1.1 | g | 420273.81 | 332679.48 | 79.4
AHU-03-ATMOSPHERIC-supply-fan |  |  | 64.1 | 64.1 | 64.1 | Lw | AHU_03_ATMOSPHERIC_supply_fan |  | 0 | 0 | 0 |  |  | NC40 |  |  |  | 0 |  | (none) | 1.1 | g | 420273.14 | 332678 | 79.4
AHU-03-Casing |  |  | 64.5 | 64.5 | 64.5 | Lw | AHU_03_Casing |  | 0 | 0 | 0 | [6 empty] | 0 |  | (none) | 1.7 | g | 420266.07 | 332682.02 | 80
AHU-07-ATMOSPHERIC-extract-fan |  |  | 78.2 | 78.2 | 78.2 | Lw | AHU_07_ATMOSPHERIC_extract_fan |  | 0 | 0 | 0 |  |  | NC40 |  |  |  | 0 |  | (none) | 0.8 | g | 420162.06 | 332615.58 | 84
AHU-07-ATMOSPHERIC-extract-fan - Assumed Phase 2 |  |  | 78.2 | 78.2 | 78.2 | Lw | AHU_07_ATMOSPHERIC_extract_fan |  | 0 | 0 | 0 |  |  | NC40 |  |  |  | 0 |  | (none) | 0.8 | g | 420138.28 | 332623.72 | 84
AHU-07-ATMOSPHERIC-supply-fan |  |  | 74.8 | 74.8 | 74.8 | Lw | AHU_07_ATMOSPHERIC_supply_fan |  | 0 | 0 | 0 |  |  | NC40 |  |  |  | 0 |  | (none) | 0.8 | g | 420158.07 | 332624.07 | 84
AHU-07-ATMOSPHERIC-supply-fan - Assumed Phase 2 |  |  | 74.8 | 74.8 | 74.8 | Lw | AHU_07_ATMOSPHERIC_supply_fan |  | 0 | 0 | 0 |  |  | NC40 |  |  |  | 0 |  | (none) | 0.8 | g | 420134.3 | 332632.21 | 84
AHU-07-Casing |  |  | 79 | 79 | 79 | Lw | AHU_07_Casing |  | 0 | 0 | 0 | [6 empty] | 0 |  | (none) | 1.7 | g | 420163.84 | 332622.6 | 84.9
AHU-07-Casing - Assumed Phase 2 |  |  | 79 | 79 | 79 | Lw | AHU_07_Casing |  | 0 | 0 | 0 | [6 empty] | 0 |  | (none) | 1.7 | g | 420140.07 | 332630.74 | 84.9
AHU-08-ATMOSPHERIC-extract-fan |  |  | 78.3 | 78.3 | 78.3 | Lw | AHU_08_ATMOSPHERIC_extract_fan |  | 0 | 0 | 0 |  |  | NC40 |  |  |  | 0 |  | (none) | 0.8 | g | 420169.67 | 332637.64 | 84
AHU-08-ATMOSPHERIC-extract-fan - Assumed Phase 2 |  |  | 78.3 | 78.3 | 78.3 | Lw | AHU_08_ATMOSPHERIC_extract_fan |  | 0 | 0 | 0 |  |  | NC40 |  |  |  | 0 |  | (none) | 0.8 | g | 420145.9 | 332645.78 | 84
AHU-08-ATMOSPHERIC-supply-fan |  |  | 74.6 | 74.6 | 74.6 | Lw | AHU_08_ATMOSPHERIC_supply_fan |  | 0 | 0 | 0 |  |  | NC40 |  |  |  | 0 |  | (none) | 0.8 | g | 420168.1 | 332646.71 | 84
AHU-08-ATMOSPHERIC-supply-fan - Assumed Phase 2 |  |  | 74.6 | 74.6 | 74.6 | Lw | AHU_08_ATMOSPHERIC_supply_fan |  | 0 | 0 | 0 |  |  | NC40 |  |  |  | 0 |  | (none) | 0.8 | g | 420144.33 | 332654.85 | 84
AHU-08-Casing |  |  | 79.2 | 79.2 | 79.2 | Lw | AHU_08_Casing |  | 0 | 0 | 0 | [6 empty] | 0 |  | (none) | 1.7 | g | 420173.74 | 332640.95 | 84.9
AHU-08-Casing - Assumed Phase 2 |  |  | 79.2 | 79.2 | 79.2 | Lw | AHU_08_Casing |  | 0 | 0 | 0 | [6 empty] | 0 |  | (none) | 1.7 | g | 420149.97 | 332649.09 | 84.9
AHU-09-ATMOSPHERIC-extract-fan |  |  | 76 | 76 | 76 | Lw | AHU_09_ATMOSPHERIC_extract_fan |  | 0 | 0 | 0 |  |  | NC40 |  |  |  | 0 |  | (none) | 0.8 | g | 420164.83 | 332626.63 | 84
AHU-09-ATMOSPHERIC-extract-fan - Assumed Phase 2 |  |  | 76 | 76 | 76 | Lw | AHU_09_ATMOSPHERIC_extract_fan |  | 0 | 0 | 0 |  |  | NC40 |  |  |  | 0 |  | (none) | 0.8 | g | 420141.06 | 332634.78 | 84
AHU-09-ATMOSPHERIC-supply-fan |  |  | 72.9 | 72.9 | 72.9 | Lw | AHU_09_ATMOSPHERIC_supply_fan |  | 0 | 0 | 0 |  |  | NC40 |  |  |  | 0 |  | (none) | 0.8 | g | 420162.95 | 332634.55 | 84
AHU-09-ATMOSPHERIC-supply-fan - Assumed Phase 2 |  |  | 72.9 | 72.9 | 72.9 | Lw | AHU_09_ATMOSPHERIC_supply_fan |  | 0 | 0 | 0 |  |  | NC40 |  |  |  | 0 |  | (none) | 0.8 | g | 420139.18 | 332642.69 | 84
AHU-09-Casing |  |  | 75.6 | 75.6 | 75.6 | Lw | AHU_09_Casing |  | 0 | 0 | 0 | [6 empty] | 0 |  | (none) | 1.7 | g | 420168.18 | 332631.14 | 84.9
AHU-09-Casing - Assumed Phase 2 |  |  | 75.6 | 75.6 | 75.6 | Lw | AHU_09_Casing |  | 0 | 0 | 0 | [6 empty] | 0 |  | (none) | 1.7 | g | 420144.41 | 332639.28 | 84.9
COND-01-Northern-Offices-Condenser-Compound & Attenuation |  |  | 78.3 | 86.3 | 78.3 | Lw | COND_01 |  | -8 | 0 | -8 | [6 empty] | 0 | 500 | (none) | 0.5 | r | 420228.22 | 332726.75 | 74.33
COND-01-Northern-Offices-Condenser-Compound & Attenuation |  |  | 78.3 | 86.3 | 78.3 | Lw | COND_01 |  | -8 | 0 | -8 | [6 empty] | 0 | 500 | (none) | 0.5 | r | 420230.37 | 332725.71 | 74.3
COND-02-Western-Condenser-Compound |  |  | 83.8 | 83.8 | 83.8 | Lw | COND_02 |  | 0 | 0 | 0 | [6 empty] | 0 | 500 | (none) | 0.5 | r | 420072.54 | 332631.46 | 74.02
COND-02-Western-Condenser-Compound |  |  | 83.8 | 83.8 | 83.8 | Lw | COND_02 |  | 0 | 0 | 0 | [6 empty] | 0 | 500 | (none) | 0.5 | r | 420070.23 | 332632.62 | 74.02
COND-03-Office |  |  | 62 | 62 | 62 | Lw | COND_03 |  | 0 | 0 | 0 | [6 empty] | 0 | 500 | (none) | 0.5 | r | 420201.03 | 332534.91 | 72.8
COND-04-Server Room |  |  | 70 | 70 | 70 | Lw | COND_04 |  | 0 | 0 | 0 | [6 empty] | 0 | 500 | (none) | 0.5 | r | 420227.61 | 332725.07 | 74.3
COND-05-Server Room |  |  | 70 | 70 | 70 | Lw | COND_05 |  | 0 | 0 | 0 | [6 empty] | 0 | 500 | (none) | 0.5 | r | 420227.17 | 332724.03 | 74.3
COND-06-IT Storage |  |  | 70 | 70 | 70 | Lw | COND_06 |  | 0 | 0 | 0 | [6 empty] | 0 | 500 | (none) | 0.5 | r | 420229.43 | 332724.29 | 74.3
COND-07-IT Storage |  |  | 70 | 70 | 70 | Lw | COND_07 |  | 0 | 0 | 0 | [6 empty] | 0 | 500 | (none) | 0.5 | r | 420228.95 | 332723.2 | 74.3
COND-08-UPS Room |  |  | 62 | 62 | 62 | Lw | COND_08 |  | 0 | 0 | 0 | [6 empty] | 0 | 500 | (none) | 0.5 | r | 420226.31 | 332722.57 | 74.3
COND-09-Server Room |  |  | 70 | 70 | 70 | Lw | COND_09 |  | 0 | 0 | 0 | [6 empty] | 0 | 500 | (none) | 0.5 | r | 420225.94 | 332721.78 | 74.29
COND-10-Server Room |  |  | 70 | 70 | 70 | Lw | COND_10 |  | 0 | 0 | 0 | [6 empty] | 0 | 500 | (none) | 0.5 | r | 420225.57 | 332720.97 | 74.28
Delivery Unloading |  | Unloading | 82.2 | 82.2 | 82.2 | Lw | Unloading |  | 0 | 0 | 0 | [6 empty] | 0 |  | (none) | 1.1 | g | 420147.9 | 332742.16 | 75.05
EF-01-ATMOSPHERIC-extract-fan |  |  | 77 | 77 | 77 | Lw | EF_01_ATMOSPHERIC_extract_fan |  | 0 | 0 | 0 |  |  | NC40 |  |  |  | 0 |  | (none) | 0.8 | g | 420185.39 | 332667.68 | 84
EF-01-ATMOSPHERIC-extract-fan - Assumed Phase 2 |  |  | 77 | 77 | 77 | Lw | EF_01_ATMOSPHERIC_extract_fan |  | 0 | 0 | 0 |  |  | NC40 |  |  |  | 0 |  | (none) | 0.8 | g | 420161.62 | 332675.82 | 84
EF-01-Casing |  |  | 69.9 | 69.9 | 69.9 | Lw | EF_01_Casing |  | 0 | 0 | 0 | [6 empty] | 0 |  | (none) | 1.7 | g | 420190.31 | 332664.71 | 84.9
EF-01-Casing - Assumed Phase 2 |  |  | 69.9 | 69.9 | 69.9 | Lw | EF_01_Casing |  | 0 | 0 | 0 | [6 empty] | 0 |  | (none) | 1.7 | g | 420166.54 | 332672.85 | 84.9
EF-02-ATMOSPHERIC-extract-fan |  |  | 77.5 | 77.5 | 77.5 | Lw | EF_02_ATMOSPHERIC_extract_fan |  | 0 | 0 | 0 |  |  | NC40 |  |  |  | 0 |  | (none) | 0.8 | g | 420237.23 | 332628.91 | 84
EF-02-Casing |  |  | 69.8 | 69.8 | 69.8 | Lw | EF_02_Casing |  | 0 | 0 | 0 | [6 empty] | 0 |  | (none) | 1.7 | g | 420238.55 | 332633.76 | 84.9
EF-03-ATMOSPHERIC-extract-fan |  |  | 77.5 | 77.5 | 77.5 | Lw | EF_03_ATMOSPHERIC_extract_fan |  | 0 | 0 | 0 |  |  | NC40 |  |  |  | 0 |  | (none) | 0.8 | g | 420190.41 | 332696.23 | 84
EF-03-Casing |  |  | 69.8 | 69.8 | 69.8 | Lw | EF_03_Casing |  | 0 | 0 | 0 | [6 empty] | 0 |  | (none) | 1.7 | g | 420191.51 | 332700.63 | 84.9
EF-04-ATMOSPHERIC-extract-fan |  |  | 77.5 | 77.5 | 77.5 | Lw | EF_04_ATMOSPHERIC_extract_fan |  | 0 | 0 | 0 |  |  | NC40 |  |  |  | 0 |  | (none) | 0.8 | g | 420209.64 | 332683.57 | 84
EF-04-Casing |  |  | 69.8 | 69.8 | 69.8 | Lw | EF_04_Casing |  | 0 | 0 | 0 | [6 empty] | 0 |  | (none) | 1.7 | g | 420215.59 | 332681.84 | 84.9
EF-05-ATMOSPHERIC-extract-fan |  |  | 77.5 | 77.5 | 77.5 | Lw | EF_05_ATMOSPHERIC_extract_fan |  | 0 | 0 | 0 |  |  | NC40 |  |  |  | 0 |  | (none) | 0.8 | g | 420212.42 | 332688.63 | 84
EF-05-Casing |  |  | 69.8 | 69.8 | 69.8 | Lw | EF_05_Casing |  | 0 | 0 | 0 | [6 empty] | 0 |  | (none) | 1.7 | g | 420217.14 | 332685.59 | 84.9
SF-01-ATMOSPHERIC-supply-fan |  |  | 72.7 | 72.7 | 72.7 | Lw | SF_01_ATMOSPHERIC_supply_fan |  | 0 | 0 | 0 |  |  | NC40 |  |  |  | 0 |  | (none) | 0.8 | g | 420178.02 | 332661.34 | 84
SF-01-ATMOSPHERIC-supply-fan - Assumed Phase 2 |  |  | 72.7 | 72.7 | 72.7 | Lw | SF_01_ATMOSPHERIC_supply_fan |  | 0 | 0 | 0 |  |  | NC40 |  |  |  | 0 |  | (none) | 0.8 | g | 420154.25 | 332669.48 | 84
SF-01-Casing |  |  | 71.4 | 71.4 | 71.4 | Lw | SF_01_Casing |  | 0 | 0 | 0 | [6 empty] | 0 |  | (none) | 1.7 | g | 420183.87 | 332657.78 | 84.9
SF-01-Casing - Assumed Phase 2 |  |  | 71.4 | 71.4 | 71.4 | Lw | SF_01_Casing |  | 0 | 0 | 0 | [6 empty] | 0 |  | (none) | 1.7 | g | 420160.1 | 332665.92 | 84.9
SF-02-ATMOSPHERIC-supply-fan |  |  | 73.7 | 73.7 | 73.7 | Lw | SF_02_ATMOSPHERIC_supply_fan |  | 0 | 0 | 0 |  |  | NC40 |  |  |  | 0 |  | (none) | 0.8 | g | 420234.59 | 332639.9 | 84
SF-02-Casing |  |  | 72 | 72 | 72 | Lw | SF_02_Casing |  | 0 | 0 | 0 | [6 empty] | 0 |  | (none) | 1.7 | g | 420232.74 | 332633.73 | 84.9
AHU-04-Casing |  |  | 80.6 | 80.6 | 80.6 | Lw | AHU_04_Casing |  | 0 | 0 | 0 | [6 empty] | 0 |  | (none) | 1.7 | g | 420152.31 | 332596.78 | 84.9
AHU-05-Casing |  |  | 80.5 | 80.5 | 80.5 | Lw | AHU_05_Casing |  | 0 | 0 | 0 | [6 empty] | 0 |  | (none) | 1.7 | g | 420147.13 | 332586.56 | 84.9
AHU-06-Casing |  |  | 78 | 78 | 78 | Lw | AHU_06_Casing |  | 0 | 0 | 0 | [6 empty] | 0 |  | (none) | 1.7 | g | 420139.2 | 332565.46 | 84.9
AHU-04-ATMOSPHERIC-supply-fan |  |  | 77.4 | 77.4 | 77.4 | Lw | AHU_04_ATMOSPHERIC_supply_fan |  | 0 | 0 | 0 |  |  | NC40 |  |  |  | 0 |  | (none) | 0.8 | g | 420147.07 | 332600.33 | 84
AHU-04-ATMOSPHERIC-extract-fan |  |  | 80.2 | 80.2 | 80.2 | Lw | AHU_04_ATMOSPHERIC_extract_fan |  | 0 | 0 | 0 |  |  | NC40 |  |  |  | 0 |  | (none) | 0.8 | g | 420149.85 | 332591.93 | 84
AHU-05-ATMOSPHERIC-extract-fan |  |  | 80.3 | 80.3 | 80.3 | Lw | AHU_05_ATMOSPHERIC_extract_fan |  | 0 | 0 | 0 |  |  | NC40 |  |  |  | 0 |  | (none) | 0.8 | g | 420145.66 | 332581.15 | 84
AHU-05-ATMOSPHERIC-supply-fan |  |  | 77.2 | 77.2 | 77.2 | Lw | AHU_05_ATMOSPHERIC_supply_fan |  | 0 | 0 | 0 |  |  | NC40 |  |  |  | 0 |  | (none) | 0.8 | g | 420142.25 | 332589.85 | 84
AHU-06-ATMOSPHERIC-supply-fan |  |  | 75.6 | 75.6 | 75.6 | Lw | AHU_06_ATMOSPHERIC_supply_fan |  | 0 | 0 | 0 |  |  | NC40 |  |  |  | 0 |  | (none) | 0.8 | g | 420133.96 | 332571.15 | 84
AHU-06-ATMOSPHERIC-extract-fan |  |  | 77.8 | 77.8 | 77.8 | Lw | AHU_06_ATMOSPHERIC_extract_fan |  | 0 | 0 | 0 |  |  | NC40 |  |  |  | 0 |  | (none) | 0.8 | g | 420136.5 | 332561.79 | 84
AHU-04-Casing - Assumed Phase 2 |  |  | 80.6 | 80.6 | 80.6 | Lw | AHU_04_Casing |  | 0 | 0 | 0 | [6 empty] | 0 |  | (none) | 1.7 | g | 420129.64 | 332611.8 | 84.9
AHU-05-Casing - Assumed Phase 2 |  |  | 80.5 | 80.5 | 80.5 | Lw | AHU_05_Casing |  | 0 | 0 | 0 | [6 empty] | 0 |  | (none) | 1.7 | g | 420124.26 | 332597.73 | 84.9
AHU-06-Casing - Assumed Phase 2 |  |  | 78 | 78 | 78 | Lw | AHU_06_Casing |  | 0 | 0 | 0 | [6 empty] | 0 |  | (none) | 1.7 | g | 420115.91 | 332577.99 | 84.9
AHU-04-ATMOSPHERIC-supply-fan - Assumed Phase 2 |  |  | 77.4 | 77.4 | 77.4 | Lw | AHU_04_ATMOSPHERIC_supply_fan |  | 0 | 0 | 0 |  |  | NC40 |  |  |  | 0 |  | (none) | 0.8 | g | 420124.4 | 332615.35 | 84
AHU-04-ATMOSPHERIC-extract-fan - Assumed Phase 2 |  |  | 80.2 | 80.2 | 80.2 | Lw | AHU_04_ATMOSPHERIC_extract_fan |  | 0 | 0 | 0 |  |  | NC40 |  |  |  | 0 |  | (none) | 0.8 | g | 420126.66 | 332605.96 | 84
AHU-05-ATMOSPHERIC-extract-fan - Assumed Phase 2 |  |  | 80.3 | 80.3 | 80.3 | Lw | AHU_05_ATMOSPHERIC_extract_fan |  | 0 | 0 | 0 |  |  | NC40 |  |  |  | 0 |  | (none) | 0.8 | g | 420121.54 | 332591.07 | 84
AHU-05-ATMOSPHERIC-supply-fan - Assumed Phase 2 |  |  | 77.2 | 77.2 | 77.2 | Lw | AHU_05_ATMOSPHERIC_supply_fan |  | 0 | 0 | 0 |  |  | NC40 |  |  |  | 0 |  | (none) | 0.8 | g | 420117.87 | 332601.07 | 84
AHU-06-ATMOSPHERIC-supply-fan - Assumed Phase 2 |  |  | 75.6 | 75.6 | 75.6 | Lw | AHU_06_ATMOSPHERIC_supply_fan |  | 0 | 0 | 0 |  |  | NC40 |  |  |  | 0 |  | (none) | 0.8 | g | 420110.04 | 332583.88 | 84
AHU-06-ATMOSPHERIC-extract-fan - Assumed Phase 2 |  |  | 77.8 | 77.8 | 77.8 | Lw | AHU_06_ATMOSPHERIC_extract_fan |  | 0 | 0 | 0 |  |  | NC40 |  |  |  | 0 |  | (none) | 0.8 | g | 420112.27 | 332573.07 | 84
Silo Dry Air Generator & Injector |  |  | 97.5 | 89.5 | 97.5 | Lw | 89++80 |  | 8 | 0 | 8 | [6 empty] | 0 | 500 | (none) | 2 | r | 420240.28 | 332618.96 | 74.44
Silo Filter |  | Silo_Filter@18m height | 94 | 86 | 94 | Lw | 86 |  | 8 | 0 | 8 | [6 empty] | 0 | 500 | (none) | 9.3 | r | 420240.28 | 332618.96 | 81.74

## Receivers
Individual Receivers
Name | M. | ID | Level Lr |  | Limit. Value |  | Land Use |  |  | Height |  | Coordinates
|  |  | Day | Night | Day | Night | Type | Auto | Noise Type |  |  | X | Y | Z
|  |  | (dBA) | (dBA) | (dBA) | (dBA) |  |  |  | (m) |  | (m) | (m) | (m)
Receiver 2 |  |  | 41.7 | 39.9 | 0 | 0 |  | x | Total | 4.5 | r | 420234.89 | 332791.24 | 81.22
Receiver 1 |  |  | 40.3 | 40.2 | 0 | 0 |  | x | Total | 4.5 | r | 420144.91 | 332818.35 | 81.27
Receiver 3 |  |  | 43.1 | 41.2 | 0 | 0 |  | x | Total | 4.5 | r | 420251.65 | 332779.67 | 81.04
Receiver 4 |  |  | 37.6 | 37.5 | 0 | 0 |  | x | Total | 4.5 | r | 419954.12 | 332533.75 | 76.42
Building Evaluation Receivers
Name | M. | ID | Level |  | Excess Levels |  | Land Use |  |  | Coordinates |  |  | Floor Height |  | Round up | Atribute Height Code
|  |  | Day | Night | From | To | Type | Auto | Noise Type | X | Y | Ø | EG | OG-OG
|  |  | (dBA) | (dBA) | Floor | Floor |  |  |  | (m) | (m) | (m) | (m) | (m)
Receiver 3 |  |  | 43.2 | 41.3 |  |  |  | x | Roads | 420252.92 | 332783.31 | 4 | 4.5 | 1000 | 0.5 | r
Receiver 1 |  |  | 40.4 | 40.2 |  |  |  | x | Roads | 420148.21 | 332823.36 | 4.5 | 4.5 | 1000 | 0.5 | r
Receiver 2 |  |  | 41.7 | 40 |  |  |  | x | Roads | 420235.92 | 332795.28 | 4 | 4.5 | 1000 | 0.5 | r
Receiver 4 |  |  | 37.6 | 37.5 |  |  |  | x | Roads | 419949.72 | 332535.12 | 4 | 4.5 | 1000 | 0.5 | r