## Tabelle1
Valve tag [-] | Set pressure [barg] | Discharge area [mm^2] | Discharge flow-rate capacity [kg/h] | Fluid discharged [-] | Equipment on which relief valve is installed [-] | Vent location [-]
RV-022 | 13 | 551.61 | 3021 | Compressed air | Compressed air vessel T-032 | Atmosphere safe location outside building
RV-030 | 7 | 551.61 | 26930 | Water (liquid) | Condenser E-004 (cooling water side) | Ground safe location inside building
RV-031 | 9 | 70.97 | 849.4 | Water (liquid) | Plate heat exchanger E-006 (cooling water side) | Containment bund safe location inside building
RV-032 | 9 | 70.97 | 852 | Water (liquid) | Plate heat exchanger E-006 (process water side) | Ground safe location inside building
RV-007 | 13 | 581.07 | 4018.7 | Water (saturated vapour) | Reactor R-0104 | Blowdown vessel T-033
RV-008 | 13 | 581.07 | 4018.7 | Water (saturated vapour) | Reactor R-0105 | Blowdown vessel T-033
RV-010 | 7 | 373.25 | 39500.7 | Water (liquid) | Condenser E-003 (cooling water side) | Ground safe location inside building
RV-012 | 0.4 | 226.98 | 251.4 | Compressed air | T-022 compressed air inlet line | Atmosphere safe location outside building
RV-013 | 0.4 | 226.98 | 251.4 | Compressed air | T-021 compressed air inlet line | Atmosphere safe location outside building
RV-014 | 12.3 | 198 | 931 | Water (liquid) | Plate heat exchanger E-8931 (cooling water side) | Containment bund safe location inside building
RV-015 | 12.3 | 198 | 931 | Process fluid (liquid) | Plate heat exchanger E-8931 (process fluid side) | Containment bund safe location inside building
RV-016 | 12.3 | 198 | 931 | Water (liquid) | Plate heat exchanger E-8932 (cooling water side) | Containment bund safe location inside building
RV-017 | 12.3 | 198 | 931 | Process fluid (liquid) | Plate heat exchanger E-8932 (process fluid side) | Containment bund safe location inside building
RV- 01 | 16.8 | 198 | 2550 | Oxygen | Oxygen root pipe | Safe location outside building old tank farm bund
RV-005 | 6 | 70.97 | 4055 | Water (liquid) | Condenser E-001 (cooling water side) | Ground safe location inside building
RV-006 | 6 | 70.97 | 4055 | Water (liquid) | Condenser E-002 (cooling water side) | Ground safe location inside building
RV-02 | 7.8 | 581.07 | 3890 | Water (saturated vapour) | Reactor R-0101 | Blowdown vessel T-033
RV-03 | 7.8 | 581.07 | 3890 | Water (saturated vapour) | Reactor R-0102 | Blowdown vessel T-033
RV-04 | 7.8 | 581.07 | 3890 | Water (saturated vapour) | Reactor R-0103 | Blowdown vessel T-033