## Calculations
| Unit | EP 01 | EP 02 | EP 03 | EP 04 | EP 05
Stack heights (m) - VTU | m |  | 0 | 0 | 0
Stack diameters (m) - VTU | m | 0.2678 | 0.2678 | 0.317 | 0.317 | 0.213
Emission velocity (m/s) - VTU | m/s | 15.7891 | 15.7891 | 16.9 | 16.9025 | 0.58497
Fan flow-rates (Actual m3/h) - VTU | m3/h | 3200 | 3200 | 4800 | 4800 | 75
Volume flow rates (Actual m3/s) - VTU | m3/s | 0.88889 | 0.88889 | 1.33 | 1.3333 | 0.020833
Volume flow rates (Normalised m3/s) - VTU | Nm3/s | 0.69732 | 0.69732 | 1.05 | 1.046 | 0.016343
Emission temperatures (Celsius) – Gary 75’c Max | °C | 75 | 75 | 75 | 75 | 75
Stack locations OS Grid Eastings and Northings (m) - VTU | m
Pollutant emissions (in mg/Nm3 and/or g/s) – Gary *Below* | mg/Nm3 | 0.06
EP1 and EP2 flow rates considered as per fan Halifax No33 curve 3200 m3/h at outlet
Temperature max 75 degree, downstream fan, for motor thermal dissipation.
This dissipation is not considered in the calculation
To be completed by client upstream scrubber
EP3 and EP4 flow rates considered as per fan curve 4800 m3/h at outlet, fan Halifax no. 35.5 CNZ 2 STAGE
EP1, EP2, EP5 has a discharge pipe of 250mm while EP3 and EP4 300 mm
As per stack of 0.213 diameter
As per basic KEM_IB27 datasheet of 75m3/h

## K-003 & K-004 datasheet
[6 empty] | Fan Data Sheet | [9 empty] | Kemira Chemicals (UK), Ltd.
Project: |  | Goole expansion project II - KEM-IB27_1 |  |  |  | Plant Location: |  | Goole (United Kingdom) |  |  |  |  | Rev. No.: | 03 |  | Date: | 2024-07-17
PID No.: |  | KEM-IB27_1-PS-PID-032.01 |  |  |  | Supplier: | [6 empty] | Order No.: |  |  | KEM-IB27_1-PS-EQS-011.03-E_Exhaust fan for dissolving tank_K004
Item No.: |  |  | K-004 |  |  | Item Name: |  |  | Exhaust fan for dissolving tank
Motor-No.: | [5 empty] | Usage:
Medium
Composition w/w:
100% water vapour
Properties:
Operating data | [13 empty] | Design point |  |  |  | Nom. | No. 2 | No. 3
Working temperature TW |  |  |  | min. | 80 | °C | Vapor pressure at |  |  |  | TW,min | 600 | mbar | Flow |  |  |  | 4800 |  |  | m³/h
|  |  |  | max. | 107 | °C |  |  |  |  | TW,max | 1400 | mbar | Total Head |  |  |  | 1 |  |  | m
Density at TW |  |  |  | min. | 0.6 | kg/m3 | Specific heat at |  |  |  | TW,min | 2.05 | kJ/kgK | Suction pressure |  |  |  | 0.95 |  |  | barabs
|  |  |  | max. | 0.85 | kg/m3 |  |  |  |  | TW,max | 2.2 | kJ/kgK | Discharge pressure |  |  |  | 1.05 | (*) |  | barabs
Viscosity at TW |  |  |  | min. | 0.012 | mPas | Solid fraction |  |  |  |  | 0 | wt-%
|  |  |  | max. | 0.012 | mPas | Vapour fraction |  |  |  |  | 100 | wt-%
Design temperature TD |  |  |  | min. | 0 | °C | Design pressure pD |  |  |  | min. | 0.1 | barabs
|  |  |  | max. | 120 | °C |  |  |  |  | max. | 0.15 | barabs
Operation |  |  | o | Continuous |  |  | Batch |  | Operating time [h/d]: |  |  | 20 hours / 7 days |  | Operating time [h/batch]: |  |  |  | ≈ 6 hours / batch
Mechanical design
Fan | [10 empty] | Motor (1)
Fan design (*) |  |  | o | Radial Fan |  | o | Axial Fan |  |  |  | Type |  |  | ORB (Open Radial Bladed)
|  |  | o | Others: | [6 empty] | Size |  |  | 39''
[11 empty] | Rotation speed |  |  | 2961 |  |  | rpm
No. of stages: | [5 empty] | 1 |  |  |  |  | Power |  |  | 30 |  |  | kW
Nominal rotation speed |  |  |  | rpm |  | 2961 |  |  |  |  | Voltage |  |  | 415 |  |  | V
Rotor diameter |  |  |  | max. |  | 904 |  |  |  |  | Frequenzy |  |  | 50 |  |  | Hz
|  |  |  | designed |  | 902 |  |  |  |  | Protection |  |  | IP 55
|  |  |  | min. |  | 900 |  |  |  |  | Ex-Class |  | o | yes |  |  |  |  | no
Power consumption | [5 empty] | * |  |  | kW |  | Drive
Max. power consumption | [5 empty] | * |  |  | kW |  | Type | x | Stiff | o | Gear |  | o | Pole-shift
Efficiency | [5 empty] | * |  |  | % |  |  | o | FC | o | Others:
Impeller design | [5 empty] | * |  |  |  |  | Shaft seal
Shaft orientation |  |  |  |  | Horizontal |  | o | Vertical |  |  | o | Gland |  | o | Double face seal |  |  | x | Face seal
Suction port |  |  |  | DN | 300 |  | [mm] | PN | 20 | bar abs | o | Magnetic |  | o | Others:
|  |  |  | Orientation |  | TBD
|  |  |  | Design |  | ANSI 150# |  |  |  |  | Others
Discharge port |  |  |  | DN | 300 |  | mm | PN | 20 | bar abs | Design |  | o | Insulation |  | o | Heating |  | x | Guard
|  |  |  | Orientation |  | TBD | [6 empty] | x | Base plate |  | x | Case drain
|  |  |  | Design |  | ANSI 150# | [6 empty] | o | Drip tray under pump
Materials | [12 empty] | o | Others:
Medium contacted parts |  |  |  | AISI 304 | [6 empty] | Weight
Not medium cont. parts |  |  |  | Mild steel | [6 empty] | Fan |  | * |  | kg
Seals |  |  |  | PTFE gasket strip | [6 empty] | Motor |  | * |  | kg
Face seal |  |  |  | Halifax fan standard Novus labyrinth seal | [6 empty] | Base plate |  | * |  | kg
Bearing |  |  |  | SKF | [6 empty] | Others |  | * |  | kg
[11 empty] | Sum |  | * |  | kg
Regulations to be followed
BS848; BSEN ISO 9606 9606-1; ISO 9001:2015; ISO 5801: 2008; ISO 3744: 2010
Remarks
* to be added by supplier
03 |  | Update |  |  |  | R. Baldari |  | 2024-07-17 |  | D. Abram |  | 2024-07-17 |  | M. Benuzzi |  | 2024-07-17
02 |  | Update as per supplier offer |  |  |  | R. Baldari |  | 2024-05-27 |  | D. Abram |  | 2024-05-27 |  | M. Benuzzi |  | 2024-05-27
01 |  | First issue |  |  |  | R. Baldari |  | 2024-03-08 |  | D. Abram |  | 2024-03-08 |  | M. Benuzzi |  | 2024-03-08 |  | G. Pickard
Rev. |  | Description |  |  |  | Created |  | Date |  | Checked |  | Date |  | Approved |  | Date |  | Approved |  | Date
[6 empty] | VTU |  |  |  | VTU |  |  |  | VTU |  |  |  | KEMIRA
Formulas:
x = [Vertical]
o = [x]
kontinuierlich
diskontinuierlich
x
x
x
x

## E-004 datasheet
[6 empty] | Heat Exchanger Data Sheet | [9 empty] | Kemira Chemicals (UK), Ltd.
Project: |  | Goole expansion project II - KEM-IB27 |  |  |  | Plant Location: |  | Goole (United Kingdom) |  |  |  |  | Rev. No.: | 02 |  | Date: | 2024-05-23
PID No.: |  | KEM-IB27_1-PS-PID-032 |  |  |  | Supplier: | [6 empty] | Order No.: |  |  | KEM-IB27_1-PS-EQS-004_Condenser for dissolving tank_E004
Item No.: |  |  | E-004 |  |  | Item Name: |  |  | Condensers for Dissolving Tanks
Brand: | [5 empty] | Type: |  |  | Shell & Tube
Operation |  |  |  |  | o | Continuous |  | x | Batch |  |  |  | Operating time [h/batch]: |  |  | ~10,800 seconds (approx 3 hours)
1b) DESIGN CASE (n° 5), vertical configuration |  |  |  |  | Shell side | [7 empty] | Tube side
Medium |  |  |  |  | Cooling Water | [7 empty] | Dissolving Tank Vapours
Properties
Flowmax |  |  |  | kg/h | 51364 | [7 empty] | 5047
Composition |  |  |  |  | Inlet |  |  |  | Outlet |  |  |  | Inlet |  |  |  | Outlet
[5 empty] | Vapor |  | Liquid |  | Vapor |  | Liquid |  | Vapor |  | Liquid |  | Vapor |  |  | Liquid
water |  |  |  | kg/h |  |  | 51364 |  |  |  | 51364 |  | 2688.15 |  | 8.85 |  | 787.59 |  |  | 1909,41
Air |  |  |  | kg/h
Noncondensables |  |  |  | kg/h | [8 empty] | 2349.9 |  |  |  | 2349,9
kg/h
kg/h
kg/h
Design pressure |  |  |  | bara | min. | 0.9 |  |  | max. | 8 |  |  | min. | 0.9 |  |  | max. | 2
Design temperature |  |  |  | °C | min. | 0 |  |  | max. | 150 |  |  | min. | 0 |  |  | max. | 120
Inlet
Working temperature TW, in |  |  |  | °C | 26 | [7 empty] | 87.93
Working pressure |  |  |  | bara | 4 | [7 empty] | 1
Physical state |  |  |  |  | liquid | [7 empty] | vapour / liquid (traces)
Density at TW, in |  |  |  | kg/m³ | 997.42 | [7 empty] | 0,732 / 966,2
Viscosity at TW, in |  |  |  | cP | 0.987 | [7 empty] | 0,015 (vap) / 0,323 (liq)
Specific heat |  |  |  | kcal/kgC | 0.999 | [7 empty] | 0,3702 (vap) / 1 (liq)
Thermal conductivity |  |  |  | Kcal/hr-m-C | 0.516 | [7 empty] | 0,0257 (vap) / 0,576 (liq)
Latent heat (Δ h) |  |  |  | kJ/kg | - | [7 empty] | 2287.9
Surface tension |  |  |  | mN/m
Outlet
Working temperature TW, out |  |  |  | °C | 46.2 | [7 empty] | 74.02
Working pressure |  |  |  | bara | 3.75 | [7 empty] | 1
Pysical state |  |  |  |  | liquid | [7 empty] | vapour (non-condensables) liquid (condensate)
Density at TW, out |  |  |  | kg/m³ | 990.75 | [7 empty] | 0,87 / 975,89
Viscosity at TW, out |  |  |  | cP | 0.6397 | [7 empty] | 0,0171(vap) / 0,395 (liq)
Specific heat |  |  |  | kcal/kgC | 0.999 | [7 empty] | 0,298 (vap) / 1 (liq)
Thermal conductivity |  |  |  | Kcal/hr-m-C | 0.542 | [7 empty] | 0,026 (vap) / 0,576 (liq)
Latent heat (Δ h) |  |  |  | kJ/kg | - | [7 empty] | 2304.7
Surface tension |  |  |  | mN/m
Data Heat Exchanger
Effective Log. MTD |  |  |  | C | 49,64 (*) | [5 empty] | Fouling factor shell side |  |  |  |  | m2-hr-C/Kcal | 0.0002
Heat transfer coefficient |  |  |  | Kcal/m2-hr-C | 636,62 (*) | [5 empty] | Fouling factor tube side |  |  |  |  | m2-hr-C/Kcal | 0.0002
Exchanger area |  |  |  | m² | 36.8 | [5 empty] | Area safety factor |  |  |  |  | %
Heat exchanged max. / average |  |  |  | MW |  |  |  | / | 1.2575 |  | Max. pressure drop shell side |  |  |  |  | mbar | 0.34
[11 empty] | Max. pressure drop tube side |  |  |  |  | mbar | 0.00355
Design Heat Exchanger
Type |  |  |  | BEL |  |  | Calculation acc. to |  |  |  | TEMA |  | Accessory:
Dimensions (Tubes x Length) |  |  |  | 223 tubes x 1750 mm (*) |  |  | Design temperature |  |  | °C | * |  | x | Lifting loop |  | x | Grounding |  | o | Shield holder
Dead weight |  |  |  | kg | * |  | Inspection by |  |  |  | * |  | Insulation | x | Type: | Personnel prot. |  | Thickness: |  | TBD | [mm]
Total weight |  |  |  | kg | * |  | Test pressure |  |  | barg | * |  | Materials: | AISI 316L (17Cr, 12Ni)
Orientation |  |  | x | Vertical | o | Horizontal | [6 empty] | Seals: | PTFE
Baffles |  |  |  | n. | 12 |  | Type |  |  |  | perpendicolar |  | % Cut baffles (diam.) |  |  | 14
Regulations to be followed
Remarks
* ... To be added/verified by manufacturer. Tube length is reffered to tube part effectivley in contact with fluid (rolled parts into tubesheets not counted)
Personnel protection insulation is required for sections where physical access is possible from the ground or from platforms. To be confirmed after equipment layout approval.
2 |  | Update temperatures |  |  |  | G.Maestro |  | 2024-05-23 |  | D.Abram |  | 2024-05-23 |  | M.Benuzzi |  | 2024-05-23
01 |  | First issue |  |  |  | G.Maestro |  | 2024-02-27 |  | D.Abram |  | 2024-02-27 |  | M.Benuzzi |  | 2024-02-27
Rev. |  | Description |  |  |  | Created |  | Date |  | Checked |  | Date |  | Approved |  | Date |  | Approved |  | Date
[6 empty] | VTU |  |  |  | VTU |  |  |  | VTU
[6 empty] | Heat Exchanger Data Sheet | [9 empty] | Kemira Chemicals (UK), Ltd.
Project: |  | Goole expansion project II - KEM-IB27 |  |  |  | Plant Location: |  | Goole (United Kingdom) |  |  |  |  | Rev. No.: | 02 |  | Date: | 2024-05-23
PID No.: |  | KEM-IB27_1-PS-PID-032 |  |  |  | Supplier: | [6 empty] | Order No.: |  |  | KEM-IB27_1-PS-EQS-004_Condenser for dissolving tank_E004
Item No.: |  |  | E-004 |  |  | Item Name: |  |  | Condensers for Dissolving Tanks
| No.: | Description |  |  | DN |  | PN |  | Length |  | Type |  |  | Remarks / Details
[5 empty] | [mm] |  |  |  | [mm]
| N1 | Dissolving tank vapor inlet |  |  | 16" |  | * |  | * |  | std. 150 ANSI Slip on
| N2 | Condensate outlet |  |  | 2" |  | * |  | * |  | std. 150 ANSI Slip on
| N3 | Non condensable vapor outlet |  |  | 12" |  | * |  | * |  | std. 150 ANSI Slip on
| N4 | Cooling water inlet |  |  | 6" |  | * |  | * |  | std. 150 ANSI Slip on
| N5 | Cooling water outlet |  |  | 6" |  | * |  | * |  | std. 150 ANSI Slip on
Tube Bundle HX
Tube outside diameter |  |  |  | mm | 31.7 |  | Tube pattern |  |  |  | TRI30 |  |  | Pitch |  |  | mm | 39.625
Tube thickness |  |  |  | mm | 1.65 |  | Number passes (Shell/Tube) |  |  |  | 1 : 1
Tube length |  |  |  | mm | 1750 |  | Shell outside diameter |  |  | mm | 680
Number of tubes |  |  |  |  | 223 |  | Number of baffles |  |  |  | 12
Remarks
N = Nozzle, B = Other type
NOTES:
(1) | Personnel protection insulation is required for sections where physical access is possible from the ground or from platforms. To be confirmed after equipment layout approval.
2 |  | Update temperatures |  |  |  | G.Maestro |  | 2024-05-23 |  | D.Abram |  | 2024-05-23 |  | M.Benuzzi |  | 2024-05-23
01 |  | First issue |  |  |  | G.Maestro |  | 2024-02-27 |  | D.Abram |  | 2024-02-27 |  | M.Benuzzi |  | 2024-02-27
Rev. |  | Description |  |  |  | Created |  | Date |  | Checked |  | Date |  | Approved |  | Date |  | Approved |  | Date
[6 empty] | VTU |  |  |  | VTU |  |  |  | VTU
Formulas:
x = [Date]
Date = [x]