## Cover
|  |  | CLIENT: |  | SSE |  |  | 60650403-PE-CA-###
|  |  | PROJECT: |  | Keadby 3 Low Carbon Power Station Project |  |  | REV | DATE |  | BY | CHK. | APP.
[8 empty] | 1 | 2022-06-13 |  | KM | -
|  |  | LOCATION: |  | Keadby, Lincolnshire, UK
DOCUMENT TITLE: |  |  |  | Waste Water Modelling Inputs Calculation
DESCRIPTION: |  |  |  | Calculation of the flows, temperatures and concentrations associated with waste water to be discharged from Keadby 3 to River Trent.
1 | OBJECTIVE
2
3
4 |  | The objective of this workbook/calculation is to summarise the reference data from Keadby 3 FEED Contractor and Keadby 2 to provide the inputs to the waste water modelling undertaken for Keadby 3 discharges with and without Keadby 2.
5
6
7
8
9
10
11 | KEY CONCLUSIONS
12
13
14 |  | Source |  |  |  | Keadby 3 Option 1 | Keadby 3 Option 2 |  |  | Keadby 2
15 |  | Temperature |  |  |  | 25°C | 31°C |  |  | 26°C
16 |  | Rate |  |  |  | 209.6m³/hr (58.2L/s) | 300.5m³/s (83.5L/s) |  |  | 100 L/s
17 |  | Velocity |  |  |  | 1.32 m/s | 1.32 m/s |  |  | 1.32 m/s
18 |  | Composition
19 |  | Total ammonia (NH3 and NH4) |  |  |  | 13.23 mg/L | 10.98 mg/L |  |  | Normally 0
20 |  | Ammonia un-ionised as NH3 |  |  |  | 1.36 mg/L | 0.9 mg/L |  |  | Not available
21 |  | TDS |  |  |  | 2367 mg/L | 7182 mg/L |  |  | 2600 mg/L
22 |  | Solids, Suspended @ 105 °C |  |  |  | 0 mg/L | 387.5 mg/L |  |  | 80 mg/L
23 |  | Barium |  |  |  | 302 ug/L | 302 ug/L |  |  | 302 ug/L
24 |  | Calcium |  |  |  | 260 mg/L | 260 mg/L |  |  | 260 mg/L
25 |  | Chloride |  |  |  | 630 mg/L | 630 mg/L |  |  | 630 mg/L
26 |  | Copper |  |  |  | 150 ug/L | 150 ug/L |  |  | 150 ug/L
27 |  | Fluoride |  |  |  | 48 ug/L | 48 ug/L |  |  | 48 ug/L
28 |  | Iron |  |  |  | 1440 ug/L | 1440 ug/L |  |  | 1440 ug/L
29 |  | Magnesium |  |  |  | 100 mg/L | 100 mg/L |  |  | 100 mg/L
30 |  | Nitrate NO3 |  |  |  | 240 mg/L | 240 mg/L |  |  | 240 mg/L
31 |  | Nitrite NO2 |  |  |  | 1.14 mg/L | 1.14 mg/L |  |  | 1.14 mg/L
32 |  | Phosphate PO4 |  |  |  | 5 mg/L | 5 mg/L |  |  | 5 mg/L
33 |  | Potassium |  |  |  | 45 mg/L | 45 mg/L |  |  | 45 mg/L
34 |  | Sodium |  |  |  | 390 mg/L | 390 mg/L |  |  | 390 mg/L
35 |  | Strontium |  |  |  | 0.72 mg/L | 0.72 mg/L |  |  | 0.72 mg/L
36 |  | Sulphate SO4 |  |  |  | 1000 mg/L | 1000 mg/L |  |  | 1000 mg/L
37
38
39
40
41
42
43
44
45

## Sheet 1
|  |  | CLIENT: |  | SSE | 60650403-PE-CA-###
|  |  | PROJECT: |  | Keadby 3 Low Carbon Power Station Project | REV |  | DATE | BY | CHK. | APP.
[6 empty] | 1 |  | 2022-06-13 | KM | -
|  |  | LOCATION: |  | Keadby, Lincolnshire, UK
CALCULATION TITLE: |  |  |  | Waste Water Modelling Inputs Calculation
DESCRIPTION: |  |  |  | Calculation of the flows, temperatures and concentrations associated with waste water to be discharged from Keadby 3 to River Trent.
1 | 1. CONTENTS
2
3
4 | Section | Title |  |  |  |  | Sheet
5 | 1. | Contents |  |  |  |  | 2
6 | 2. | References |  |  |  |  | 3
7 | 3. | Flowrate |  |  |  |  | 4
8 | 4. | Temperature |  |  |  |  | 5
9 | 5. | Composition |  |  |  |  | 6
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45

## Sheet 2
|  |  |  | CLIENT: |  | SSE | 60650403-PE-CA-###
|  |  |  | PROJECT: |  | Keadby 3 Low Carbon Power Station Project | REV | DATE | BY | CHK. | APP.
[7 empty] | 1 | 2022-06-13 | KM | -
|  |  |  | LOCATION: |  | Keadby, Lincolnshire, UK
CALCULATION TITLE: |  |  |  |  | Waste Water Modelling Inputs Calculation
DESCRIPTION: |  |  |  |  | Calculation of the flows, temperatures and concentrations associated with waste water to be discharged from Keadby 3 to River Trent.
1 | 2. REFERENCES
2
3
4 | 1. | PRO-DSB-DOC-UT-RP-KEAD3-00002_Utilities Heat and Mass Balance Report Rev A1 Signed.pdf
5 | 2. | K2 Environmental Permit Variation: Supporting Information, Nov 2019, accessed June 2022:
6 |  |  | https://consult.environment-agency.gov.uk/psc/dn17-3ef-keadby-generation-limited/supporting_documents/Supporting%20Information.pdf
7
8 | 3. | Appendix A - Water Impact Assessment Rev 1, AECOM June 2022
9 | 4. | Keadby 2 canal water blowdown data estimate with 4 cycles of concentration
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45

## Sheet 3
|  |  | CLIENT: |  | SSE | [5 empty] | 60650403-PE-CA-###
|  |  | PROJECT: |  | Keadby 3 Low Carbon Power Station Project | [5 empty] | REV | DATE | BY | CHK. | APP.
[11 empty] | 1 | 2022-06-13 | KM | -
|  |  | LOCATION: |  | Keadby, Lincolnshire, UK
CALCULATION TITLE: |  |  |  | Waste Water Modelling Inputs Calculation
DESCRIPTION: |  |  |  | Calculation of the flows, temperatures and concentrations associated with waste water to be discharged from Keadby 3 to River Trent.
1 | 3. FLOWRATE
2
3
4 |  | Keadby 3 Option 1 flowrate
5 |  | Stream 510 represents the intermittent ion exchange regeneration waste water, discharged to the neutralisation basin
6 |  | Stream 511 represents the combined Keadby 3 waste stream (except the ion exchange waste) discharged into the neutralisation basin
7 |  | Stream 512 is the sum of 510 and 511, representing total waste water pumped from the neutralisation basin to the outfall.
8
9
10 |  | Stream Number |  |  |  | 510 | 511 | 512
11 |  | Stream Description |  |  |  | IX regen waste to neutralisation basin | Concentrated waste water to neutralisation basin | Total waste water to outfall
12 |  | Flowrate normal (0 if intermittent), m³/hr |  |  |  | 0 | 206.1 | 209.6
13 |  | Frequency |  |  |  | twice weekly | Continuous | Continous
14 |  | Flowrate max, m³/hr |  |  |  | 300 | 206.1 | 209.6
15 |  | Remarks |  |  |  | avg to 3.6m3/h |  | 512 = 510 + 511
16 |  | Reference |  |  |  | Ref. 1 pg 9 | Ref. 1 pg 9 | Ref. 1 pg 9
17
18 |  | Keadby 3 Option 2 flowrate
19 |  | Stream 510 represents the intermittent ion exchange regeneration waste water, discharged to the neutralisation basin
20 |  | Stream 511 represents the combined Keadby 3 waste stream (except the ion exchange waste) discharged into the neutralisation basin
21 |  | Stream 512 is the sum of 510 and 511, representing total waste water pumped from the neutralisation basin to the outfall.
22 |  | Stream 104 is introduced in Option 2 only as a direct blowdown from cooling towers (not necessary for option 1 as CW blowdown sent through RO plant first)
23
24 |  | Stream Number |  |  |  | 510 | 511 | 104 | 512
25 |  | Stream Description |  |  |  | IX regen waste to neutralisation basin | Concentrated waste water to neutralisation basin | CW blowdown | Total waste water to outfall
26 |  | Flowrate normal (0 if intermittent), m³/hr |  |  |  | 0 | 28.1 | 268.8 | 300.5
27 |  | Frequency |  |  |  | twice weekly | Continuous |  | Continous
28 |  | Flowrate max, m³/hr |  |  |  | 300 | 28.1 |  | 300.5
29 |  | Remarks |  |  |  | avg to 3/6m3/h |  | Option 2 only | 512 = 510 + 511 + 104
30 |  | Reference |  |  |  | Ref. 1 pg 13 | Ref. 1 pg 13 |  | Ref. 1 pg 13
31
32 |  | Keadby 2
33 |  | Max flowrate to be considered in thermal plume dispersion modelling: | [5 empty] | 100 | L/s | Ref. 2 Section 3.2.1 Table 3.3
34 | [7 empty] | 360 | m³/h | converted
35
36
37 |  | Flowrate summary
38 |  | Form C6 requires only a single maximum flowrate case to be recorded, therefore, the Option 2 flowrate is to be used for Form C6. Keadby 2 flows are not reported in Form C6.
39 |  | The water dispersion modelling will consider both flow and concentration effects to determine the overall worst case, as well as in combination with Keadby 2
40
41
42
43
44
45

## Sheet 4
|  |  | CLIENT: |  | SSE |  |  | 60650403-PE-CA-###
|  |  | PROJECT: |  | Keadby 3 Low Carbon Power Station Project |  |  | REV | DATE | BY | CHK. | APP.
[8 empty] | 1 | 2022-06-13 | KM | -
|  |  | LOCATION: |  | Keadby, Lincolnshire, UK
CALCULATION TITLE: |  |  |  | Waste Water Modelling Inputs Calculation
DESCRIPTION: |  |  |  | Calculation of the flows, temperatures and concentrations associated with waste water to be discharged from Keadby 3 to River Trent.
1 | 4. TEMPERATURE
2
3
4 |  | Summer conditions
5 |  | The thermal plume dispersion modelling software uses input discharge temperature in terms of 'excess' water
6 |  | temperature in addition to the temperature of the receiving body (discharge temperature minus river temperature).
7 | [5 empty] | Value | Units | Remarks
8 |  | Summer mean river water temperature: |  |  |  | 18.4 | °C | Ref. 3 Table 5.2
9
10 |  | Keadby 3 Option 1 water discharge temperature |  |  |  | 25 | °C | Ref 1 pg9
11 |  | Keadby 3 Option 2 water discharge temperature |  |  |  | 31 | °C | Ref 1 pg13
12
13 |  | Keadby 3 Option 1 excess water temp vs mean river water |  |  |  | 6.6 | °C | Mean river water temp minus disch. Temp
14 |  | Keadby 3 Option 2 excess water temp vs mean river water |  |  |  | 12.6 | °C | Mean river water temp minus disch. Temp
15
16 |  | For Keadby 2, mean summer ambient air dry bulb temperature |  |  |  | 23 | °C | +1.5°C margin over mean summer temp
17 |  | Keadby 2, resulting CW blowdown discharge temperature |  |  |  | 26 | °C | Calculated by SSE Thermoflex model
18 |  | Keadby 2, resulting excess vs mean river water temperature |  |  |  | 7.6 | °C | Mean river water temp minus disch. Temp
19
20 |  | Winter conditions
21 |  | For winter, the excess water temperatures calculated for summer (6.6, 12.6, 7.6°C for K3 Op1, Op2, and K2, respectively) were applied
22 |  | to the winter mean river water temperature.
23
24 |  | Winter mean river water temperature |  |  |  | 5.6 | °C | Ref. 3 Table 5.2
25
26 |  | Keadby 3 Option 1 excess water temp vs mean river water |  |  |  | 12.2 | °C | Mean river water temp minus disch. Temp
27 |  | Keadby 3 Option 2 excess water temp vs mean river water |  |  |  | 18.2 | °C | Mean river water temp minus disch. Temp
28 |  | Keadby 2, resulting excess vs mean river water temperature |  |  |  | 5.6 | °C | Mean river water temp minus disch. Temp
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45

## Sheet 5
|  |  | CLIENT: |  | SSE |  |  |  | 60650403-PE-CA-###
|  |  | PROJECT: |  | Keadby 3 Low Carbon Power Station Project |  |  |  | REV | DATE | BY | CHK. | APP.
[9 empty] | 1 | 2022-06-13 | KM | -
|  |  | LOCATION: |  | Keadby, Lincolnshire, UK
CALCULATION TITLE: |  |  |  | Waste Water Modelling Inputs Calculation
DESCRIPTION: |  |  |  | Calculation of the flows, temperatures and concentrations associated with waste water to be discharged from Keadby 3 to River Trent.
1 | 5. COMPOSITION
2
3
4
5 |  | Stream |  |  |  | Keadby 3 Option 1 | Keadby 3 Option 2 | Keadby 2
6 |  | Composition
7 |  | Total ammonia (NH3 and NH4) |  |  |  | 13.23 mg/L | 10.98 mg/L | 0
8 |  | Ammonia un-ionised as NH3 |  |  |  | 1.36 mg/L | 0.9 mg/L | N/A
9 |  | TDS |  |  |  | 2367 mg/L | 7182 mg/L | N/A
10 |  | Solids, Suspended @ 105 °C |  |  |  | 0 mg/L | 387.5 mg/L | N/A
11 |  | Ammonia reference |  |  |  | Ref. 1 pg9 | Ref. 1 pg13 | Ref. 4
12
13 |  | Other ions
14 |  | Barium |  |  |  | 302 ug/L | 302 ug/L | 302 ug/L
15 |  | Calcium |  |  |  | 260 mg/L | 260 mg/L | 260 mg/L
16 |  | Chloride |  |  |  | 630 mg/L | 630 mg/L | 630 mg/L
17 |  | Copper |  |  |  | 150 ug/L | 150 ug/L | 150 ug/L
18 |  | Fluoride |  |  |  | 48 ug/L | 48 ug/L | 48 ug/L
19 |  | Iron |  |  |  | 1440 ug/L | 1440 ug/L | 1440 ug/L
20 |  | Magnesium |  |  |  | 100 mg/L | 100 mg/L | 100 mg/L
21 |  | Nitrate NO3 |  |  |  | 240 mg/L | 240 mg/L | 240 mg/L
22 |  | Nitrite NO2 |  |  |  | 1.14 mg/L | 1.14 mg/L | 1.14 mg/L
23 |  | Phosphate PO4 |  |  |  | 5 mg/L | 5 mg/L | 5 mg/L
24 |  | Potassium |  |  |  | 45 mg/L | 45 mg/L | 45 mg/L
25 |  | Sodium |  |  |  | 390 mg/L | 390 mg/L | 390 mg/L
26 |  | Strontium |  |  |  | 0.72 mg/L | 0.72 mg/L | 0.72 mg/L
27 |  | Sulphate SO4 |  |  |  | 1000 mg/L | 1000 mg/L | 1000 mg/L
28 |  | Other ions reference |  |  |  | Ref. 4 | Ref. 4 | Ref. 4
29
30 |  | Note - in absence of detailed ionic breakdown for either Keadby 3 Option 1 nor Option 2, the concentration of other ions has been applied for
31 |  | Keadby 3 Options 1 and 2 as was calculated for Keadby 2. This is a reasonable assumption because Keadby 3 would use the same source
32 |  | for make-up water (i.e. canal water), and the same cycles of concentration (4) have been assumed for both power stations.
33
34
35
36
37
38
39
40
41
42
43
44
45