## Grimsby A
Emission Calculations
|  | Data Provided |  | Data Provided
|  | Data Calculated |  | Data Calculated
Parameter | Data Provided |  | Flow (Actual) | Flow (Norm 0deg, Wet,Act O2) | Flow (Norm 0deg, dry,11% O2) | Velocity | Flue Area | Calc % H2O | Flow (Actual Wet O2) | Plume Visibility
Height (m)
# of Engines | [9 empty] | Flue gas density | 1.2 | kg/m3 wet
Flue gas flow wet, Am3/h |  | 24480 | 24480 | 24480 | 24156.252 | 24480 | 24480 | 24480 | 24480 | Flue gas mass | #REF! | kg/s
Flue gas flow wet, Am3/s | 6.8 | 6.8 | 6.8 | 6.8 | 6.7101 | 6.8 | 6.8 | 6.8 | 6.8 | water | #REF! | Nm3/h
Duct temp, Deg C | 451 | 451 | 451 | 451 | 451 | 451 | 451 | 451 | 451 | water | #REF! | Nm3/s
Duct O2, % vol (wet basis) |  | 8.319 | 8.319 | 8.319 | 8.4305 | 8.319 | 8.319 |  | 8.319 | water density | 0.7622 | kg/m3
Duct O2, % vol (dry basis) | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | water mass | #REF! | kg/s
Duct H2O, % vol | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | water % mass | #REF! | %
Flue gas flow, Nm3/h (0 degC, WET, Actual O2) |  | 9230.7182 | 9230.7182 | 9230.7182 | 9108.642 | 9230.7182 | 9230.7182 | 9230.7182 | 9230.7182
Flue gas flow, Nm3/s (0 degC, WET, Actual O2) |  | 2.5641 | 2.5641 | 2.5641 | 2.5302 | 2.5641 | 2.5641 | 2.5641 | 2.5641
Flue diameter, m | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.50023 | #REF! | 0.5 | 0.5 | Air Density
Flue area, m2 |  | 0.19635 | 0.19635 | 0.19635 | 0.19635 | 0.19653 | #REF! | 0.19635 | 0.19635 | Air pressure | 101325 | Pa | 101325 | Pa
Stack velocity, m/s | 34.6 | 34.6 | 34.6321 | 34.6321 | 34.1741 | 34.6 | #REF! | 34.6321 | 34.6321 | Specific gas constant | 287.05 | j/(kg.k) | 287.05 | j/(kg.k)
Flue gas flow, Nm3/h (0 degC, DRY, Actual O2) |  | 8169.1856 | 8169.1856 | 8169.1856 | 8169.1856 | 8169.1856 | 8169.1856 | 8169.1856 | 8169.1856 | Temp | 451 | Deg C | #REF! | Deg C
Flue gas flow, Nm3/s (0 degC, DRY, Actual O2) |  | 2.2692 | 2.2692 | 2.2692 | 2.2692 | 2.2692 | 2.2692 | 2.2692 | 2.2692 |  | 724.15 | deg K | #REF! | deg K
[10 empty] | Density of dry air | 0.48745 | kg/m3 | #REF! | kg/m3
| Concentration | Mass Emissions
Pollutant | mg.Nm3 | g.s-1 | [7 empty] | Concentration Change with temp
% O2 for Emission Values | 5 | - | - | - | - | - | - |  |  | Measured Conc | 1257 | g or ouE/m3
Flue gas flow, Nm3/h (0 degC, DRY, 5% O2 | - | 5922.6596 | 5922.6596 | 5922.6596 | 5922.6596 | 5922.6596 | 5922.6596 |  | 5922.6596 | Sampling temp | 29 | Deg C
Flue gas flow, Nm3/s (0 degC, DRY, 5% O2 | - | 1.6452 | 1.6452 | 1.6452 | 1.6452 | 1.6452 | 1.6452 |  | 1.6452 | Normalised Conc | 1390.5275 | g or ouE/m3
NOx |  | 0 | [7 empty] | Measured Conc | 1323.122 | g or ouE/m3
CO |  | 0 | [7 empty] | Sampling temp | 30 | Deg C
[10 empty] | Normalised Conc | 1468.52 | g or ouE/m3
| Concentration | Mass Emissions | [7 empty] | Re: Conversion Kg/Hr to M3/h
Pollutant | mg.Nm3 | g.s-1 | [7 empty] | Flue Gas Mass Flow |  | g/s |  | g/s
% O2 for Emission Values | 15 | - | - | - | - | - | - |  |  | Flue Gas Mass Flow | 24773 | kg/h | 15396 | kg/h
Flue gas flow, Nm3/h (0 degC, DRY, 5% O2 | - | 15793.7589 | [7 empty] | Dry air at 0º C has a density of | 1.2944 | kg/m³ | 1.2944 | kg/m³
Flue gas flow, Nm3/s (0 degC, DRY, 5% O2 | - | 4.3872 | [7 empty] | Density of stack gas @ temperature | 0.48745 | kg/m³ | #REF! | kg/m³
NOx | 190 | 0.83356 | [7 empty] | kg/hr / (Density kg/m³) = m³/hr | 19138.0352 | m³/hr | 11893.9648 | m³/hr | 12149
CO | 393.75 | 1.7274 | [7 empty] | kg/hr / (Density kg/m³) = m³/hr | 50821.5699 | m³/hr | #REF! | m³/hr | #REF!
Converting air pollutant concentrations
ppmv = mg/m3*((0.08205*T)/M)
NO2 | 133 | 0.58349 | 66.5 | [6 empty] | mg/m3 = ppmv*(M/(0,08205*T))
@ 1,500 hours | 22.774 | 0.099913 | [8 empty] | ppmv = air pollutant concentration, in parts per million by volume
@ 2,250 hours | 34.161 | 0.14987 | [8 empty] | mg/m³ = milligrams of pollutant per cubic meter of air
T = atmospheric temperature in kelvins = 273.15 + °C
0.08205 = Universal Gas Law constant in atm·l/(mol·K)
M = molecular weight of the air pollutant (dimensionless)
Pressure Corrections
= measured value * (101.3 (Kpa)/measured [pressure (Kpa))
[10 empty] | Standard Pressure | 101.3
[10 empty] | Measure Pressure | 100
[10 empty] | Measure Value | 344
[10 empty] | Corrected Value | 348.472
Note on M7: Approximation
Note on L17: Patrick Froggatt: Standard pressure at sea level 101325 Pa)
Note on L18: Patrick Froggatt: Specifi gas constant for dry air 287.05 j/(kg.k)

## Grimsby B
Emission Calculations
|  | Data Provided | [5 empty] | Data Provided
|  | Data Calculated | [5 empty] | Data Calculated
|  | JMS 624 GS-N.L |  | JMS 616 GS-N.L
Parameter | Data Provided | Per Engine Clark 4.5MW | Per Engine Clark 4.5MW | Per Engine Clark 2.67MW |  |  | Flow (Actual) | Flow (Norm 0deg, Wet,Act O2) | Flow (Norm 0deg, dry,11% O2) | Velocity | Flue Area | Calc % H2O | Flow (Actual Wet O2) | Plume Visibility
Height (m) |  | 10 | 10 | 10
# of Engines |  | 1 | 4 | 1 | [9 empty] | Flue gas density | 1.2 | kg/m3 wet
Flue gas flow wet, Am3/h |  | 44479.978 | 78216 | 28258.663 |  |  | 44479.978 | 44479.978 | 44052.7923 | 44479.978 | 44479.978 | 44479.978 | 44479.978 | Flue gas mass | #REF! | kg/s
Flue gas flow wet, Am3/s |  | 12.3555 | 21.7267 | 7.8496 |  |  | 12.3555 | 12.3555 | 12.2369 | 12.3555 | 12.3555 | 12.3555 | 12.3555 | water | #REF! | Nm3/h
Duct temp, Deg C |  | 348 | 0 | 362 |  |  | 348 | 348 | 348 | 348 | 348 | 348 | 348 | water | #REF! | Nm3/s
Duct O2, % vol (wet basis) | 9.8 / 10 | 9.7596 | 9.7596 | 9.9711 |  |  | 9.7596 | 9.7596 | 9.8543 | 9.7596 | 9.7596 |  | 9.7596 | water density | 0.7622 | kg/m3
Duct O2, % vol (dry basis) | 10.82 / 11.03 | 10.82 | 10.82 | 11.03 |  |  | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | 10.82 | water mass | #REF! | kg/s
Duct H2O, % vol | 9.8 / 9.6 | 9.8 | 9.8 | 9.6 |  |  | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | water % mass | #REF! | %
Flue gas flow, Nm3/h (0 degC, WET, Actual O2) |  | 19554 | 78216 | 12149 |  |  | 19554 | 19554 | 19366.2034 | 19554 | 19554 | 19554 | 19554
Flue gas flow, Nm3/s (0 degC, WET, Actual O2) |  | 5.4317 | 21.7267 | 3.3747 |  |  | 5.4317 | 5.4317 | 5.3795 | 5.4317 | 5.4317 | 5.4317 | 5.4317
Flue diameter, m |  | 0.68022 |  | 0.54218 |  |  | 0.68022 | 0.68022 | 0.68022 | 0.68022 | #REF! | 0.68022 | 0.68022 | Air Density
Flue area, m2 |  | 0.3634 |  | 0.23087 |  |  | 0.3634 | 0.3634 | 0.3634 | 0.3634 | #REF! | 0.3634 | 0.3634 | Air pressure | 101325 | Pa | 101325 | Pa
Stack velocity, m/s |  | 34 |  | 34 |  |  | 34 | 34 | 33.6735 | 34 | #REF! | 34 | 34 | Specific gas constant | 287.05 | j/(kg.k) | 287.05 | j/(kg.k)
Flue gas flow, Nm3/h (0 degC, DRY, Actual O2) |  | 17637.708 | 70550.832 | 10982.696 |  |  | 17637.708 | 17637.708 | 17637.708 | 17637.708 | 17637.708 | 17637.708 | 17637.708 | Temp | 348 | Deg C | 362 | Deg C
Flue gas flow, Nm3/s (0 degC, DRY, Actual O2) |  | 4.8994 | 19.5975 | 3.0507 |  |  | 4.8994 | 4.8994 | 4.8994 | 4.8994 | 4.8994 | 4.8994 | 4.8994 |  | 621.15 | deg K | 635.15 | deg K
[14 empty] | Density of dry air | 0.56828 | kg/m3 | 0.55575 | kg/m3
| Concentration | Mass Emissions
Pollutant | mg.Nm3 | g.s-1 | [11 empty] | Concentration Change with temp
% O2 for Emission Values | 5 | - |  |  |  |  | - | - | - | - | - |  |  | Measured Conc | 1257 | g or ouE/m3
Flue gas flow, Nm3/h (0 degC, DRY, 5% O2 | - | 11221.9917 | 44887.9669 | 6843.5924 |  |  | 11221.9917 | 11221.9917 | 11221.9917 | 11221.9917 | 11221.9917 |  | 11221.9917 | Sampling temp | 29 | Deg C
Flue gas flow, Nm3/s (0 degC, DRY, 5% O2 | - | 3.1172 | 12.4689 | 1.901 |  |  | 3.1172 | 3.1172 | 3.1172 | 3.1172 | 3.1172 |  | 3.1172 | Normalised Conc | 1390.5275 | g or ouE/m3
NOx | 250 | 0.7793 | 3.1172 | 0.47525 |  | 3.1964 | 0.7793 | 0.7793 | 0.7793 | 0.7793 | 0.7793 |  | 0.7793 | Measured Conc | 1323.122 | g or ouE/m3
CO | 1050 | 3.2731 | 13.0923 | 1.996 |  |  | 3.2731 | 3.2731 | 3.2731 | 3.2731 | 3.2731 |  | 3.2731 | Sampling temp | 30 | Deg C
[14 empty] | Normalised Conc | 1468.52 | g or ouE/m3
| Concentration | Mass Emissions | [11 empty] | Re: Conversion Kg/Hr to M3/h
Pollutant | mg.Nm3 | g.s-1 | [11 empty] | Flue Gas Mass Flow |  | g/s |  | g/s
% O2 for Emission Values | 15 | - |  |  |  |  | - | - | - | - | - |  |  | Flue Gas Mass Flow | 24773 | kg/h | 15396 | kg/h
Flue gas flow, Nm3/h (0 degC, DRY, 5% O2 | - | 29925.3112 | 119701.245 | 18249.5799 | [9 empty] | Dry air at 0º C has a density of | 1.2944 | kg/m³ | 1.2944 | kg/m³
Flue gas flow, Nm3/s (0 degC, DRY, 5% O2 | - | 8.3126 | 33.2503 | 5.0693 | [9 empty] | Density of stack gas @ temperature | 0.56828 | kg/m³ | 0.55575 | kg/m³
NOx | 95 | 0.7897 | 3.1588 | 0.48159 | [9 empty] | kg/hr / (Density kg/m³) = m³/hr | 19138.0352 | m³/hr | 11893.9648 | m³/hr | 12149
CO | 393.75 | 3.2731 | 13.0923 | 1.996 | [9 empty] | kg/hr / (Density kg/m³) = m³/hr | 43592.9271 | m³/hr | 27702.8942 | m³/hr | 28258.663
Converting air pollutant concentrations
ppmv = mg/m3*((0.08205*T)/M)
NO2 | 66.5 | 0.55279 | 33.25 | [10 empty] | mg/m3 = ppmv*(M/(0,08205*T))
@ 1,500 hours | 11.387 | 0.094655 | [12 empty] | ppmv = air pollutant concentration, in parts per million by volume
@ 2,250 hours | 17.0805 | 0.14198 | [12 empty] | mg/m³ = milligrams of pollutant per cubic meter of air
T = atmospheric temperature in kelvins = 273.15 + °C
0.08205 = Universal Gas Law constant in atm·l/(mol·K)
M = molecular weight of the air pollutant (dimensionless)
Pressure Corrections
= measured value * (101.3 (Kpa)/measured [pressure (Kpa))
[14 empty] | Standard Pressure | 101.3
[14 empty] | Measure Pressure | 100
[14 empty] | Measure Value | 344
Power Input | kW | 9918 |  | 6075 | [9 empty] | Corrected Value | 348.472
Mechanical output | kW | 4594 |  | 2745
Electrical output | kW el | 4507 |  | 2676
Total output generated | kW total | 7401 |  | 4374
Gas Vol | Nm3/h | 1044 |  | 639
Fuel Gas LHV | kWh/Nm3 | 9.5 |  | 9.5
| kWh/h | 9918 |  | 6070.5 | 45742.5
[5 empty] | 1500 | hrs
[5 empty] | 68613750 | kW/yr
[5 empty] | 68613.75 | MW/yr
|  |  |  | GWP | 190 | CO2 Emission Factor (kg/MWh)
[5 empty] | 13036612.5 | Annual CO2 Emissions (kg)
[5 empty] | 13036.6125 | Annual CO2 Emissions (tonnes)
Note on Q7: Approximation
Note on P17: Patrick Froggatt: Standard pressure at sea level 101325 Pa)
Note on P18: Patrick Froggatt: Specifi gas constant for dry air 287.05 j/(kg.k)

## BG
|  | R1 | R2 | R3 |  |  | R4 | X3 | R5 | R6
Annual | PC | 0.8 | 0.2 | 0.1 |  |  | 0.9 | 0.4 | 2.9 | 1.4
Annual | CC | 2.9 | 0.8 | 0.3 |  |  | 3.2 | 1.3 | 10.9 | 8.3
Annual | PEC | 14.9 | 15 | 14.5 |  |  | 19.4 | 17.6 | 27.1 | 24.5
ST | PC 99.79 | 17.2 | 11.7 | 4.7 |  |  | 30.5 | 14.6 | 94.8 | 119
ST | PC 98.8 | 15.5 | 9.1 | 3.6 |  |  | 21.8 | 9.3 | 71.4 | 75.2
ST | CC 99.32 | 55.9 | 35.6 | 14.3 |  |  | 108 | 50.6 | 319.7 | 607.8
ST | PEC 99.33 | 80 | 64 | 42.7 |  |  | 140.5 | 83.1 | 352.2 | 640.3
|  | 12 | 14.2 | 14.2 |  |  | 16.2 | 16.3 | 16.2 | 16.2
|  | 24.1 | 28.4 | 28.4 |  |  | 32.5 | 32.5 | 32.5 | 32.5
Annual | PC | 2% | 0.5% | 0.25% |  |  | 3% | 1.333% | 9.667% | 4.667%
Annual | CC | 7.25% | 2% | 0.75% |  |  | 10.67% | 4.333% | 36.33% | 27.67%
Annual | PEC | 37.25% | 37.5% | 36.25% |  |  | 64.67% | 58.67% | 90.33% | 81.67%
ST | PC 99.79 | 8.6% | 5.85% | 2.35% |  |  | 40.67% | 19.47% | 126.4% | 158.7%
ST | PC 98.8 | 7.75% | 4.55% | 1.8% |  |  | 29.07% | 12.4% | 95.2% | 100.3%
ST | CC 99.32 | 27.95% | 17.8% | 7.15% |  |  | 144% | 67.47% | 426.3% | 810.4%
|  | N/A | N/A | N/A |  |  | N/A | N/A | N/A | N/A
ST | PEC 99.33 | 31.78% | 20.75% | 8.333% | ST | PEC 99.33 | 254.1% | 119.1% | 752.2% | 1430%