## SL3 X DRAUGHT
SPINNING MACHINES CROSS DRAUGHT EXHAUST
STREAM 3 | [6 empty] | STREAM 4
DATE | Sampled Time | DEMISTER FLOW (m3 / hr) | TEMPERATURE (OC) | AIR SPEED (ms-1) | AMINES CONCENTRATION (ppm as NH3) | AMINES CONCENTRATION (As amines) | DATE | Sampled Time | DEMISTER FLOW (m3 / hr) | TEMPERATURE (OC) | AIR SPEED (ms-1) | AMINES CONCENTRATION (ppm as NH3) | AMINES CONCENTRATION (As amines)
[5 empty] | Limit 5 ppm | Limit 10 ppm | [5 empty] | Limit 5 ppm | Limit 10 ppm
2002-12-30 |  | 0.63 | 30 | 11.03 | 0.25 | 0.5 | 2002-12-30 |  | 0.63 | 26 | 8.06 | 0.5 | 1
2003-01-06 |  | 3 | 31 | 11.31 | 0.25 | 0.5 | 2003-01-06 |  | 1.6 | 29 | 7.95 | 0.5 | 1
2003-01-13 |  | 3 | 32 | 8.59 | 0.75 | 1.5 | 2003-01-16 |  | 1.8 | 31 | 9.5 | 1 | 2
2003-01-20 |  | 3.4 | 29 | 10.6 | 0.5 | 1 | 2003-01-20 |  | 1.6 | 30 | 7.9 | 0.75 | 1.5
2003-01-27 |  | 3.4 | 33 | 10.3 | 0.5 | 1 | 2003-01-27 |  | 1.8 | 34 | 9.43 | 0.75 | 1.5
2003-02-03 |  | 3.2 | 30 | 10.79 | 0.5 | 1 | 2003-02-03 |  | 1.8 | 24 | 7.63 | 0.5 | 1
2003-02-10 |  | 3 | 31 | 10.5 | 0.5 | 1 | 2003-02-10 |  | 1.8 | 30 | 8.3 | 0.5 | 1
2003-02-17 |  | 3 | 33 | 10.03 | 0.5 | 1 | 2003-02-17 |  | 1.8 | 33 | 9.18 | 1 | 2
2003-02-25 |  | 2.9 | 32 | 11.3 | 0.75 | 1.5 | 2003-02-25 |  | 1.8 | 31 | 10.01 | 0.5 | 1
2003-03-03 |  | 3 | 33 | 10.96 | 0.75 | 1.5 | 2003-03-03 |  | 1.7 | 32 | 10.35 | 0.75 | 1.5
2003-03-11 |  | 2.8 | 32.5 | 10.54 | 0.5 | 1 | 2003-03-11 |  | 1.7 | 32 | 8.52 | 1 | 2
2003-03-17 |  | 3 | 34 | 10.07 | 0.5 | 1 | 2003-03-17 |  | 1.7 | 34 | 8.46 | 1 | 2
2003-03-24 |  | 3 | 34 | 8.75 | 1 | 2 | 2003-03-24 |  | 1.6 | 35 | 9.25 | 1 | 2
2003-04-01 |  | 3 | 33 | 8.05 | 0.75 | 1.5 | 2003-04-01 |  | 1.6 | 33 | 6.3 | 1 | 2
2003-04-07 |  | 3 | 33 | 8.2 | 0.5 | 1 | 2003-04-07 |  | 0 | 0 | 0 | 0 | 0
2003-04-14 |  | 2.8 | 32 | 8.55 | 0.5 | 1 | 2003-04-14 |  | 1.6 | 33 | 5.25 | 0.2 | 0.4
2003-04-23 |  | 2.9 | 35 | 9.3 | 0.75 | 1.5 | 2003-04-23 |  | 1.6 | 35.5 | 6.4 | 0.75 | 1.5
2003-05-01 |  | 3 | 33.5 | 8.25 | 1 | 2 | 2003-05-01 |  | 1.6 | 34.5 | 7.95 | 1 | 2
2003-05-07 |  | 3 | 36 | 8.3 | 1 | 2 | 2003-05-07 |  | 1.6 | 37 | 6.45 | 1.5 | 3
2003-05-12 |  | 3 | 29 | 4.6 | 0.5 | 1 | 2003-05-12 |  | 1.4 | 33 | 6.4 | 1 | 2
2003-05-19 |  | 3 | 35 | 8.65 | 0.75 | 1.5 | 2003-05-19 |  | 1.6 | 35 | 7.65 | 1 | 2
2003-05-27 |  | 3 | 36 | 9.25 | 0.5 | 1 | 2003-05-27 |  | 1.6 | 36 | 8.15 | 0.75 | 1.5
2003-06-02 |  | 3 | 38 | 7.5 | 0.75 | 1.5 | 2003-06-02 |  | 2.6 | 35 | 7.1 | 0.75 | 1.5
2003-06-09 |  | 3 | 40 | 7.75 | 1 | 2 | 2003-06-09 |  | 1.6 | 40 | 6.65 | 0.75 | 1.5
2003-06-16 |  | 3 | 32 | 6.75 | 0.5 | 1 | 2003-06-16 |  | 1.8 | 40 | 7.8 | 0.75 | 1.5
2003-06-24 |  | 3 | 37 | 10.09 | 0.75 | 1.5 | 2003-06-24 |  | 1.8 | 39 | 6.71 | 0.75 | 1.5
2003-07-01 |  | 1.8 | 35 | 5.12 | 0.78 | 1.56 | 2003-07-01 |  | 3.2 | 34 | 9.49 | 0.75 | 1.5
2003-07-07 |  | 3 | 36 | 9.53 | 1 | 2 | 2003-07-07 |  | 1.6 | 36 | 8.93 | 1 | 2
2003-07-16 |  | 2.8 | 36 | 10.64 | 0.75 | 1.5 | 2003-07-16 |  | 1.6 | 34 | 7.43 | 0.5 | 1
2003-07-22 | [5 empty] | 0 | 2003-07-22 |  | 1.6 | 34 | 8.94 | 0.5 | 1
2003-07-29 |  | 2.9 | 34 | 9.5 | 0.4 | 0.8 | 2003-07-29 |  | 1.6 | 38 | 10.3 | 0.75 | 1.5
2003-08-05 |  | 3 | 37 | 9.84 | 0.75 | 1.5 | 2003-08-05 |  | 1.7 | 39 | 7.19 | 0.5 | 1
2003-08-14 |  | 2.8 | 38 | 9.9 | 0.75 | 1.5 | 2003-08-14 |  | 1.4 | 39.5 | 7 | 0.75 | 1.5
2003-08-18 |  | 2.9 | 40 | 8.5 | 0.9 | 1.8 | 2003-08-18 |  | 1.5 | 38 | 7.5 | 1 | 2
2003-08-26 |  | 2.9 | 38 | 9.2 | 0.9 | 1.8 | 2003-08-26 |  | 1.4 | 38 | 5 | 1 | 2
2003-09-02 |  | 2.8 | 38 | 7.5 | 1 | 2 | 2003-09-02 |  | 1.1 | 39 | 5.3 | 1 | 2
2003-09-10 |  | 2.9 | 38 | 9.26 | 1 | 2 | 2003-09-10 |  | 1.5 | 39 | 5.47 | 1 | 2
2003-09-16 |  | 2.9 | 38 | 9.2 | 1 | 2 | 2003-09-16 |  | 1.4 | 39 | 5 | 1 | 2
2003-09-23 |  | 3 | 32 | 8.75 | 1 | 2 | 2003-09-23 |  | 1.5 | 32 | 6.39 | 0.75 | 1.5
2003-10-01 |  | 2.8 | 36 | 10.2 | 0.5 | 1 | 2003-10-01 |  | 1.4 | 36 | 8.8 | 0.5 | 1
2003-10-10 |  | 2.8 | 19 | 1.8 | <0.25 | <0.5 | 2003-10-07 |  | 1.4 | 34 | 8.1 | 0.5 | 1
2003-10-13 |  | 2.8 | 36 | 8.5 | 0.5 | 1 | 2003-10-13 |  | 1.4 | 34 | 5.2 | 0.5 | 1
2003-10-20 |  | 3 | 34 | 9.67 | 1 | 2 | 2003-10-20 |  | 1.6 | 36 | 7.67 | 1 | 2
2003-10-28 |  | 3 | 31 | 9.64 | 1 | 2 | 2003-10-28 |  | 1.6 | 35 | 7.55 | 1 | 2
2003-11-04 |  | 2.8 | 35 | 9.25 | 0.75 | 1.5 | 2003-11-04 |  | 1.7 | 32 | 7.5 | 0.5 | 1
2003-11-11 |  | 2.9 | 34 | 9.3 | 0.5 | 1 | 2003-11-11 |  | 1.6 | 35 | 6.1 | 0.5 | 1
2003-11-18 |  | 3 | 31 | 8.75 | 0.75 | 1.5 | 2003-11-18 |  | 1.8 | 32 | 7.93 | 0.75 | 1.5
2003-11-25 |  | 3 | 32 | 8.8 | 0.5 | 1 | 2003-11-25 |  | 1.6 | 34 | 8.5 | 0.5 | 1
2003-12-01 |  | 3.1 | 28 | 7.86 | 0.5 | 1 | 2003-12-01 |  | 1.75 | 24 | 8.97 | 0.5 | 1
2003-12-08 |  | 2.9 | 27 | 7.91 | 0.75 | 1.5 | 2003-12-08 |  | 1.4 | 23 | 7.82 | 0.3 | 0.6
2003-12-15 |  | 2.95 | 31.7 | 9.05 | 0.3 | 0.6 | 2003-12-15 |  | 1.6 | 34.5 | 10.34 | 0.3 | 0.6
2003-12-22 |  | 2.95 | 32.3 | 8.99 | 0.5 | 1 | 2003-12-22 |  | 1.6 | 33.3 | 5.79 | 0.8 | 1.6
2003-12-31 |  | 3 | 32.1 | 8.68 | 0.8 | 1.6 | 2003-12-31 |  | 1.6 | 36.1 | 8.89 | 0.5 | 1
2004-01-05 |  | 3 | 34 | 9.48 | 0.75 | 1.5 | 2004-01-05 |  | 1.6 | 35 | 4.21 | 1 | 2
2004-01-12 |  | 3.1 | 34.6 | 10.15 | 0.3 | 0.6 | 2004-01-12 |  | 1.6 | 34.5 | 8.64 | 0.35 | 0.7
2004-01-19 |  | 3 | 33 | 9.69 | 1 | 2 | 2004-01-19 |  | 1.6 | 34.6 | 6.4 | 1 | 2
2004-01-26 |  | 3.3 | 32.4 | 8.46 | 0.75 | 1.5 | 2004-01-26 |  | 1.6 | 32.6 | 7.95 | 0.5 | 1
2004-02-09 |  | 3 | 33.3 | 6.95 | 0.75 | 1.5 | 2004-02-09 |  | 1.6 | 36.8 | 9.38 | 1 | 2
2004-02-17 |  | 3 | 33 | 8 | 0.75 | 1.5 | 2004-02-17 |  | 1.5 | 37 | 5.95 | 1 | 2
2004-02-23 |  | 3 | 30 | 8.85 | 1 | 2 | 2004-02-23 |  | 1.5 | 32 | 5.4 | 0.5 | 1
2004-03-01 |  | 3 | 33 | 9.84 | 1 | 2 | 2004-03-01 |  | 1.6 | 35 | 5.55 | 1 | 2
2004-03-08 |  | 2.95 | 33 | 8.76 | 0.3 | 0.6 | 2004-03-08 |  | 1.7 | 34 | 7.03 | 0.45 | 0.9
2004-03-15 |  | 3 | 32 | 8.69 | 0.75 | 1.5 | 2004-03-15 |  | 1.8 | 34 | 6.76 | 1 | 2
2004-03-23 |  | 3 | 30 | 10.34 | 0.5 | 1 | 2004-03-26 |  | 1.4 | 33 | 7.26 | 0.75 | 1.5
2004-03-29 |  | 2.9 | 32 | 10.23 | 0.3 | 0.6 | 2004-03-29 |  | 1.4 | 36 | 8.95 | 0.35 | 0.7
2004-04-05 |  | 3 | 34 | 8.75 | 0.75 | 1.5 | 2004-04-05 |  | 1.4 | 34 | 9.46 | 0.5 | 1
2004-04-13 |  | 3 | 34 | 9.25 | 0.6 | 1.2 | 2004-04-13 |  | 1.6 | 35 | 8.25 | 0.6 | 1.2
2004-04-19 |  | 3 | 28 | 8.35 | 0.2 | 0.4 | 2004-04-19 |  | 1.4 | 35 | 9.7 | 0.3 | 0.6
2004-04-26 |  | 2.9 | 37 | 9.25 | 0.5 | 1 | 2004-04-26 |  | 1.4 | 40 | 9.95 | 0.3 | 0.6
2004-05-04 |  | 3 | 35 | 8.65 | 0.75 | 1.5 | 2004-05-04 |  | 1.6 | 38 | 7.25 | 1 | 2
2004-05-10 |  | 3 | 37 | 8.3 | 0.75 | 1.5 | 2004-05-10 |  | 1.6 | 40 | 7.65 | 1 | 2
2004-05-18 |  | 2.9 | 38 | 9 | 0.5 | 1 | 2004-05-18 |  | 1.6 | 39 | 9.1 | 0.35 | 0.7
2004-05-24 |  | 3 | 36 | 7.32 | 0.75 | 1.5 | 2004-05-24 |  | 1.4 | 35 | 9.38 | 1 | 2
2004-06-01 |  | 3 | 36 | 7.62 | 1 | 2 | 2004-06-01 |  | 1.5 | 37 | 5.83 | 0.75 | 1.5
2004-06-07 |  | 3 | 39 | 7.9 | 0.75 | 1.5 | 2004-06-07 |  | 1.4 | 40 | 6.2 | 0.75 | 1.5
2004-06-14 |  | 3 | 37 | 8.4 | 0.6 | 1.2 | 2004-06-14 |  | 1.4 | 39 | 9.95 | 0.25 | 0.5
2004-06-21 |  | 3 | 37 | 10.56 | 1 | 2 | 2004-06-21 |  | 1.4 | 38 | 4.92 | 1 | 2
2004-06-28 |  | 3 | 36 | 10.96 | 0.75 | 1.5 | 2004-06-28 |  | 1.4 | 37 | 5.71 | 1 | 2
2004-07-05 |  | 2.9 | 36 | 9.59 | 0.5 | 1 | 2004-07-05 |  | 1.5 | 37 | 8.05 | 0.6 | 1.2
2004-07-12 |  | 1.5 | 37 | 6.39 | 1 | 2 | 2004-07-12 |  | 1.5 | 38 | 9.72 | 1 | 2
2004-07-20 |  | 2.9 | 36 | 11.04 | 1 | 2 | 2004-07-20 |  | 1.4 | 37 | 7.23 | 1 | 2
2004-07-26 |  | 2.8 | 36 | 9.73 | 0.4 | 0.8 | 2004-07-26 |  | 1.4 | 39 | 11.48 | 0.35 | 0.7
2004-08-06 |  | 3 | 38 | 11.86 | 1 | 2 | 2004-08-06 |  | 1.4 | 39 | 7.61 | 1 | 2
2004-08-10 |  | 2.8 | 37 | 10.97 | 0.3 | 0.6 | 2004-08-10 |  | 1.4 | 38 | 10.86 | 0.25 | 0.5
2004-08-16 |  | 3 | 38 | 10.87 | 1 | 2 | 2004-08-16 |  | 1.5 | 40 | 7.01 | 1 | 2
2004-08-23 |  | 3 | 36 | 10.72 | 0.75 | 1.5 | 2004-08-23 |  | 1.4 | 38 | 6.49 | 1 | 2
2004-08-31 |  | 2.8 | 37 | 10.94 | 1 | 2 | 2004-08-31 |  | 1.3 | 39 | 7.43 | 1 | 2
2004-09-06 |  | 3 | 37 | 10.53 | 0.75 | 1.5 | 2004-09-06 |  | 1.3 | 38 | 8.97 | 0.75 | 1.5
2004-09-13 |  | 2.8 | 34 | 10.6 | 0.5 | 1 | 13-Seo-04 |  | 1.5 | 36 | 10.63 | 0.7 | 1.4
2004-09-22 |  | 3 | 35 | 7.26 | 1 | 2 | 2004-09-22 |  | 1.2 | 36 | 9.35 | 1 | 2
2004-09-27 |  | 2 | 36 | 6.79 | 0.75 | 1.5 | 2004-09-27 |  | 1.2 | 37 | 9.57 | 1 | 2
2004-10-06 |  | 2.6 | 36 | 6.79 | 0.5 | 1 | 2004-10-06 |  | 1.2 | 38 | 9.36 | 0.5 | 1
2004-10-11 |  | 2.8 | 34 | 10.47 | 0.3 | 0.6 | 2004-10-11 |  | 1.3 | 35 | 10.7 | 0.4 | 0.8
2004-10-18 |  | 2.8 | 33 | 9.36 | 0.75 | 1.5 | 2004-10-18 |  | 1.4 | 34 | 6.02 | 0.75 | 1.5
2004-10-25 |  | 2.8 | 36 | 10.18 | 0.5 | 1 | 2004-10-25 |  | 1.5 | 35 | 6.32 | 1 | 2
2004-11-01 |  | 2.9 | 35 | 10.42 | 0.3 | 0.6 | 2004-11-01 |  | 1.4 | 35 | 10.94 | 0.5 | 1
2004-11-08 |  | 2.8 | 34 | 10.12 | 0.25 | 0.5 | 2004-11-08 |  | 1.3 | 35 | 10.66 | 0.4 | 0.8
2004-11-15 |  | 2 | 36 | 9.56 | 1 | 2 | 2004-11-15 |  | 0.63 | 37 | 6.06 | 0.5 | 1
2004-11-22 |  | 2.8 | 35 | 10.45 | 1 | 2 | 2004-11-22 |  | 1.4 | 35 | 6.7 | 1 | 2
2004-11-29 |  | 2.8 | 34 | 10.4 | 0.35 | 0.7 | 2004-11-29 |  | 1.4 | 30 | 9.4 | 0.65 | 1.3
2004-12-06 |  | 2.8 | 35 | 9.33 | 0.25 | 0.5 | 2004-12-06 |  | 1.4 | 35 | 4.6 | 1 | 2
2004-12-13 |  | 2.8 | 33 | 10.57 | 0.5 | 1 | 2004-12-13 |  | 1.3 | 34 | 10.18 | 0.6 | 1.2
2004-12-20 |  | 2.9 | 33 | 9.86 | 0.5 | 1 | 2004-12-20 |  | 1.4 | 33 | 11.05 | 0.3 | 0.6
2004-12-30 |  | 3 | 34 | 9.86 | 0.5 | 1 | 2004-12-30 |  | 1.3 | 34 | 5.52 | 0.5 | 1
2005-01-05 |  | 3 | 34 | 10.7 | 0.25 | 0.5 | 2005-01-05 |  | 1.5 | 34 | 9.97 | 0.5 | 1
2005-01-11 |  | 3 | 33 | 10.4 | 0.4 | 0.8 | 2005-01-11 |  | 1.6 | 35 | 6.5 | 0.45 | 0.9
2005-01-17 |  | 3 | 33 | 10.78 | 0.5 | 1 | 2005-01-17 |  | 1.6 | 34 | 11.09 | 0.7 | 1.4
2005-01-24 |  | 2.5 | 34 | 9.5 | 0.25 | 0.5 | 2005-01-24 |  | 1.4 | 35 | 7.5 | 0.25 | 0.5
2005-01-31 |  | 2.8 | 35 | 9.74 | 0.25 | 0.5 | 2005-01-31 |  | 1.4 | 31 | 11.22 | 1.5 | 3
2005-02-07 |  | 2.6 | 35 | 10.5 | 0.5 | 1 | 2005-02-07 |  | 1 | 36 | 5.4 | 0.5 | 1
2005-02-15 |  | 2.8 | 34 | 8.35 | 1 | 2 | 2005-02-15 |  | 1.3 | 35 | 6.1 | 1 | 2
2005-02-22 |  | 2.8 | 34 | 11.3 | 0.7 | 1.4 | 2005-02-22 |  | 1.2 | 34 | 9.1 | 0.85 | 1.7
2005-02-28 |  | 3 | 34 | 10.4 | 0.3 | 0.6 | 2005-02-28 |  | 1.2 | 35 | 6.8 | 0.25 | 0.5
2005-03-08 |  | 2.8 | 33 | 11.06 | 1 | 2 | 2005-03-08 |  | 1.2 | 34 | 5.3 | 0.75 | 1.5
2005-03-14 |  | 2.5 | 35 | 9.4 | 0.5 | 1 | 2005-03-14 |  | 1.2 | 35 | 7.9 | 0.52 | 1.04
2005-03-21 |  | 2.8 | 35 | 10.4 | 0.35 | 0.7 | 2005-03-21 |  | 1.4 | 37 | 8 | 0.5 | 1
2005-03-29 |  | 2.8 | 35 | 9.3 | 0.25 | 0.5 | 2005-03-29 |  | 1.4 | 35 | 8 | 0.5 | 1
2005-04-04 |  | 2.7 | 34 | 10.8 | 0.5 | 1 | 2005-04-04 |  | 1.2 | 35 | 9.7 | 0.5 | 1
2005-04-11 |  | 3 | 33 | 11.76 | 0.75 | 1.5 | 2005-04-11 |  | 1.2 | 36 | 5.39 | 0.8 | 1.6
2005-04-18 |  | 2.8 | 35 | 10.94 | 1 | 2 | 2005-04-18 |  | 1.2 | 30 | 6.57 | 0.5 | 1
2005-04-25 |  | 2.7 | 31 | 9.75 | 0.25 | 0.5 | 2005-04-25 |  | 1.2 | 32 | 6.6 | 0.6 | 1.2
2005-05-03 |  | 2.7 | 37 | 10.5 | 0.6 | 1.2 | 2005-05-03 |  | 1.2 | 38 | 9.5 | 0.6 | 1.2
2005-05-09 |  | 2.8 | 34 | 10.35 | 0.75 | 1.5 | 2005-05-09 |  | 1.3 | 35 | 5.79 | 1 | 2
2005-05-16 |  | 2.7 | 33 | 10.46 | 0.3 | 0.6 | 2005-05-16 |  | 1.2 | 35 | 10.76 | 0.35 | 0.7
2005-05-23 |  | 2.8 | 36 | 9.75 | 0.3 | 0.6 | 2005-05-23 |  | 1.4 | 36 | 9.2 | 0.6 | 1.2
2005-05-31 |  | 2.8 | 35 | 10.45 | 0.8 | 1.6 | 2005-05-31 |  | 1.2 | 36 | 5.5 | 0.8 | 1.6
2005-06-06 |  | 2.8 | 36 | 10.43 | 0.6 | 1.2 | 2005-06-06 |  | 1.6 | 36 | 10.77 | 0.6 | 1.2
2005-06-13 |  | 2.4 | 35 | 11.58 | 0.5 | 1 | 2005-06-13 |  | 1.2 | 35 | 10.88 | 0.5 | 1
2005-06-20 |  | 2.7 | 37 | 11.44 | 0.25 | 0.5 | 2005-06-20 |  | 1.4 | 38 | 11.56 | 0.25 | 0.5
2005-06-27 |  | 2.6 | 37 | 10.9 | 0.5 | 1 | 2005-06-27 |  | 1.4 | 39 | 8 | 0.8 | 1.6
2005-07-04 |  | 2.7 | 35 | 10.98 | 0.3 | 0.6 | 2005-07-04 |  | 1.4 | 36 | 11.99 | 0.5 | 1
2005-07-11 |  | 2.8 | 33 | 9.65 | 0.65 | 1.3 | 2005-07-11 |  | 1.4 | 33 | 7.75 | 0.6 | 1.2
2005-07-18 |  | 2.8 | 37 | 10.5 | 0.6 | 1.2 | 2005-07-18 |  | 1.4 | 37 | 9.5 | 0.5 | 1
2005-07-25 |  | 2.8 | 37 | 9.85 | 0.35 | 0.7 | 2005-07-25 |  | 1.2 | 37 | 8.5 | 0.35 | 0.7
2005-08-01 |  | 2.8 | 37 | 9.75 | 0.6 | 1.2 | 2005-08-01 |  | 1.2 | 37 | 8.5 | 0.25 | 0.5
2005-08-08 |  | 2.8 | 36.3 | 10.62 | 1 | 2 | 2005-08-08 |  | 1.2 | 36.8 | 5.68 | 1 | 2
2005-08-15 |  | 2.7 | 39.2 | 9.96 | 0.5 | 1 | 2005-08-15 |  | 1.3 | 36.9 | 10.62 | 0.5 | 1
2005-08-22 |  | 2.8 | 33 | 10.92 | 0.5 | 1 | 2005-08-22 |  | 1.3 | 34.1 | 11.14 | 0.4 | 0.8
2005-09-02 |  | 2.8 | 37 | 10.54 | 0.8 | 1.6 | 2005-09-02 |  | 1.2 | 35.8 | 11.76 | 0.5 | 1
2005-09-05 |  | 2.7 | 37.8 | 10 | 0.6 | 1.2 | 2005-09-05 |  | 1.2 | 36 | 9.75 | 0.4 | 0.8
2005-09-12 |  | 2.8 | 38.1 | 9.6 | 0.25 | 0.5 | 2005-09-12 |  | 1.3 | 37.7 | 8.2 | 0.4 | 0.8
2005-09-19 |  | 2.8 | 37 | 10.8 | 0.4 | 0.8 | 2005-09-19 |  | 1.2 | 37.1 | 8 | 0.4 | 0.8
2005-09-26 |  | 2.4 | 35.9 | 11.82 | 0.5 | 1 | 2005-09-26 |  | 1.1 | 36.1 | 10.53 | 0.5 | 1
2005-10-04 |  | 2.6 | 37 | 9.25 | 0.25 | 0.5 | 2005-10-04 |  | 1.4 | 37 | 8 | 0.1 | 0.2
2005-10-10 |  | 2.4 | 36.8 | 11.06 | 0.5 | 1 | 2005-10-10 |  | 1.4 | 36.7 | 10.12 | 0.5 | 1
2005-10-17 |  | 2.7 | 31 | 8.75 | 0.25 | 0.5 | 2005-10-17 |  | 1.2 | 36.2 | 8.8 | 0.55 | 1.1
2005-10-25 |  | 2.7 | 35.1 | 10.71 | 0.6 | 1.2 | 2005-10-25 |  | 1.4 | 35.1 | 11.38 | 0.5 | 1
2005-10-31 |  | 2.9 | 36 | 11.51 | 0.4 | 0.8 | 2005-10-31 |  | 1.6 | 34 | 9.84 | 0.75 | 1.5
2005-11-07 |  | 3 | 35.2 | 11.1 | 0.6 | 1.2 | 2005-11-07 |  | 1.6 | 34.2 | 10.5 | 0.5 | 1
2005-11-14 |  | 3 | 37 | 9.75 | 0.6 | 1.2 | 2005-11-14 |  | 1.4 | 30 | 10 | 0.6 | 1.2
2005-11-21 |  | 3 | 29.2 | 10.31 | 0.6 | 1.2 | 2005-11-21 |  | 1.4 | 33.5 | 9.41 | 0.6 | 1.2
[7 empty] | 2005-11-29 |  | 1.6 | 34.9 | 9.85 | 0.5 | 1
2005-12-05 |  | 3.6 | 30.4 | 10.75 | 0.5 | 1 | 2005-12-05 |  | 1.8 | 33.8 | 11.82 | 0.5 | 1
2005-12-12 |  | 2.6 | 34.1 | 10.68 | 0.4 | 0.8 | 2005-12-12 |  | 1.2 | 33.2 | 10.61 | 0.5 | 1
2005-12-19 |  | 2.6 | 33.8 | 10.79 | 0.5 | 1 | 2005-12-19 |  | 1.2 | 32.8 | 11.72 | 0.75 | 1.5
2005-12-28 |  | 2.6 | 32.9 | 10.76 | 0.5 | 1 | 2005-12-28 |  | 1.2 | 30.6 | 10.86 | 0.5 | 1
2006-01-04 |  | 2.7 | 30.8 | 10.25 | 0.25 | 0.5 | 2006-01-04 |  | 1.2 | 29.8 | 9.5 | 0.5 | 1
2006-01-09 |  | 2.7 | 32.3 | 10.91 | 0.5 | 1 | 2006-01-09 |  | 1.2 | 33.6 | 9.99 | 0.5 | 1
2006-01-16 |  | 2.6 | 32 | 10.43 | 0.5 | 1 | 2006-01-16 |  | 1.2 | 32.6 | 10.88 | 0.5 | 1
2006-01-23 |  | 2.6 | 33.8 | 10.61 | 0.6 | 1.2 | 2006-01-23 |  | 1.2 | 25.1 | 10.59 | 0.3 | 0.6
2006-01-30 |  | 2.8 | 34.4 | 11.29 | 0.4 | 0.8 | 2006-01-30 |  | 1.2 | 35.6 | 11.7 | 0.75 | 1.5
2006-02-06 |  | 2.4 | 32.1 | 10 | 0.5 | 1 | 2006-02-06 |  | 1.2 | 30.9 | 7.2 | 0.5 | 1
2006-02-14 |  | 2.7 | 34.8 | 11.58 | 0.6 | 1.2 | 2006-02-14 |  | 1.3 | 32.9 | 10.61 | 0.7 | 1.4
2006-02-23 |  | 2.6 | 35 | 10.5 | 0.25 | 0.5 | 2006-02-24 |  | 1.2 | 30 | 9.1 | 0.75 | 1.5
2006-03-01 |  | 2.8 | 33.4 | 10.8 | 0.5 | 1 | 2006-03-01 |  | 1.3 | 24.8 | 7.8 | 0.6 | 1.2
2006-03-06 |  | 2.8 | 33.7 | 9.6 | 0.6 | 1.2 | 2006-03-06 |  | 1.3 | 33.4 | 10.1 | 0.5 | 1
2006-03-13 |  | 2.8 | 32.4 | 9 | 0.7 | 1.4 | 2006-03-13 |  | 1.3 | 32.5 | 10.3 | 0.6 | 1.2
2006-03-20 |  | 2.8 | 34.1 | 7.5 | 0.5 | 1 | 2006-03-20 |  | 1.4 | 32.8 | 8.8 | 0.6 | 1.2
2006-03-27 |  | 2.8 | 34.7 | 11.22 | 0.5 | 1 | 2006-03-27 |  | 1.4 | 33.8 | 11.16 | 0.75 | 1.5
2006-04-03 |  | 2.8 | 34.9 | 11.39 | 0.7 | 1.4 | 2006-04-03 |  | 1.4 | 34.8 | 11.2 | 0.7 | 1.4
2006-04-10 |  | 2.8 | 34.2 | 10.97 | 0.75 | 1.5 | 2006-04-10 |  | 1.3 | 34.9 | 11.65 | 0.6 | 1.2
2006-04-18 |  | 2.7 | 35.6 | 11.32 | 0.6 | 1.2 | 2006-04-18 |  | 1.6 | 36.3 | 11.45 | 0.6 | 1.2
2006-04-24 |  | 2.7 | 35.4 | 11.13 | 0.6 | 1.2 | 2006-04-24 |  | 1.2 | 29.9 | 10.29 | 0.4 | 0.8
2006-05-02 |  | 2.7 | 35.5 | 10.37 | 0.6 | 1.2 | 2006-05-02 |  | 1.4 | 34.9 | 11.66 | 0.6 | 1.2
2006-05-09 |  | 2.7 | 37.1 | 10.46 | 0.6 | 1.2 | 2006-05-09 |  | 1.4 | 36.4 | 10.97 | 0.5 | 1
2006-05-15 |  | 2.8 | 35.9 | 10.38 | 0.3 | 0.6 | 2006-05-15 |  | 1.3 | 36.4 | 10.63 | 0.4 | 0.8
2006-05-22 |  | 2.8 | 35.9 | 10.39 | 0.3 | 0.6 | 2006-05-22 |  | 1.3 | 36.2 | 11.47 | 0.6 | 1.2
2006-05-30 |  | 2.8 | 35.2 | 9.7 | 0.25 | 0.5 | 2006-05-30 |  | 1.4 | 33.4 | 5.3 | 0.5 | 1
2006-06-05 |  | 2.8 | 35.5 | 10.3 | 0.6 | 1.2 | 2006-06-05 |  | 1.3 | 35.5 | 9.45 | 0.75 | 1.5
2006-06-12 | [6 empty] | 2006-06-12 |  | 1.2 | 36.9 | 10 | 0.5 | 1
2006-06-19 |  | 2.7 | 37.2 | 9.15 | 0.6 | 1.2 | 2006-06-19 |  | 1.6 | 32.1 | 11.3 | 0.7 | 1.4
2006-06-26 |  | 2.7 | 35.8 | 10 | 0.5 | 1 | 2006-06-26 |  | 1.9 | 32.3 | 8.85 | 0.9 | 1.8
2006-07-03 |  | 2.7 | 37.7 | 10.1 | 0.6 | 1.2 | 2006-07-03 |  | 1.8 | 37.7 | 9.8 | 0.75 | 1.5
2006-07-11 |  | 2.8 | 36.9 | 8.9 | 0.4 | 0.8 | 2006-07-11 |  | 1.4 | 39.2 | 10.15 | 0.5 | 1
2006-07-17 |  | 2.7 | 38.4 | 9.65 | 0.5 | 1 | 2006-07-17 |  | 1.4 | 38.7 | 9.6 | 0.7 | 1.4
2006-07-24 |  | 3.1 | 38.3 | 8.75 | 0.75 | 1.5 | 2006-07-24 |  | 1.3 | 37.4 | 9.45 | 0.6 | 1.2
2006-07-31 |  | 3.2 | 38.6 | 9.35 | 0.75 | 1.5 | 2006-07-31 |  | 1.8 | 38.2 | 9.5 | 0.8 | 1.6
2006-08-07 |  | Both streams down all week for site shutdown |  |  |  |  | 2006-08-07 |  | Both streams down all week for site shutdown |  |  |  | 0
2006-08-15 |  | 2.6 | 28 | 8 | 1 | 2 | 2006-08-15 |  | 1.2 | 29.5 | 9 | 1.1 | 2.2
2006-08-21 |  | 2.7 | 36.8 | 11.6 | 0.4 | 0.8 | 2006-08-21 |  | 1.6 | 36.1 | 10.83 | 1.2 | 2.4
2006-08-29 |  | 2.6 | 35.4 | 9.5 | 0.8 | 1.6 | 2006-08-29 |  | 1.9 | 34.5 | 10.25 | 1.1 | 2.2
2006-09-04 |  | 2.6 | 32.8 | 9.4 | 0.3 | 0.6 | 2006-09-04 |  | 2 | 31 | 9.25 | 0.7 | 1.4
2006-09-11 |  | 2.6 | 39.4 | 9.4 | 0.6 | 1.2 | 2006-09-11 |  | 2.2 | 40.4 | 9.7 | 0.7 | 1.4
2006-09-18 |  | 2.6 | 37.6 | 9.35 | 0.5 | 1 | 2006-09-20 |  | 2 | 37.6 | 9.45 | 0.4 | 0.8
2006-09-25 |  | 2.7 | 36.3 | 10.76 | 1.3 | 2.6 | 2006-09-25 |  | 2.1 | 22 | 2.4 | 0.15 | 0.3
2006-10-02 |  | 2.6 | 30.3 | 8.6 | 0.3 | 0.6 | 2006-10-02 |  | 1.2 | 33.8 | 9.35 | 0.5 | 1
2006-10-09 |  | 2.6 | 35 | 11.01 | 0.55 | 1.1 | 2006-10-09 |  | 1.4 | 35.3 | 10.4 | 0.7 | 1.4
2006-10-16 |  | 2.6 | 36.1 | 11.66 | 0.5 | 1 | 2006-10-16 |  | 1.4 | 28.4 | 10.59 | 0.4 | 0.8
2006-10-23 |  | 2.6 | 35.2 | 11.56 | 0.6 | 1.2 | 2006-10-23 |  | 1.2 | 31.4 | 12.26 | 0.6 | 1.2
2006-10-30 |  | 2.6 | 35.6 | 10.59 | 0.4 | 0.8 | 2006-10-30 |  | 1.2 | 36.4 | 10.94 | 0.5 | 1
2006-11-06 |  | 2.6 | 35.5 | 10.92 | 0.6 | 1.2 | 2006-11-06 |  | 1.2 | 34.8 | 11.09 | 0.5 | 1
2006-11-14 |  | 2.8 | 35.4 | 11.58 | 0.5 | 1 | 2006-11-13 |  | 1.2 | 33 | 9.86 | 0.6 | 1.2
2006-11-20 |  | 2.7 | 36.3 | 10.55 | 0.5 | 1 | 2006-11-20 |  | 1.2 | 36.3 | 11.01 | 0.6 | 1.2
2006-11-27 |  | 2.7 | 36.7 | 10.63 | 0.5 | 1 | 2006-11-27 |  | 1.3 | 36.9 | 11.29 | 0.7 | 1.4
2006-12-04 |  | 2.7 | 34 | 10.47 | 0.5 | 1 | 2006-12-04 |  | 1.3 | 34 | 10.69 | 0.5 | 1
2006-12-11 |  | 2.8 | 34.2 | 10.8 | 0.75 | 1.5 | 2006-12-11 |  | 1.4 | 34.5 | 9.8 | 0.8 | 1.6
2006-12-19 |  | 2.8 | 34.8 | 10.23 | 0.4 | 0.8 | 2006-12-19 |  | 1.4 | 33.9 | 11.41 | 0.4 | 0.8
2006-12-28 |  | 2.8 | 36.2 | 10.5 | 0.7 | 1.4 | 2006-12-28 |  | 1.4 | 30.1 | 11 | 0.8 | 1.6
2007-01-04 |  | 2.9 | 34.9 | 11.2 | 0.5 | 1 | 2007-01-04 |  | 1.5 | 34.2 | 10.72 | 0.5 | 1
2007-01-09 |  | 2.95 | 35.2 | 11.35 | 0.5 | 1 | 2007-01-09 |  | 1.6 | 28.6 | 8.74 | 0.5 | 1
2007-01-15 |  | 3 | 28.7 | 8.88 | 0.7 | 1.4 | 2007-01-15 |  | 1.6 | 31.5 | 9.66 | 0.9 | 1.8
2007-01-23 |  | 2.8 | 33.8 | 11.06 | 0.7 | 1.4 | 2007-01-23 |  | 1.5 | 25.8 | 11.47 | 0.6 | 1.2
2007-01-30 |  | 2.9 | 32.3 | 11.14 | 0.7 | 1.4 | 2007-01-30 |  | 1.6 | 25.2 | 12.25 | 0.9 | 1.8
2007-02-05 |  | 3 | 32.6 | 11.11 | 0.5 | 1 | 2007-02-05 |  | 1.3 | 27.1 | 11.43 | 0.25 | 0.5
2007-02-12 |  | 2.8 | 30.2 | 9.84 | 1.5 | 3 | 2007-02-12 |  | 1.5 | 30.8 | 7.81 | 0.4 | 0.8
2007-02-19 |  | 3 | 31.6 | 10.76 | 0.4 | 0.8 | 2007-02-19 |  | 1.8 | 32.3 | 10.27 | 0.3 | 0.6
2007-02-27 |  | 3.3 | 33.4 | 10.61 | 0.75 | 1.5 | 2007-02-27 |  | 1.7 | 30.3 | 10.67 | 0.5 | 1
2007-03-05 |  | 3.4 | 31.4 | 10.18 | 0.8 | 1.6 | 2007-03-05 |  | 1.8 | 25.2 | 7.24 | 0.5 | 1
2007-03-13 |  | 3.5 | 35.9 | 11.02 | 0.6 | 1.2 | 2007-03-13 |  | 2.2 | 29.8 | 10.62 | 0.5 | 1
2007-03-23 |  | 2.6 | 35.1 | 11.52 | 0.7 | 1.4 | 2007-03-23 |  | 1.5 | 35.8 | 10.3 | 1.2 | 2.4
2007-03-26 |  | 2.6 | 35.5 | 11.2 | 0.8 | 1.6 | 2007-03-26 |  | 1.8 | 29.6 | 11.73 | 0.5 | 1
2007-04-02 |  | 2.9 | 36.3 | 11.9 | 0.9 | 1.8 | 2007-04-02 |  | 2.2 | 28.7 | 10.4 | 1.1 | 2.2
2007-04-11 |  | 2.8 | 37.8 | 11.49 | 0.6 | 1.2 | 2007-04-11 |  | 2 | 31.2 | 10.89 | 0.25 | 0.5
2007-04-16 |  | 2.7 | 36.8 | 10.8 | 0.75 | 1.5 | 2007-04-16 |  | 2.2 | 33.9 | 9 | 0.6 | 1.2
2007-04-23 |  | 2.8 | 35 | 10.29 | 0.4 | 0.8 | 2007-04-23 |  | 2.2 | 30.1 | 10.28 | 0.4 | 0.8
2007-05-01 |  | 2.6 | 36.4 | 11.28 | 0.4 | 0.8 | 2007-05-01 |  | 2.2 | 37.3 | 10.86 | 0.3 | 0.6
2007-05-08 |  | 2.4 | 35.2 | 11.84 | 0.4 | 0.8 | 2007-05-08 |  | 1.1 | 28.4 | 12.4 | 0.5 | 1
2007-05-15 |  | 2.6 | 35.2 | 11.28 | 0.7 | 1.4 | 2007-05-15 |  | 1.2 | 31.6 | 11.69 | 0.6 | 1.2
2007-05-21 |  | 2.4 | 35.7 | 12.17 | 0.5 | 1 | 2007-05-21 |  | 1 | 27.3 | 10.37 | 0.25 | 0.5
2007-05-30 |  | 2.4 | 30.9 | 11.86 | 0.5 | 1 | 2007-05-30 |  | 1 | 35.9 | 11.05 | 0.5 | 1
2007-06-08 |  | 2.4 | 34.4 | 10.98 | 0.3 | 0.6 | 2007-06-08 |  | 1 | 31 | 10.95 | 0.25 | 0.5
2007-06-13 |  | 2.8 | 36.2 | 11.32 | 0.9 | 1.8 | 2007-06-13 |  | 0.95 | 29.9 | 10.42 | 0.8 | 1.6
2007-06-18 |  | 3 | 36.9 | 11.38 | 0.5 | 1 | 2007-06-18 |  | 1.3 | 37.1 | 11.53 | 0.5 | 1
2007-06-26 |  | 3.4 | 29.6 | 11.23 | 0.5 | 1 | 2007-06-26 |  | 1.6 | 36.9 | 11.72 | 0.5 | 1
2007-07-03 |  | 2.4 | 37.4 | 11.66 | 0.3 | 0.6 | 2007-07-03 |  | 1.6 | 38.1 | 11.39 | 0.5 | 1
2007-07-11 |  | 2.6 | 38.1 | 11.15 | 0.9 | 1.8 | 2007-07-11 |  | 1.4 | 30.8 | 10.66 | 1.1 | 2.2
2007-07-19 |  | 2.8 | 36.7 | 11.11 | 0.5 | 1 | 2007-07-19 |  | 1.6 | 36.2 | 11.41 | 0.4 | 0.8
2007-07-23 |  | 2.6 | 36.4 | 11.11 | 0.5 | 1 | 2007-07-23 |  | 1.6 | 35.9 | 11.18 | 0.6 | 1.2
2007-07-30 |  | 1.4-2.8 | 35.9 | 11.41 | 0.6 | 1.2 | 2004-07-30 |  | 1.7 | 37.9 | 10.45 | 0.5 | 1
2007-08-09 |  | 2.6 | 37.4 | 9.75 | 0.5 | 1 | 2007-08-09 |  | 2.2 | 38.9 | 11.6 | 0.5 | 1
2007-08-13 |  | 2.4 | 30.9 | 6.5 | 0.5 | 1 | 2007-08-13 |  | 2.1 | 37.6 | 9.65 | 0.5 | 1
2007-08-21 |  | 2.6 | 36.5 | 9.35 | 0.5 | 1 | 2007-08-21 |  | 2.4 | 36.3 | 11.3 | 1.3 | 2.6
2007-08-30 |  | 2.8 | 35.4 | 9.75 | 0.5 | 1 | 2007-08-30 |  | 2.8 | 38.3 | 10.1 | 0.5 | 1
2007-09-03 |  | 2.8 | 36.1 | 11.67 | 0.3 | 0.6 | 2007-09-03 |  | 3 | 34.2 | 10.68 | 0.6 | 1.2
2007-09-12 |  | 2.8 | 38.3 | 9.75 | 0.5 | 1 | 2007-09-12 |  | 1 | 37.9 | 9.65 | 0.25 | 0.5
2007-09-20 |  | 2.8 | 36.5 | 11 | 1 | 2 | 2007-09-20 |  | 1.4 | 31.8 | 10.65 | 0.5 | 1
2007-09-25 |  | 2.7 | 35.8 | 11.02 | 0.8 | 1.6 | 2007-09-25 |  | 1.4 | 35.5 | 11.5 | 0.9 | 1.8
2007-10-02 |  | 2.6 | 37.2 | 11.2 | 0.6 | 1.2 | 2007-10-02 |  | 1.3 | 35.3 | 11.18 | 0.5 | 1
2007-10-10 |  | 2.6 | 37.6 | 10.36 | 0.8 | 1.6 | 2007-10-10 |  | 1.05 | 31.6 | 11.46 | 0.6 | 1.2
2007-10-15 |  | 2.6 | 37.2 | 11.58 | 0.7 | 1.4 | 2007-10-15 |  | 1.2 | 37.4 | 10.96 | 0.5 | 1
2007-10-22 |  | 2.6 | 35.7 | 10.48 | 0.7 | 1.4 | 2007-10-22 |  | 1 | 34.4 | 11.68 | 0.9 | 1.8
2007-10-29 |  | 2.8 | 33.3 | 10.83 | 0.7 | 1.4 | 2007-10-29 |  | 1 | 31.4 | 10.51 | 1 | 2
2007-11-07 |  | 2.8 | 34.4 | 10.98 | 0.6 | 1.2 | 2007-11-07 |  | 1.2 | 36.7 | 11.88 | 0.7 | 1.4
2007-11-14 |  | 2.6 | 32.9 | 10.72 | 0.5 | 1 | 2007-11-14 |  | 1.2 | 34.3 | 11.42 | 1 | 2
2007-11-21 |  | 2.8 | 35.9 | 11.06 | 0.6 | 1.2 | 2007-11-21 |  | 1.3 | 28.2 | 11.88 | 0.5 | 1
2007-11-26 |  | 2.7 | 33.7 | 10.88 | 0.7 | 1.4 | 2007-11-26 |  | 1.2 | 31.5 | 10.9 | 0.6 | 1.2
2007-12-03 |  | 2.6 | 34.6 | 11.44 | 0.6 | 1.2 | 2007-12-03 |  | 1.2 | 33.6 | 12.7 | 0.5 | 1
2007-12-10 |  | 2.6 | 34.1 | 11.21 | 0.6 | 1.2 | 2007-12-10 |  | 1.3 | 33.8 | 12.42 | 0.4 | 0.8
2007-12-17 |  | 2.7 | 33.4 | 10.98 | 0.6 | 1.2 | 2007-12-17 |  | 1.3 | 31 | 11.47 | 0.5 | 1
2007-12-24 |  | 2.6 | 27.9 | 9.15 | 0.8 | 1.6 | 2007-12-24 |  | 1.2 | 32.6 | 10.4 | 0.5 | 1
2007-12-31 |  | 2.6 | 27.9 | 10.2 | 0.6 | 1.2 | 2007-12-31 |  | 1.2 | 35.4 | 10.4 | 0.5 | 1
2008-01-09 |  | 2.4 | 32.3 | 11.4 | 0.6 | 1.2 | 2008-01-09 |  | 0.63 | 30.3 | 10.8 | 0.6 | 1.2
2008-01-14 |  | 2.4 | 33.6 | 9.8 | 0.8 | 1.6 | 2008-01-14 |  | 0.63 | 31.7 | 10.6 | 0.5 | 1
2008-01-22 |  | 2.5 | 34.9 | 9.9 | 0.3 | 0.6 | 2008-01-22 |  | 0.7 | 36.2 | 11.1 | 0.6 | 1.2
2008-01-28 |  | 2.4 | 33.6 | 11.6 | 1 | 2 | 2008-01-28 |  | 0.63 | 33.9 | 11.1 | 0.8 | 1.6
2008-02-04 |  | 2.4 | 34.7 | 12.1 | 1 | 2 | 2008-02-04 |  | 0.63 | 30 | 7.85 | 0.25 | 0.5
2008-02-11 |  | 2.5 | 37.3 | 9.8 | 0.6 | 1.2 | 2008-02-11 |  | 0.63 | 37.2 | 11.8 | 0.6 | 1.2
2008-02-19 |  | 2.6 | 32.7 | 8.8 | 0.5 | 1 | 2008-02-19 |  | 0.63 | 32 | 10.9 | 0.7 | 1.4
2008-02-26 |  | 2.6 | 32.7 | 9.3 | 0.4 | 0.8 | 2008-02-26 |  | 0.63 | 33.3 | 10.6 | 0.4 | 0.8
2008-03-06 |  | 2.6 | 34.5 | 9.7 | 0.5 | 1 | 2008-03-06 |  | 0.63 | 33.4 | 9.35 | 0.6 | 1.2
2008-03-14 |  | 2.7 | 35.1 | 10.3 | 0.5 | 1 | 2008-03-14 |  | 0.63 | 36.2 | 12.5 | 0.7 | 1.4
2008-03-18 |  | 2.7 | 31.5 | 10.1 | 0.3 | 0.6 | 2008-03-18 |  | 0.8 | 32.5 | 10.8 | 0.5 | 1
2008-03-25 |  | 2.7 | 33.8 | 10.4 | 0.4 | 0.8 | 2008-03-25 |  | 0.8 | 34.2 | 11.5 | 0.5 | 1
2008-04-01 |  | 2.8 | 35.5 | 10.5 | 0.4 | 0.8 | 2008-04-01 |  | 0.8 | 36.1 | 10.8 | 0.5 | 1
2008-04-08 |  | 2.5 | 35.9 | 10.02 | 0.5 | 1 | 2008-04-08 |  | 0.63 | 34.7 | 12.02 | 0.6 | 1.2
2008-04-16 |  | 2.6 | 34.2 | 11.43 | 0.6 | 1.2 | 2008-04-16 |  | 0.8 | 31.1 | 9.5 | 0.5 | 1
2008-04-22 |  | 2.5 | 33.4 |  | 0.6 | 1.2 | 2008-04-22 |  | 1.2 | 30.6 |  | 0.7 | 1.4
2008-04-29 |  | 2.6 | 35.9 |  | 0.5 | 1 | 2008-04-29 |  | 1 | 34.8 |  | 0.5 | 1
2008-05-08 |  | 2.4 | 37.5 | 10.46 | 0.5 | 1 | 2008-05-08 |  | 1 | 38.3 | 9.82 | 0.6 | 1.2
2008-05-13 |  | 2.4 | 36.2 | 10.85 | 0.5 | 1 | 2008-05-13 |  | 1 | 37.7 | 10.1 | 0.7 | 1.4
2008-05-19 |  | 2.5 | 36.3 | 11.13 | 0.4 | 0.8 | 2008-05-19 |  | 0.7 | 37.7 | 13 | 0.4 | 0.8
2008-05-30 |  | 2.4 | 36.4 | 11.19 | 0.4 | 0.8 | 2008-05-30 |  | 0.6 | 37.4 | 12.46 | 0.6 | 1.2
2008-06-02 |  | 2.4 | 36.3 | 10.85 | 0.6 | 1.2 | 2008-06-02 |  | 0.81 | 36.7 | 10.23 | 0.7 | 1.4
2008-06-12 |  | 2.4 | 34.7 | 10.94 | 0.5 | 1 | 2008-06-12 |  | 0.63 | 36.5 | 9.99 | 0.6 | 1.2
2008-06-18 |  | 2.6 | 37 | 10.5 | 0.5 | 1 | 2008-06-18 |  | 0.9 | 36 | 11 | 0.5 | 1
2008-06-23 |  | 2.6 | 35.3 | 10.94 | 0.5 | 1 | 2008-06-23 |  | 0.82 | 37.2 | 10.44 | 0.5 | 1
2008-06-30 |  | 2.6 | 37.5 | 10.27 | 0.8 | 1.6 | 2008-06-30 |  | 0.82 | 39.3 | 9.64 | 0.7 | 1.4
2008-07-09 |  | 2.4 | 37 | 10.6 | 0.3 | 0.6 | 2008-07-09 |  | 0.8 | 38 | 10.86 | 0.4 | 0.8
2008-07-18 |  | 2.4 | 37.6 | 11.13 | 0.6 | 1.2 | 18/07/08/ |  | 0.82 | 38.4 | 11.98 | 0.6 | 1.2
2008-07-21 |  | 2.5 | 34.9 | 10.69 | 0.4 | 0.8 | 2008-07-21 |  | 0.7 | 34.2 | 8.78 | 0.4 | 0.8
2008-07-29 |  | 2.4 | 37.7 | 10.83 | 0.7 | 1.4 | 2008-07-29 |  | 0.82 | 34.9 | 11.46 | 0.5 | 1
2008-08-05 |  | 2.4 | 36.4 | 10.61 | 0.6 | 1.2 | 2008-08-05 |  | 0.82 | 32.8 | 10.32 | 0.7 | 1.4
2008-08-13 |  | 2.4 | 34.5 | 11.24 | 0.6 | 1.2 | 13/08/08 |  | 1 | 35.8 | 9.83 | 0.6 | 1.2
2008-08-18 |  | 2.6 | 34.5 | 11.21 | 0.8 | 1.6 | 2008-08-18 |  | 1.1 | 34.9 | 10.52 | 0.7 | 1.4
2008-08-18 |  | 2.6 | 34.5 | 11.21 | 0.8 | 1.6 | 2008-08-18 |  | 1.1 | 34.9 | 10.52 | 0.7 | 1.4
2008-08-29 |  | 2.7 | 40.1 | 10.68 | 0.4 | 0.8 | 2008-08-29 |  | 0.7 | 40.4 | 12.21 | 0.4 | 0.8
2008-09-01 |  | 2.6 | 36.8 | 11.39 | 0.6 | 1.2 | 2008-09-01 |  | 1 | 38.2 | 10.42 | 0.6 | 1.2
2008-09-08 |  | 2.6 | 35.5 | 11.16 | 0.6 | 1.2 | 2008-09-08 |  | 1.1 | 35.9 | 10.35 | 0.6 | 1.2
2008-09-19 |  | 2.6 | 38.8 | 11.06 | 0.6 | 1.2 | 2008-09-19 |  | 1.1 | 38.8 | 11.13 | 0.5 | 1
2008-09-26 |  | 2.5 | 37.2 | 10.17 | 0.5 | 1 | 2008-09-26 |  | 1 | 37.2 | 13.45 | 0.5 | 1
2008-10-03 |  | 2.4 | 33.6 | 11.12 | 0.3 | 0.6 | 2008-10-03 |  | 0.9 | 32.2 | 12.47 | 0.4 | 0.8
2008-10-07 |  | 2.4 | 36.6 | 10.97 | 0.7 | 1.4 | 2008-10-07 |  | 1 | 37.2 | 10.87 | 0.5 | 1
2008-10-17 |  | 2.5 | 34.5 | 10.87 | 0.6 | 1.2 | 2008-10-17 |  | 1 | 32.4 | 11.1 | 0.6 | 1.2
2008-10-21 |  | 2.5 | 34.3 | 10.86 | 0.6 | 1.2 | 2008-10-21 |  | 1.2 | 31.4 | 12.92 | 0.4 | 0.8
2008-10-31 |  | 2.2 | 34.2 | 11.56 | 0.6 | 1.2 | 2008-10-31 |  | 1 | 33.3 | 11.14 | 0.5 | 1
2008-11-04 |  | 2.6 | 35.2 | 10.96 | 0.5 | 1 | 2008-11-04 |  | 1 | 36.4 | 10.84 | 0.6 | 1.2
2008-11-11 |  | 2.6 | 33.8 | 11.17 | 0.5 | 1 | 2008-11-11 |  | 1 | 31.8 | 11.44 | 0.6 | 1.2
2008-11-19 |  | 2.7 | 35.1 | 11.09 | 0.3 | 0.6 | 2008-11-19 |  | 1.1 | 32.8 | 13.01 | 0.4 | 0.8
2008-11-25 |  | 2.7 | 34.3 | 11.45 | 0.3 | 0.6 | 2008-11-25 |  | 1 | 33.9 | 9.94 | 0.5 | 1
2008-12-03 |  | 2.6 | 32.4 | 11.33 | 0.5 | 1 | 2008-12-02 |  | 1 | 34.1 | 10.41 | 0.7 | 1.4
2008-12-12 |  | 2.8 | 27.7 | 9.74 | 0.4 | 0.8 | 2008-12-12 |  | 1 | 31.4 | 9.27 | 0.6 | 1.2
2008-12-19 |  | 2.8 | 33.2 | 10.1 | 0.3 | 0.6 | 2008-12-17 |  | 1 | 33.1 | 10.9 | 0.4 | 0.8
2008-12-22 |  | 2.9 | 34.1 | 9.2 | 1.5 | 3 | 1900-01-21 02:53 |  | 1 | 33.3 | 8.45 | 1 | 2
2008-12-30 |  | 2.4 | 32.6 | 8.95 | 0.6 | 1.2 | 2008-12-30 |  | 1 | 32.9 | 7.98 | 0.6 | 1.2
2009-01-08 |  | 2.4 | 33.6 | 9.2 | 0.5 | 1 | 2009-01-08 |  | 1 | 35 | 10.1 | 0.7 | 1.4
2009-01-16 |  | 2.5 | 32.4 | 9.75 | 0.6 | 1.2 | 2009-01-16 |  | 1 | 32.1 | 12 | 0.4 | 0.8
2009-01-21 |  | 2.6 | 32.6 | 9.55 | 0.6 | 1.2 | 2009-01-21 |  | 1 | 30.8 | 9.45 | 0.5 | 1
2009-01-26 |  | 2.4 | 32.9 | 9.5 | 0.5 | 1 | 2009-01-26 |  | 1 | 34.5 | 9.6 | 0.6 | 1.2
2009-02-02 |  | 2.6 | 29.9 | 8.6 | 0.5 | 1 | 2009-02-02 |  | 1 | 31 | 9.55 | 0.5 | 1
2009-02-10 |  | 2.6 | 32.9 | 10.69 | 0.7 | 1.4 | 2009-02-10 |  | 1 | 32.7 | 11.17 | 0.6 | 1.2
2009-02-16 |  | str shut down for week |  |  |  |  | 2009-02-16 |  | 1 | 33.8 | 10.47 | 0.5 | 1
2009-02-25 |  | 2.8 | 32.1 | 10.85 | 0.3 | 0.6 | 2009-02-25 |  | 1 | 32.3 | 12.11 | 0.3 | 0.6
2009-03-03 |  | 2.4 | 31 | 10.68 | 0.3 | 0.6 | 2009-03-03 |  | 1 | 30.6 | 12.05 | 0.6 | 1.2
2009-03-10 |  | 2.4 | 32.8 | 9.94 | 0.5 | 1 | 2009-03-10 |  | 1 | 23.6 | 9.71 | 0.3 | 0.6
2009-03-17 |  | 2.6 | 34.1 | 10.41 | 0.4 | 0.8 | 2009-03-17 |  | 1 | 33.2 | 11.08 | 0.6 | 1.2
2009-03-24 |  | 2.6 | 31.6 | 9.96 | 0.5 | 1 | 2009-03-24 |  | str shut down
2009-03-30 |  | 2.4 | 35.1 | 10.82 | 0.5 | 1 | 2009-03-30 |  | str shut down
2009-04-07 |  | 2.6 | 31.9 | 11.6 | 0.5 | 1 | 2009-04-07 |  | 1 | 37.4 | 9.53 | 0.7 | 1.4
2009-04-16 |  | str shut down |  |  |  |  | 2009-04-16 |  | 1 | 34.7 | 9.54 | 0.6 | 1.2
2009-04-21 |  | str shut down |  |  |  |  | 2009-04-21 |  | 1 | 36.7 | 11.58 | 0.8 | 1.6
2009-04-28 |  | 0 | 41.1 | 11.45 | 0.5 | 1 | 2009-04-28 |  | 1 | 33.2 | 12.29 | 0.5 | 1
2009-05-05 |  | str shut down |  |  |  |  | 2009-05-05 |  | 1.1 | 30.1 | 11.03 | 0.3 | 0.6
2009-05-11 |  | str shut down |  |  |  |  | 2009-05-11 |  | 1 | 31.7 | 11.7 | 0.8 | 1.6
2009-05-20 |  | 0 | 39.3 | 11.68 | 0.8 | 1.6 | 2009-05-20 |  | str shut down
2009-05-29 |  | str shut down |  |  |  |  | 2009-05-29 |  | 1.1 | 38.4 | 13.45 | 0.6 | 1.2
2009-06-02 |  | 2 | 38.1 | 11.27 | 0.5 | 1 | 2009-06-02 |  | 1 | 38.2 | 11.84 | 0.8 | 1.6
2009-06-09 |  | 2.6 | 38.1 | 11.54 | 0.2 | 0.4 | 2009-06-09 |  | 1.2 | 39.8 | 13.61 | 0.4 | 0.8
2009-06-19 |  | str shut down |  |  |  |  | 2009-06-19 |  | 1.1 | 36.9 | 12.67 | 0.4 | 0.8
2009-06-24 |  | str shut down |  |  |  |  | 2009-06-24 |  | 1.1 | 37.2 | 12.48 | 0.5 | 1
2009-07-01 |  | str shut down |  |  |  |  | 2009-07-01 |  | 1.2 | 38.9 | 13.37 | 0.4 | 0.8
2009-07-10 |  | 1 | 38.6 | 11.37 | 0.3 | 0.6 | 2009-07-10 |  | 1.2 | 38.5 | 10.84 | 0.4 | 0.8
2009-07-13 |  | 1 | 39.8 | 11.16 | 0.5 | 1 | 2009-07-13 |  | 1.2 | 40.9 | 12.76 | 0.8 | 1.6
2009-07-21 |  | 2.4 | 38.6 | 10.56 | 1.1 | 2.2 | 2009-07-21 |  | 1.1 | 38.7 | 11.95 | 0.9 | 1.8
2009-07-31 |  | str shut down |  |  |  |  | 2009-07-31 |  | str shut down - not run for min 12hrs
2009-08-04 |  | str shut down |  |  |  |  | 2009-08-04 |  | 1 | 39 | 12.53 | 0.7 | 1.4
2009-08-12 |  | 2.4 | 39.9 | 11.54 | 0.7 | 1.4 | 2009-08-12 |  | 1.2 | 41.3 | 11.94 | 1 | 2
2009-08-18 |  | 2.4 | 40.2 | 11.47 | 0.8 | 1.6 | 2009-08-18 |  | 1 | 41.4 | 11.73 | 0.9 | 1.8
2009-08-25 |  | 2.4 | 38.1 | 11.39 | 0.6 | 1.2 | 2009-08-25 |  | 1 | 38.1 | 11.25 | 0.6 | 1.2
2009-09-02 |  | 2.4 | 36.8 | 11.54 | 0.8 | 1.6 | 2009-09-02 |  | 1.1 | 38.4 | 12.85 | 1.1 | 2.2
2009-09-08 |  | 2.4 | 39.2 | 10.7 | 0.6 | 1.2 | 2009-09-08 |  | 1 | 38.2 | 11.88 | 0.7 | 1.4
2009-09-17 |  | 2.4 | 31.8 | 11.12 | 0.5 | 1 | 2009-09-17 |  | 1 | 38.2 | 12.62 | 0.6 | 1.2
2009-09-25 |  | 2.6 | 36.7 | 11.2 | 0.9 | 1.8 | 2009-09-25 |  | 1.2 | 39.1 | 12.86 | 1.1 | 2.2
2009-09-28 |  | 2.4 | 36.4 | 10.54 | 0.6 | 1.2 | 2009-09-28 |  | 1.2 | 37.4 | 12.45 | 0.7 | 1.4
2009-10-05 |  | 2.6 | 34.3 | 11.46 | 0.5 | 1 | 2009-10-05 |  | 1.2 | 36.3 | 11.93 | 0.4 | 0.8
2009-10-15 |  | 2.4 | 37.2 | 10.81 | 0.5 | 1 | 2009-10-15 |  | 1.2 | 32.7 | 11.42 | 1 | 2
2009-10-20 |  | 2.4 | 22.9 | 4.89 | 0.5 | 1 | 2009-10-20 |  | 1.2 | 29.9 | 11.81 | 0.8 | 1.6
2009-10-29 |  | 2.4 | 37.4 | 10.8 | 0.6 | 1.2 | 2009-10-29 |  | 1.2 | 37.7 | 12.38 | 0.6 | 1.2
2009-11-04 |  | 2.5 | 36.1 | 10.89 | 1 | 2 | 2009-11-04 |  | 1.5 | 37.2 | 13.07 | 1.1 | 2.2
2009-11-12 |  | 2.4 | 34.1 | 9.71 | 0.7 | 1.4 | 2009-11-13 |  | 1.4 | 37.1 | 11.99 | 1.1 | 2.2
2009-11-17 |  | 2.5 | 35.6 | 10.57 | 1.2 | 2.4 | 2009-11-17 |  | 1.3 | 37.8 | 13.06 | 1.2 | 2.4
2009-11-24 |  | 2.5 | 35.9 | 10.46 | 0.7 | 1.4 | 2009-11-24 |  | 1.2 | 32.9 | 10.52 | 0.8 | 1.6
2009-11-30 |  | 2.5 | 33.8 | 10.71 | 0.5 | 1 | 2009-11-30 |  | 1.2 | 32.8 | 12.03 | 0.8 | 1.6
2009-12-07 |  | 2.4 | 35 | 10.5 | 0.5 | 1 | 2009-12-07 |  | 1.2 | 35.4 | 12.2 | 0.6 | 1.2
2009-12-15 |  | 2.4 | 34.8 | 10.05 | 0.5 | 1 | 2009-12-15 |  | 1.2 | 33.8 | 12.45 | 0.6 | 1.2
2009-12-21 |  | 2.4 | 32.8 | 10.46 | 0.5 | 1 | 2009-12-21 |  | 1 | 30.7 | 11.61 | 0.7 | 1.4
2009-12-29 |  | 2.4 | 34.8 | 10.43 | 0.8 | 1.6 | 2009-12-29 |  | 1.1 | 33.9 | 9.31 | 0.6 | 1.2
2010-01-04 |  | 2.4 | 33.5 | 10.39 | 0.5 | 1 | 2010-01-04 |  | 1.2 | 24 | 11.66 | 0.5 | 1
2010-01-11 |  | 2.5 | 34 | 9.7 | 0.25 | 0.5 | 2010-01-11 |  | 1.2 | 24.9 | 10.8 | 0.5 | 1
2010-01-18 |  | 2.5 | 35.2 | 9.9 | 0.75 | 1.5 | 2010-01-18 |  | 1.2 | 237 | 10.2 | 0.5 | 1
2010-01-27 |  | 2.5 | 32.6 | 10.48 | 1 | 2 | 2010-01-27 |  | 1.2 | 34.1 | 12.66 | 0.9 | 1.8
2010-02-04 |  | 2.4 | 32 | 10.92 | 0.6 | 1.2 | 2010-02-04 |  | 1.2 | 25 | 11.27 | 0.6 | 1.2
2010-02-09 |  | 2.2 | 33.5 | 10.3 | 0.5 | 1 | 2010-02-09 |  | 1.2 | 26.3 | 11.8 | 0.6 | 1.2
2010-02-15 |  | 2.2 | 32.3 | 11.31 | 0.5 | 1 | 2010-02-15 |  | 1 | 26.7 | 11.68 | 0.6 | 1.2
2010-02-23 |  | 2.3 | 34.9 | 10.3 | 0.75 | 1.5 | 2010-02-23 |  | 2.1 | 32.3 | 10.1 | 0.6 | 1.2
2010-03-01 |  | 2.2 | 34.2 | 10.2 | 0.5 | 1 | 2010-03-01 |  | 2 | 33.7 | 10.9 | 0.5 | 1
2010-03-08 |  | 2.4 | 31.2 | 11.02 | 0.8 | 1.6 | 2010-03-08 |  | 2.2 | 29.2 | 11.06 | 0.6 | 1.2
2010-03-15 |  | 2.2 | 34.8 | 10.68 | 0.6 | 1.2 | 2010-03-15 |  | 2 | 29.7 | 10.36 | 0.5 | 1
2010-03-24 |  | 2.4 | 35.7 | 11.27 | 0.9 | 1.8 | 2010-03-25 |  | 2.2 | 34.2 | 11.75 | 0.6 | 1.2
2010-03-29 |  | 2.2 | 34.9 | 10.9 | 0.6 | 1.2 | 2010-03-29 |  | 2 | 34.4 | 12.57 | 0.6 | 1.2
2010-04-09 |  | 2.4 | 37.9 | 11.6 | 0.8 | 1.6 | 2010-04-09 |  | 2 | 36.8 | 12.1 | 1.1 | 2.2
2010-04-12 |  | 2.2 | 34.6 | 10.95 | 0.5 | 1 | 2010-04-12 |  | 2 | 35.7 | 12.85 | 1 | 2
2010-04-19 |  | 2.4 | 29.6 | 9.79 | 0.5 | 1 | 2010-04-19 |  | 2.1 | 31.8 | 12.4 | 0.7 | 1.4
2010-04-26 |  | 2.4 | 36.3 | 10.5 | 0.6 | 1.2 | 2010-04-26 |  | 2.2 | 35.3 | 11.9 | 1.1 | 2.2
2010-05-05 |  | 2.4 | 36.5 | 10.72 | 0.7 | 1.4 | 2010-05-05 |  | 2.2 | 38.2 | 12.96 | 0.9 | 1.8
2010-05-10 |  | 2.4 | 34.6 | 9.5 | 0.5 | 1 | 2010-05-10 |  | 2 | 35.2 | 11.4 | 0.75 | 1.5
2010-05-19 |  | 2.4 | 36 | 10.2 | 0.5 | 1 | 2010-05-19 |  | 2.1 | 35.3 | 11.9 | 0.7 | 1.4
2010-05-25 |  | 2.4 | 35.7 | 10.92 | 0.5 | 1 | 2010-05-25 |  | 2.2 | 34.5 | 12.89 | 0.7 | 1.4
2010-06-03 |  | 2.4 | 38.1 | 10.4 | 0.75 | 1.5 | 2010-06-03 |  | 2 | 35.4 | 7.4 | 0.25 | 0.5
2010-06-09 |  | 2.5 | 36.7 | 10.79 | 0.8 | 1.6 | 2010-06-09 |  | 2 | 35.6 | 10.89 | 0.6 | 1.2
2010-06-15 |  | 2.6 | 36.8 | 10.79 | 0.7 | 1.4 | 2010-06-15 |  | 2.2 | 37.2 | 13.36 | 0.8 | 1.6
2010-06-21 |  | 2.2 | 38.7 | 10.87 | 0.6 | 1.2 | 2010-06-21 |  | 1.8 | 32.8 | 12.29 | 0.5 | 1
2010-06-28 |  | 2.6 | 38.1 | 8.82 | 0.6 | 1.2 | 2010-06-28 |  | 2 | 35.8 | 12.44 | 0.6 | 1.2
2010-07-05 |  | 2.4 | 37.3 | 10.64 | 0.6 | 1.2 | 2010-07-05 |  | 2 | 35.3 | 12.93 | 0.6 | 1.2
2010-07-13 |  | 2.4 | 37 | 10.88 | 0.6 | 1.2 | 2010-07-13 |  | 2 | 35.8 | 12.16 | 0.7 | 1.4
2010-07-19 |  | 2.5 | 39.9 | 10.19 | 0.6 | 1.2 | 2010-07-19 |  | 2 | 39.2 | 12.44 | 1.1 | 2.2
2010-07-26 |  | 2.5 | 39.1 | 10.85 | 0.6 | 1.2 | 2010-07-26 |  | 1.9 | 37.1 | 12.12 | 0.6 | 1.2
2010-08-02 |  | 2.4 | 39.2 | 11.5 | 0.7 | 1.4 | 2010-08-02 |  | 2 | 38.4 | 12.25 | 0.6 | 1.2
2010-08-10 |  | 2.4 | 38.8 | 10.37 | 0.6 | 1.2 | 2010-08-10 |  | 2 | 34.2 | 12.56 | 1 | 2
2010-08-16 |  | 2.4 | 37.3 | 10.5 | 0.25 | 0.5 | 2010-08-16 |  | 2.2 | 35.3 | 12.2 | 0.25 | 0.5
2010-08-25 |  | 2.4 | 36.9 | 11.06 | 1 | 2 | 2010-08-25 |  | 2.1 | 36.6 | 14.3 | 0.7 | 1.4
2010-09-03 |  | 2.4 | 39 | 10.8 | 1 | 2 | 2010-09-03 |  | 2.1 | 38.6 | 13.57 | 0.9 | 1.8
2010-09-06 |  | 2.2 | 37.7 | 9.25 | 0.6 | 1.2 | 2010-09-06 |  | 2.2 | 32.8 | 12.52 | 0.6 | 1.2
2010-09-13 |  | 2.4 | 37.1 | 10.46 | 0.6 | 1.2 | 2010-09-13 |  | 2.2 | 34.4 | 12.8 | 0.5 | 1
2010-09-20 |  | 2.6 | 36.8 | 11.05 | 0.8 | 1.6 | 2010-09-20 |  | 2.4 | 35.1 | 13.31 | 0.7 | 1.4
2010-09-28 |  | 2.6 | 36.1 | 10.86 | 0.5 | 1 | 2010-09-27 |  | 2.3 | 34.3 | 13.04 | 0.6 | 1.2
2010-10-04 |  | 2.4 | 36.9 | 10.56 | 0.6 | 1.2 | 2010-10-04 |  | 2 | 35.6 | 10.98 | 0.6 | 1.2
2010-10-15 |  | 2.2 | 34.7 | 10.23 | 0.5 | 1 | 2010-10-12 |  | 1.8 | 34.8 | 13.71 | 0.6 | 1.2
2010-10-19 |  | 2.5 | 34.2 | 10.72 | 0.7 | 1.4 | 2010-10-19 |  | 1.9 | 34.5 | 12.81 | 1.1 | 2.2
2010-10-27 |  | 2.4 | 35.9 | 10.8 | 0.6 | 1.2 | 2010-10-27 |  | 1.8 | 35 | 11.2 | 0.25 | 0.5
2010-11-02 |  | 2.4 | 35.1 | 10.4 | 0.9 | 1.8 | 2010-11-02 |  | 1.8 | 34.2 | 14.25 | 1 | 2
2010-11-09 |  | 2.4 | 33.1 | 11.59 | 0.5 | 1 | 2010-11-09 |  | 1.8 | 31.9 | 13.46 | 0.5 | 1
2010-11-18 |  | 2.4 | 34.9 | 10.8 | 0.7 | 1.4 | 2010-11-18 |  | 1.8 | 27.8 | 12.81 | 0.6 | 1.2
2010-11-23 |  | 2.5 | 34.6 | 10.3 | 0.7 | 1.4 | 2010-11-23 |  | 2 | 32.7 | 11.8 | 0.8 | 1.6
2010-11-29 |  | 2.5 | 34.6 | 10.2 | 1.2 | 2.4 | 2010-11-29 |  | 1.9 | 31.9 | 12.8 | 1 | 2
2010-12-07 |  | 2.4 | 26.9 | 8.5 | 0.6 | 1.2 | 2010-12-07 |  | 1.9 | 30.7 | 13 | 0.5 | 1
2010-12-15 |  | 2.5 | 29.5 | 7.8 | 0.6 | 1.2 | 2010-12-15 |  | 2.5 | 33.3 | 12.85 | 1 | 2
2010-12-22 |  | 2.5 | 34.2 | 10.6 | 0.7 | 1.4 | 2010-12-22 |  | 2 | 29.6 | 13.6 | 0.7 | 1.4
2010-12-29 |  | 2.6 | 35.6 | 10.5 | 1.2 | 2.4 | 2010-12-29 |  | 2 | 35.7 | 13.5 | 1.1 | 2.2
2011-01-05 |  | 2.7 | 32.8 | 9.2 | 0.8 | 1.6 | 2011-01-05 |  | 2 | 32.2 | 11.8 | 1 | 2
2011-01-11 |  | 2.4 | 34.9 | 10.64 | 0.8 | 1.6 | 2011-01-11 |  | 2 | 32.3 | 13.33 | 0.8 | 1.6
2011-01-17 |  | 2.4 | 25.8 | 5.78 | 0.5 | 1 | 2011-01-17 |  | 2 | 30.3 | 11.22 | 1 | 2
2011-01-25 |  | 2.2 | 36.1 | 11.3 | 0.8 | 1.6 | 2011-01-25 |  | 1.8 | 34.2 | 15.58 | 1 | 2
2011-02-02 |  | 2.2 | 33.1 | 10.79 | 0.9 | 1.8 | 2011-02-02 |  | 1.8 | 33.4 | 13.08 | 0.8 | 1.6
2011-02-07 |  | 2.2 | 33.3 | 10.92 | 0.5 | 1 | 2011-02-07 |  | 1.8 | 32.1 | 13.56 | 1 | 2
2011-02-15 |  | 2.4 | 33.6 | 11.27 | 0.8 | 1.6 | 2011-02-15 |  | 1.8 | 33.7 | 12.57 | 0.7 | 1.4
2011-02-22 |  | 2.4 | 31 | 11.11 | 0.6 | 1.2 | 2011-02-22 |  | 1.9 | 30 | 13.59 | 0.6 | 1.2
2011-03-02 |  | 2.4 | 33 | 9.79 | 1.1 | 2.2 | 2011-03-02 |  | 1.8 | 32 | 12.66 | 1 | 2
2011-03-07 |  | 2.4 | 35.2 | 11.13 | 0.7 | 1.4 | 2011-03-07 |  | 1.8 | 33.4 | 12.28 | 0.6 | 1.2
2011-03-17 |  | 2.4 | 33 | 11 | 0.5 | 1 | 2011-03-17 |  | 1.8 | 32 | 13.21 | 0.5 | 1
2011-03-22 |  | 2.6 | 31 | 7.21 | 1 | 2 | 2011-03-22 |  | 1.8 | 36 | 15.31 | 1.1 | 2.2
2011-03-29 |  | 2.6 | 34 | 11.43 | 0.9 | 1.8 | 2011-03-29 |  | 1.8 | 32 | 13.52 | 1.1 | 2.2
2011-04-04 |  | 2.4 | 34.2 | 10.76 | 0.7 | 1.4 | 2011-04-04 |  | 1.8 | 33.2 | 13.37 | 0.7 | 1.4
2011-04-11 |  | 2 | 34 | 10.5 | 1 | 2 | 2011-04-11 |  | 1.6 | 35 | 13.1 | 1 | 2
2011-04-22 |  | 2.4 | 32.6 | 10.74 | 0.8 | 1.6 | 2011-04-22 |  | 1.8 | 28.5 | 13.22 | 0.6 | 1.2
2011-04-26 |  | 2.4 | 32.4 | 10.67 | 0.8 | 1.6 | 2011-04-26 |  | 1.8 | 29.1 | 13.12 | 0.7 | 1.4
2011-05-04 |  | 2.6 | 30.7 | 9.45 | 0.5 | 1 | 2011-05-04 |  | 1.8 | 35.4 | 13.68 | 0.7 | 1.4
2011-05-12 |  | 2.4 | 31.8 | 10.61 | 0.6 | 1.2 | 2011-05-12 |  | 1.8 | 33.2 | 12.11 | 0.6 | 1.2
2011-05-17 |  | 2.4 | 36.6 | 10.47 | 0.5 | 1 | 2011-05-17 |  | 1.8 | 34.3 | 13.59 | 0.7 | 1.4
2011-05-24 |  | 2.4 | 34.6 | 11.44 | 0.7 | 1.4 | 2011-05-24 |  | 1.8 | 26.5 | 15.18 | 0.8 | 1.6
2011-06-01 |  | 2.6 | 36.9 | 10.25 | 1.3 | 2.6 | 2011-06-01 |  | 1.8 | 34.2 | 12.8 | 1 | 2
2011-06-06 |  | 2.6 | 38 | 10.8 | 1.5 | 3 | 2011-06-06 |  | 1.8 | 37 | 13.3 | 1.2 | 2.4
2011-06-14 |  | 2.6 | 36.6 | 6.18 | 0.8 | 1.6 | 2011-06-14 |  | 1.8 | 38 | 12.2 | 1.2 | 2.4
2011-06-20 |  | 2.6 | 38.6 | 9.6 | 1 | 2 | 2011-06-20 |  | 1.8 | 39.5 | 10 | 1.5 | 3
2011-06-27 |  | 2.6 | 40.7 | 10 | 0.8 | 1.6 | 2011-06-27 |  | 1.8 | 38.8 | 5.8 | 0.9 | 1.8
2011-07-04 |  | 2.6 | 36 | 11.4 | 0.8 | 1.6 | 2011-07-04 |  | 1.8 | 37 | 6 | 1.8 | 3.6
2011-07-12 |  | 2.2 | 37.3 | 8.9 | 0.9 | 1.8 | 2011-07-11 |  | 1.8 | 39.2 | 7.5 | 1.7 | 3.4
2011-07-18 |  | 2.2 | 35.8 | 9.1 | 0.9 | 1.8 | 2011-07-18 |  | 1.8 | 36.2 | 7.2 | 1.6 | 3.2
2011-07-25 |  | 2.4 | 37 | 9.5 | 0.8 | 1.6 | 2011-07-25 |  | 1.8 | 38.4 | 8.6 | 1.8 | 3.6
2011-08-01 |  | 2.4 | 38.6 | 10.12 | 0.7 | 1.4 | 2011-08-01 |  | 1.8 | 40.8 | 8.36 | 0.9 | 1.8
2011-08-16 |  | 2.2 | 34.4 | 10.8 | 0.8 | 1.6 | 2011-08-17 |  | 1.8 | 33.9 | 8.65 | 1 | 2
2011-08-22 |  | 2.4 | 36.7 | 7.25 | 0.8 | 1.6 | 2011-08-22 |  | 1.8 | 39.9 | 10.65 | 0.8 | 1.6
2011-08-30 |  | 2.4 | 35.4 | 9.71 | 0.7 | 1.4 | 2011-08-30 |  | 1.8 | 36.2 | 10.95 | 0.9 | 1.8
2011-09-05 |  | 2.4 | 30.3 | 10.21 | 0.8 | 1.6 | 2011-09-05 |  | 1.8 | 36.2 | 11.8 | 0.8 | 1.6
2011-09-12 |  | 2.6 | 35.8 | 8.3 | 0.9 | 1.8 | 2011-09-12 |  | 1.8 | 34.4 | 9.3 | 0.7 | 1.4
2011-09-19 |  | 2.6 | 32.8 | 10.06 | 0.8 | 1.6 | 2011-09-19 |  | 1.9 | 30.8 | 8.86 | 0.7 | 1.4
2011-09-26 |  | 2.6 | 36.8 | 10.25 | 0.7 | 1.4 | 2011-09-26 |  | 1.8 | 36.3 | 11.2 | 0.7 | 1.4
2011-10-03 |  | 2.4 | 36.7 | 10.55 | 0.9 | 1.8 | 2011-10-26 |  | 1.8 | 36.3 | 11.89 | 0.8 | 1.6
2011-10-10 |  | 2.4 | 35.8 | 10.09 | 0.7 | 1.4 | 2011-10-10 |  | 1.8 | 35.6 | 12.35 | 0.8 | 1.6
2011-10-17 |  | 2.4 | 34.4 | 9.62 | 0.8 | 1.6 | 2011-10-17 |  | 1.8 | 34.6 | 12.44 | 0.7 | 1.4
2011-10-25 |  | 2.4 | 35.7 | 11.32 | 0.9 | 1.8 | 2011-10-25 |  | 1.8 | 34.9 | 12.61 | ..0.8 | 1.6
2011-11-01 |  | 2.4 | 34.5 | 10.84 | 0.9 | 1.8 | 2011-11-01 |  | 1.8 | 35.3 | 12.18 | 0.5 | 1
2011-11-07 |  | 2.4 | 33.6 | 10.81 | 0.8 | 1.6 | 2011-11-07 |  | 1.8 | 35 | 12.17 | 0.7 | 1.4
2011-11-14 |  | 2.4 | 32.4 | 10.59 | 0.6 | 1.2 | 2011-11-14 |  | 1.8 | 33.3 | 12.99 | 0.6 | 1.2
2011-11-21 |  | 1.8 | 31.8 | 10.92 | 0.6 | 1.2 | 2011-11-21 |  | 1.8 | 34.7 | 12.43 | 0.6 | 1.2
2011-11-28 |  | 2.4 | 32.1 | 10.83 | 0.8 | 1.6 | 2011-11-28 |  | 1.8 | 33.1 | 11.81 | 0.8 | 1.6
2011-12-05 |  | 2.4 | 31.2 | 10.23 | 0.6 | 1.2 | 2011-12-05 |  | 1.8 | 28.3 | 12.1 | 0.6 | 1.2
2011-12-12 |  | 2.4 | 31.9 | 10.93 | 1 | 2 | 2011-12-12 |  | 1.8 | 31.5 | 11.81 | 0.7 | 1.4
2011-12-19 |  | 2.4 | 32.4 | 10..83 | 0.9 | 1.8 | 2011-12-19 |  | 1.8 | 33.8 | 12.8 | 0.7 | 1.4
2011-12-28 |  | 2.4 | 28.6 | 9.38 | 0.5 | 1 | 2011-12-28 |  | 1.8 | 30.7 | 11.51 | 0.7 | 1.4
2012-01-03 |  | 2.5 | 31.9 | 10.91 | 0.6 | 1.2 | 2012-01-03 |  | 1.9 | 32.1 | 12.62 | 0.6 | 1.2
2012-01-09 |  | 2.4 | 33.5 | 11.01 | 0.8 | 1.6 | 2012-01-09 |  | 1.8 | 28 | 7.71 | 0.4 | 0.8
2012-01-16 |  | 2.4 | 31.8 | 10.8 | 0.7 | 1.4 | 2012-01-16 |  | 1.8 | 33.2 | 10.43 | 0.6 | 1.2
2012-01-23 |  | 2.4 | 31.6 | 9.63 | 0.6 | 1.2 | 2012-01-23 |  | 1.8 | 32 | 11.77 | 0.4 | 0.8
2012-01-30 |  | 2.4 | 32.8 | 10.01 | 0.8 | 1.6 | 2012-01-30 |  | 1.8 | 22 | 8.82 | 0.5 | 1
2012-02-06 | 14:45 | 2.4 | 27.9 | 9.56 | 0.6 | 1.2 | 2012-02-06 | 1415 hrs | 1.8 | 32.3 | 10.72 | 0.5 | 1
2012-02-13 | 14:45 | 2.2 | 33.3 | 11.1 | 0.7 | 1.4 | 2012-02-13 | 1445 hrs | 1.7 | 33.2 | 11.28 | 0.5 | 1
2012-02-20 | 15:00 | 2.4 | 32.8 | 9.15 | 0.7 | 1.4 | 2012-02-20 | 1500 hrs | 1.8 | 31.1 | 11 | 0.5 | 1
2012-02-27 | 14:45 | 2.4 | 33.7 | 8.45 | 0.6 | 1.2 | 2012-02-27 | 1445 hrs | 1.8 | 32.6 | 12 | 0.5 | 1
2012-03-06 | 11:45 | 2.4 | 31.4 | 9.8 | 0.8 | 1.6 | 2012-03-06 | 1145 hrs | 1.8 | 29.1 | 9.1 | 0.3 | 0.6
2012-03-13 | 10:00 | 2.1 | 33.2 | 9.85 | 0.8 | 1.6 | 2012-03-13 | 1000 hrs | 1.6 | 34.2 | 11.4 | 0.6 | 1.2
2012-03-19 | 14:45 | 2.4 | 33.3 | 9.65 | 1.2 | 2.4 | 2012-03-19 | 1445 hrs | 1.8 | 32.9 | 12.9 | 0.5 | 1
2012-03-27 | 12:15 | 2.4 | 36.7 | 10.7 | 1 | 2 | 2012-03-27 | 1215 hrs | 1.9 | 37.1 | 12.8 | 0.7 | 1.4
2012-04-02 | 13:45 | 2.4 | 34.4 | 10.2 | 0.8 | 1.6 | 2012-04-02 | 1345 hrs | 1.8 | 30 | 10 | 0.4 | 0.8
2012-04-10 | 11:45 | 2.4 | 33.2 | 10.1 | 0.8 | 1.6 | 2012-04-10 | 1145 hrs | 2 | 32.2 | 10.5 | 0.5 | 1
2012-04-16 | 13:45 | 1.8 | 35.3 | 10.5 | 0.8 | 1.6 | 2012-04-16 | 1345 hrs | 1.8 |  |  |  | 0
2012-04-23 | 14:00 | 2.4 | 33.4 | 9.75 | 0.6 | 1.2 | 2012-04-23 | 1400 hrs | 2 | 32.9 | 11.4 | 0.8 | 1.6
2012-04-30 | 14:30 | 2.6 | 34.6 | 10.2 | 1 | 2 | 2012-05-02 | 8:35 | 2 | 34.2 | 11.4 | 1.4 | 2.8
2012-05-08 | 11:25 | 2.6 | 36.8 | 10.3 | 1.5 | 3 | 2012-05-08 | 11:25 | 2 | 37.1 | 11.4 | 1.5 | 3
2012-05-14 | 9:30 | 2.5 | 35.4 | 9.7 | 0.9 | 1.8 | 2012-05-14 | 9:30 | 2 | 36.2 | 11.3 | 1.4 | 2.8
2012-05-21 | 15:15 | 2.5 | 35.7 | 11.4 | 0.75 | 1.5 | 2012-05-21 | 15:15 | 2 | 34.5 | 10.7 | 0.25 | 0.5
2012-05-30 | 16:30 | 2.5 | 36.7 | 10.9 | 0.8 | 1.6 | 2012-05-30 | 16:30 | 2 | 36.7 | 13.2 | 0.6 | 1.2
2012-06-06 | 11:35 | 2.5 | 34.9 | 11.5 | 1.3 | 2.6 | 2011-06-06 | 11:35 | 1.9 | 37.5 | 11.6 | 1.4 | 2.8
2012-06-11 | 13:15 | 2.5 | 36.2 | 11.31 | 0.6 | 1.2 | 2012-06-11 | 13:15 | 1.9 | 35.8 | 9.71 | 0.7 | 1.4
2012-06-18 | 11:30 | 2.4 | 35.1 | 10.8 | 0.9 | 1.8 | 2012-06-18 | 11:30 | 2 | 35.4 | 11.2 | 1.3 | 2.6
2012-06-25 | 14:25 | 2.6 | 36.1 | 11.2 | 0.8 | 1.6 | 2012-06-25 | 14:25 | 2 | 36.3 | 11.3 | 1.2 | 2.4
2012-07-02 | 11:20 | 2.6 | 35.4 | 10.8 | 0.7 | 1.4 | 2012-07-02 | 11:20 | 2 | 35.2 | 11 | 1.1 | 2.2
2012-07-09 | 11:10 | 2.6 | 36.2 | 10.3 | 0.9 | 1.8 | 2012-07-09 | 11:10 | 1.9 | 37.3 | 10.3 | 1 | 2
2012-07-16 | 11:10 | 2.5 | 35.3 | 9.7 | 0.8 | 1.6 | 2012-07-16 | 11:10 | 2 | 36.4 | 11.3 | 1.2 | 2.4
2012-07-23 | 10:50 | 2.5 | 38.4 | 10.1 | 0.8 | 1.6 | 2012-07-23 | 10:50 | 2 | 39.8 | 10.5 | 1.2 | 2.4
2012-07-30 | 10:55 | 2.5 | 35.7 | 11 | 0.8 | 1.6 | 2012-07-30 | 253:12 | 2 | 36.8 | 11.1 | 1 | 2
2012-08-06 | 10:35 | 2.5 | 36.3 | 10.1 | 0.8 | 1.6 | 2012-08-06 | 10:35 | 2 | 39.2 | 11.1 | 1.2 | 2.4
2012-08-13 | 15:45 | 2.2 | 37.4 | 10.66 | 0.8 | 1.6 | 2012-08-13 | 15:45 | 1.8 | 31.2 | 10.27 | 0.5 | 1
2012-08-13 | 10:45 | 2.4 | 36.6 | 9.9 | 1.1 | 2.2 | 2012-08-13 | 10:45 | 2 | 38.4 | 9.6 | 1.3 | 2.6
2012-08-28 | 11:10 | 2.4 | 36 | 9.8 | 0.8 | 1.6 | 2012-08-28 | 11:10 | 2 | 34.9 | 10.7 | 1 | 2
2012-09-03 | 10:35 | 2.4 | 37.1 | 10.8 | 1.1 | 2.2 | 2012-09-03 | 248:24 | 2 | 37.3 | 11.5 | 1.2 | 2.4
2012-09-10 | 13:40 | 2.2 | 37.4 | 11.06 | 0.75 | 1.5 | 2012-09-10 | 13:40 | 2 | 37.3 | 7.8 | 0.5 | 1
2012-09-17 | 15:40 | 2.2 | 36.8 | 10.61 | 0.5 | 1 | 2012-09-17 | 15:40 | 2 | 35.7 | 8.79 | 0.8 | 1.6
2012-09-24 | 11:00 | 2.4 | 34.4 | 11.6 | 0.7 | 1.4 | 2012-09-24 | 11:00 | 2 | 35.6 | 10.9 | 1.2 | 2.4
2012-10-01 | 10:50 | 2.4 | 34.4 | 10.6 | 0.9 | 1.8 | 2012-10-01 | 10:50 | 2 | 37.6 | 11.3 | 1.2 | 2.4
2012-10-08 | 9:45 | 1.8 | 35.9 | 11.8 | 0.8 | 1.6 | 2012-10-08 | 9:45 | 1.2 | 36.1 | 11.4 | 1.2 | 2.4
2012-10-15 | 9:00 | 2.2 | 27.4 | 11.4 | 0.6 | 1.2 | 2012-10-15 | 9:35 | 1.8 | 32.1 | 11.5 | 1.2 | 2.4
2012-10-22 | 9:50 | 2.4 | 25.3 | 10.7 | 0.7 | 1.4 | 2012-10-22 | 9:50 | 1.9 | 30.8 | 11.3 | 1 | 2
2012-10-29 | 14:15 | 2.4 | 30.3 | 10.9 | 0.7 | 1.4 | 2012-10-29 | 14:15 | 1.9 | 30.9 | 11 | 1.3 | 2.6
2012-11-05 | 13:10 | 2.5 | 23.4 | 11.4 | 0.7 | 1.4 | 2012-11-05 | 13:10 | 1.9 | 28.4 | 10.7 | 1.1 | 2.2
2012-11-12 | 14:30 | 2.4 | 29.4 | 10.3 | 0.8 | 1.6 | 2012-11-12 | 14:30 | 1.9 | 30.1 | 11.6 | 1 | 2
2012-11-19 | 14:10 | 2.5 | 24.8 | 11.1 | 0.7 | 1.4 | 2012-11-19 | 14:10 | 1.9 | 28.4 | 11.3 | 0.9 | 1.8
2012-11-26 | 10:40 | 2.5 | 30.4 | 11.6 | 0.8 | 1.6 | 2012-11-26 | 10:40 | 1.9 | 32.1 | 11 | 1 | 2
2012-12-03 | 9:00 | 0 | 27.6 | 11.3 | 0.6 | 1.2 | 2012-12-03 | 9:00 | 0 | 29.4 | 11.1 | 1.2 | 2.4
2012-12-10 | 10:10 | 2.4 | 25.7 | 10.1 | 0.7 | 1.4 | 2012-12-10 | 10:10 | 1.2 | 2.4 | 11.9 | 1.2 | 2.4
2012-12-17 | 9:20 | 2.4 | 32.4 | 11.55 | 0.5 | 1 | 2012-12-17 | 9:20 | 1.8 | 30.3 | 10.34 | 0.4 | 0.8
2012-12-24 | 8:00 | 2.6 | 32.7 | 10.46 | 0.3 | 0.6 | 2012-12-24 | 8:00 | 1.8 | 33.2 | 10.62 | 0.6 | 1.2
2012-12-31 | 11:10 | 2.4 | 30.2 | 9.4 | 1 | 2 | 2012-12-31 | 11:10 | 2 | 31.2 | 9.7 | 1.2 | 2.4
2012-01-07 | 9:30 | 2.4 | 34.2 | 10.5 | 0.5 | 1 | 2013-01-07 | 9:30 | 2 | 35.4 | 11.2 | 0.6 | 1.2
2013-01-14 | 8:55 | 2.4 | 31.6 | 9.8 | 0.9 | 1.8 | 2013-01-14 | 8:55 | 1.9 | 32.2 | 10.8 | 0.9 | 1.8
2013-01-21 | 9:10 | 2.3 | 30.3 | 10.3 | 0.6 | 1.2 | 2013-01-21 | 9:10 | 1.8 | 29.7 | 10.3 | 0.7 | 1.4
2013-01-28 | 9:00 | 2.4 | 33 | 9.6 | 0.7 | 1.4 | 2013-01-28 | 9:00 | 1.9 | 32.7 | 10.3 | 1 | 2
2013-02-04 | 9:15 | 2.4 | 31.6 | 10.7 | 0.25 | 0.5 | 2013-02-04 | 9:15 | 1.8 | 31.5 | 10 | 1 | 2
2013-02-11 | 9:45 | 2.4 | 31.6 | 10.2 | 0.8 | 1.6 | 2013-07-11 | 9:45 | 1.8 | 32.1 | 11.2 | 0.9 | 1.8
2013-02-18 | 9:05 | 2.4 | 31.4 | 10.7 | 0.6 | 1.2 | 2013-02-18 | 9:05 | 1.9 | 32.5 | 9 | 0.9 | 1.8
2013-02-25 | 13:30 | 2.4 | 31.8 | 10.4 | 0.5 | 1 | 2013-02-25 | 13:30 | 1.8 | 33 | 10.8 | 0.75 | 1.5
2013-03-04 | 11:15 | 2.4 | 31.7 | 9.8 | 0.8 | 1.6 | 2013-03-04 | 11:15 | 1.9 | 32.6 | 11.1 | 1.1 | 2.2
2013-03-11 | 14:00 | 2.4 | 29.4 | 9.7 | 0.7 | 1.4 | 2013-03-11 | 14:00 | 1.9 | 31 | 9 | 1 | 2
2013-03-18 | 15:45 | 2.4 | 32.3 | 10.3 | 0.7 | 1.4 | 2013-03-18 | 15:45 | 1.8 | 31.6 | 9.9 | 0.8 | 1.6
2013-03-25 | 14:50 | 2.4 | 31 | 9.9 | 0.75 | 1.5 | 2013-03-25 | 14:50 | 1.9 | 32.4 | 10.2 | 0.75 | 1.5
2013-04-02 | 10:15 | 2.4 | 32.3 | 9.6 | 0.7 | 1.4 | 2013-04-02 | 10:15 | 1.9 | 29.1 | 10.1 | 0.9 | 1.8
2013-04-08 | 11:45 | 2.4 | 32.8 | 9.4 | 0.7 | 1.4 | 2013-04-09 | 13:20 | 2.1 | 33 | 9.4 | 1.2 | 2.4
2013-04-15 | 10:45 | 2.4 | 34.2 | 9.6 | 0.7 | 1.4 | 2013-04-15 | 10:45 | 2 | 34.5 | 9.8 | 0.9 | 1.8
2013-04-22 | 11:00 | 2.4 | 33.2 | 8.4 | 0.8 | 1.6 | 2013-04-22 | 11:00 | 2 | 30.2 | 8.6 | 0.6 | 1.2
2013-04-29 | 15:30 | 2.4 | 34.8 | 8.8 | 0.7 | 1.4 | 2013-04-29 | 15:30 | 2 | 29.8 | 10.4 | 0.8 | 1.6
2013-05-07 | 9:50 | 2.5 | 35.6 | 10.9 | 0.6 | 1.2 | 2013-05-07 | 9:50 | 2 | 36.2 | 10.8 | 0.8 | 1.6
2013-05-13 | 11:50 | 2.5 | 32.7 | 9.5 | 0.6 | 1.2 | 2013-05-13 | 11:50 | 2 | 33.4 | 9.8 | 0.9 | 1.8
2013-05-20 | 14:30 | 2.5 | 35.2 | 9.8 | 0.7 | 1.4 | 2013-05-20 | 14:30 | 2 | 34.4 | 8.8 | 0.9 | 1.8
2013-05-28 | 9:20 | 2.6 | 35.4 | 11.2 | 0.6 | 1.2 | 2013-05-28 | 9:20 | 2 | 36.1 | 11.3 | 0.8 | 1.6
2013-06-03 | 15:30 | 2.4 | 35.4 | 10.6 | 0.6 | 1.2 | 2013-06-03 | 15:30 | 2 | 36.7 | 11 | 0.8 | 1.6
2013-06-10 | 11:15 | 2.5 | 33.7 | 9.8 | 0.7 | 1.4 | 2013-06-10 | 11:15 | 2 | 31.2 | 10 | 0.6 | 1.2
2013-06-17 | 14:35 | 2.5 | 35.6 | 10.3 | 0.8 | 1.6 | 2013-06-17 | 14:35 | 1.9 | 36.7 | 10.4 | 1.1 | 2.2
2013-06-24 | 13:30 | 2.4 | 35.2 | 10.9 | 0.7 | 1.4 | 2013-06-24 | 13:30 | 1.9 | 36.9 | 10.8 | 0.8 | 1.6
2013-07-01 | 9:40 | 2.5 | 35.9 | 10.1 | 0.5 | 1 | 2013-07-01 | 9:40 | 2 | 37.7 | 0.44444 | 0.8 | 1.6
2013-07-08 | 15:20 | 2.4 | 36.3 | 10.3 | 0.5 | 1 | 2013-07-08 | 15:20 | 1.9 | 34.4 | 10.2 | 0.5 | 1
2013-07-15 | 15:40 | 2.4 | 37.9 | 10.1 | 0.7 | 1.4 | 2013-07-15 | 15:40 | 1.8 | 39.2 | 10.3 | 0.9 | 1.8
2013-07-22 | 11:25 | 2.3 | 35.8 | 9.4 | 0.7 | 1.4 | 2013-07-22 | 11:25 | 1.9 | 36.7 | 9.5 | 0.8 | 1.6
2013-07-29 | 14:15 | 2.4 | 36.9 | 10.2 | 0.5 | 1 | 2013-07-29 | 14:15 | 1.8 | 38.1 | 10.4 | 0.7 | 1.4
2013-08-09 | 11:50 | 2.4 | 36.1 | 9.8 | 0.8 | 1.6 | 2013-08-05 | [5 empty] | 0
2013-08-13 | 8:40 | 2.5 | 34.4 | 10.8 | 0.8 | 1.6 | 2013-08-13 | 8:40 | 1.9 | 35.4 | 9.9 | 0.7 | 1.4
2013-08-19 | 15:15 | 2.5 | 35.5 | 9.2 | 0.7 | 1.4 | 2013-08-19 | 15:15 | 2 | 37.5 | 10.6 | 0.9 | 1.8
2013-08-27 | 9:50 | 2.6 | 38.2 | 8.5 | 0.9 | 1.8 | 2013-08-27 | 9:50 | 1.9 | 39.2 | 9.5 | 1.1 | 2.2
2013-09-06 | 14:00 | [5 empty] | 2013-09-02 | 14:30 | 2 | 39.8 | 10.2 | 1.1 | 2.2
2013-09-09 | 9:30 | 2.5 |  |  |  |  | 2013-09-09 | 9:30 | 1.9 | 33.4 | 9.7 | 0.5 | 1
2013-09-16 | 11:45 | 2.5 | 33.1 | 9 | 0.8 | 1.6 | 2013-09-16 | 9:35 | 1.9 | 37.4 | 9.7 | 1.1 | 2.2
2013-09-23 | 11:45 | 2.4 | 37.1 | 8.7 | 1.3 | 2.6 | 2013-09-23 | 11:45 | 1.9 | 41.4 | 9.4 | 1.2 | 2.4
2013-09-30 | 15:00 | 2.3 | 36.8 | 10 | 0.75 | 1.5 | 2013-09-29 | 15:00 | 1.9 | 37.3 | 9.9 | 0.75 | 1.5
2013-10-08 | 7:45 | 2.4 | 34.9 | 8.8 | 1.1 | 2.2 | 2013-10-07 | 7:45 | 1.9 | 39.6 | 9.8 | 1.1 | 2.2
2013-10-14 | 9:05 | 2.4 | 35.1 | 9.8 | 1 | 2 | 2013-10-14 | 9:05 | 1.9 | 35.4 | 10.1 | 1.1 | 2.2
2013-10-21 | 8:50 | 2.5 | 35.8 | 9.8 | 1.2 | 2.4 | 2013-10-21 | 8:50 | 1.8 | 36.3 | 10.7 | 1.1 | 2.2
2013-10-28 | 9:00 | 2.4 | 33.4 | 11.1 | 0.8 | 1.6 | 2013-10-28 | 9:00 | 1.9 | 33.7 | 10.4 | 1.1 | 2.2
2013-11-04 | 10:50 | 2.4 | 34.3 | 11.16 | 0.4 | 0.8 | 2013-11-04 | 10:50 | 2 | 35.8 | 10.04 | 0.25 | 0.5
2013-11-11 | 13:00 | 2.4 | 29.8 | 9.56 | 0.8 | 1.6 | 2013-11-11 | 13:00 | 1.8 | 32.6 | 11.56 | 1.5 | 3
2013-11-19 | 16:00 | 2.5 | 32.9 | 10.92 | 0.6 | 1.2 | 2013-11-19 | 16:00 | 1.9 | 34.1 | 11.65 | 0.5 | 1
2013-11-25 | 7:12 | 2.4 | 34.6 | 10.5 | 0.8 | 1.6 | 2013-11-25 | 14.;30 | 1.9 | 34.3 | 8.75 | 0.5 | 1
2013-12-02 | 15:30 | 2.4 | 30.1 | 9.75 | 0.75 | 1.5 | 2013-12-02 | 15:30 | 1.8 | 33.4 | 11.8 | 0.5 | 1
2013-12-09 | 15:30 | 2.4 | 32.6 | 10.75 | 0.5 | 1 | 2013-12-09 | 15:30 | 1.8 | 34.2 | 11.5 | 0.5 | 1
2013-12-17 | 9:30 | 2.4 | 34.6 | 10.7 | 0.7 | 1.4 | 2013-12-17 | 9:30 | 1.8 | 32.7 | 11.39 | 0.6 | 1.2
2013-12-23 | 9:30 | 2.4 | 33.4 | 10.53 | 0.6 | 1.2 | 2013-12-23 | 9:30 | 1.8 | 33.7 | 11.84 | 1.4 | 2.8
2013-12-30 | 7:30 | 2.4 | 33.4 | 11.44 | 0.6 | 1.2 | 2013-12-30 | 7:30 | 1.8 | 35.1 | 10.78 | 0.5 | 1
2014-01-06 | 7:12 | 2.4 | 34 | 10.53 | 0.5 | 1 | 2014-01-06 | 271:12 | 1.8 | 30.4 | 11.81 | 0.7 | 1.4
2014-01-13 | 16:00 | 2.5 | 34.9 | 10.44 | 0.9 | 1.8 | 2014-01-13 | 16:00 | 1.8 | 30.7 | 11.45 | 0.5 | 1
2014-01-20 | 14:30 | 2.4 | 34.2 | 11.61 | 0.8 | 1.6 | 2014-01-20 | 14:30 | 1.8 | 30.6 | 7.36 | 0.5 | 1
2014-01-27 | 9:40 | 2.4 | 30.7 | 10.68 | 0.7 | 1.4 | 2014-01-27 | 9:40 | 1.9 | 29.4 | 10.64 | 1 | 2
2014-02-03 | 9:30 | 2.4 | 33.3 | 11.16 | 0.7 | 1.4 | 2014-02-03 | 9:30 | 1.95 | 34.8 | 11.74 | 1.1 | 2.2
2014-02-10 | 11:45 | 2.4 | 35.6 | 9.8 | 0.7 | 1.4 | 2014-02-10 | 11:45 | 1.8 | 38.1 | 11.35 | 0.7 | 1.4
2014-02-17 | 9:30 | 2.4 | 33.6 | 10.15 | 0.7 | 1.4 | 2014-02-17 | 9:30 | 18 | 36 | 11.4 | 0.7 | 1.4
2014-02-24 | 9:35 | 2.4 | 34.6 | 10.53 | 0.7 | 1.4 | 2014-02-24 | 9:35 | 1.95 | 35.6 | 10.98 | 0.8 | 1.6
2014-03-03 | 8:30 | 2.4 | 36.3 | 11.02 | 0.6 | 1.2 | 2014-03-03 | 8:30 | 1.9 | 36.7 | 10.36 | 0.7 | 1.4
2014-03-10 | 8:45 | 2.4 | 36.3 | 10.77 | 0.8 | 1.6 | 2014-03-10 | 8:45 | 1.9 | 35.6 | 10.92 | 0.9 | 1.8
2014-03-17 | 15:05 | 2.4 | 34.7 | 10.75 | 0.75 | 1.5 | 2014-03-17 | 15:05 | 1.9 | 35.5 | 11 | 0.75 | 1.5
2014-03-24 | 15:30 | 2.6 | 36.4 | 9.94 | 1 | 2 | 2014-03-24 | 15:30 | 1.8 | 36.7 | 11.88 | 0.9 | 1.8
2014-03-31 | 13:00 | 2.6 | 38.6 | 10.16 | 0.8 | 1.6 | 2014-03-31 | 13:00 | 1.9 | 39.5 | 11.16 | 0.8 | 1.6
2014-04-07 | 8:30 | 2.6 | 36 | 10.27 | 0.8 | 1.6 | 2014-04-07 | 8:30 | 1.95 | 36.6 | 11.93 | 1 | 2
2014-04-14 | 8:00 | 2.6 | 35.4 | 11.04 | 0.7 | 1.4 | 2014-04-14 | 8:00 | 2 | 36.1 | 12.14 | 1 | 2
2014-04-25 | 9:45 | 2.8 | 32.4 | 9.9 | 1.2 | 2.4 | 2014-04-22 | 11:30 | 2 | 37.6 | 10.37 | 1.4 | 2.8
2014-04-28 | 9:15 | 2.8 | 34.8 | 8.9 | 1.2 | 2.4 | 2014-04-28 | 9:15 | 2 | 38.8 | 9.82 | 1.3 | 2.6
2014-05-06 | 9:00 | 2.6 | 37.1 | 9.75 | 1 | 2 | 2014-05-06 | 9:00 | 2 | 37.6 | 9.4 | 1.2 | 2.4
2014-05-12 | 9:20 | 2.6 | 35.9 | 10.23 | 1 | 2 | 2014-05-12 | 9:20 | 2 | 36.6 | 11.2 | 1.2 | 2.4
2014-05-20 | 9:30 | 2.6 | 36.9 | 10.74 | 1 | 2 | 2014-05-22 | 15:30 | 2 | 35.8 | 11.5 | 1.1 | 2.2
2014-05-27 | 11:40 | 2.6 | 35.4 | 9.9 | 0.9 | 1.8 | 2014-05-27 | 11:45 | 1.8 | 35.3 | 10.7 | 0.8 | 1.6
2014-06-02 | 14:00 | 2.6 | 39.2 | 11.8 | 1.2 | 2.4 | 2014-06-02 | 14:00 | 2 | 38.6 | 10.25 | 1.1 | 2.2
2014-06-09 | 9:00 | 2.4 | 38.4 | 11.65 | 1 | 2 | 2014-06-09 | 9:00 | 1.9 | 38.8 | 11.28 | 0.9 | 1.8
2014-06-16 | 13:50 | 2.6 | 36.9 | 11.68 | 0.7 | 1.4 | 2014-06-16 | 13:58 | 1.9 | 38.4 | 9.15 | 1.1 | 2.2
2014-06-23 | 13:30 | 2.4 | 39.6 | 11.55 | 1.2 | 2.4 | 2014-06-23 | 13:30 | 1.8 | 39.7 | 11.54 | 1.2 | 2.4
2014-06-30 | 13:30 | 2.8 | 36.6 | 11.75 | 0.75 | 1.5 | 2014-06-30 | 13:30 | 1.9 | 35.5 | 12 | 0.75 | 1.5
2014-07-07 | 9:00 | 2.4 | 38.1 | 9.35 | 0.8 | 1.6 | 2014-07-07 | 09:.00 | 1.8 | 39.1 | 10.4 | 1.2 | 2.4
2014-07-14 | 15:15 | 2.3 | 38.3 | 9.5 | 0.75 | 1.5 | 2014-07-14 | 15:15 | 1.8 | 39.3 | 10.7 | 1 | 2
2014-07-21 | 2:30 | 2.4 | 39.3 | 11.43 | 1.2 | 2.4 | 2014-07-21 | 2:30 | 1.8 | 40.9 | 11.22 | 1.2 | 2.4
2014-07-28 | 8:45 | 2.4 | 38 | 11.36 | 0.8 | 1.6 | 2014-07-28 | 8:45 | 1.8 | 38.8 | 8.48 | 0.8 | 1.6
2014-08-05 | 9:30 | 2.5 | 38.8 | 11.47 | 0.8 | 1.6 | 2014-08-05 | 9:35 | 1.8 | 40.6 | 11.92 | 0.6 | 1.2
2014-08-12 | 9:40 | 2.5 | 36.7 | 11.2 | 0.7 | 1.4 | 2014-08-12 | 9:40 | 1.9 | 38.4 | 11.54 | 1 | 2
2014-08-18 | 9:00 | 2.6 | 36.2 | 7.7 | 1 | 2 | 2014-08-18 | 9:00 | 2 | 37.8 | 8.41 | 1.1 | 2.2
2014-08-26 | 15:10 | 2.7 | 37.1 | 10.89 | 0.7 | 1.4 | 2014-08-26 | 15:10 | 2 | 38 | 11.47 | 0.8 | 1.6
2014-09-01 | 9:00 | 2.6 | 37.1 | 11.2 | 1 | 2 | 2014-09-01 | 9:00 | 2 | 37.7 | 10.23 | 1.1 | 2.2
2014-09-08 | 9:45 | 2.6 | 38.2 | 10.75 | 1.2 | 2.4 | 2014-09-09 | 12:30 | 2 | 37.7 | 9.15 | 1.4 | 2.8
2014-09-15 | 11:45 | 2.6 | 39.4 | 10.7 | 1.1 | 2.2 | 2014-09-15 | 11:45 | 2 | 38.9 | 8.15 | 1.3 | 2.6
2014-09-22 | 9:15 | 2.6 | 36.7 | 10.72 | 1.2 | 2.4 | 2014-09-22 | 9:15 | 2 | 32.8 | 8.45 | 1.3 | 2.6
2014-09-29 | 9:00 | 2.6 | 35 | 10.13 | 1.1 | 2.2 | 2014-09-29 | 9:00 | 2 | 35.1 | 8.15 | 1.3 | 2.6
2014-10-06 | 13:30 | 2.6 | 36.9 | 10.75 | 1.25 | 2.5 | 2014-10-06 | 13:30 | 2 | 35.8 | 9.2 | 1.25 | 2.5
2014-10-14 | 15:30 | 2.4 | 37.5 | 10.38 | 1.2 | 2.4 | 2014-10-14 | 15:30 | 2 | 35.8 | 9.45 | 1.3 | 2.6
2014-10-20 | 15:30 | 2.4 | 36.2 | 10.63 | 1 | 2 | 2014-10-20 | 15:30 | 2 | 35.4 | 8.2 | 1.1 | 2.2
2014-10-27 | 9:30 | 2.4 | 36.6 | 9.99 | 1.2 | 2.4 | 2014-10-27 | 9:30 | 2 | 35.7 | 7.2 | 1.2 | 2.4
2014-11-03 | 9:30 | 2.6 | 36.3 | 11.28 | 1 | 2 | 2014-11-03 | 9:30 | 2.2 | 33.4 | 8.7 | 1.1 | 2.2
2014-11-10 | 9:30 | 2.6 | 36.8 | 10.82 | 0.7 | 1.4 | 2014-11-10 | 9:30 | 2.2 | 34.5 | 8.4 | 1.2 | 2.4
2014-11-17 | 13:30 | 2.9 | 37.5 | 10.8 | 0.7 | 1.4 | 2014-11-17 | 13:30 | 2 | 35.2 | 8.6 | 1.2 | 2.4
2014-11-24 | 10:45 | 2.7 | 35.9 | 8.6 | 0.9 | 1.8 | 2014-11-24 | 10:45 | 1.9 | 33.2 | 8.7 | 1.2 | 2.4
2014-12-01 | 13:15 | 2.8 | 36.3 | 9.07 | 0.8 | 1.6 | 2014-12-01 | 13:15 | 2 | 34.1 | 9.7 | 1.2 | 2.4
2014-12-08 | 11:45 | 2.7 | 34.7 | 9.9 | 0.7 | 1.4 | 2014-12-08 | 11:45 | 1.8 | 32.4 | 9.25 | 1.2 | 2.4
2014-12-15 | 10:45 | 2.8 | 34.9 | 11.14 | 0.8 | 1.6 | 2014-12-15 | 10:45 | 2 | 33.7 | 8.41 | 0.9 | 1.8
2014-12-22 | 13:00 | 2.6 | 36.6 | 11.55 | 0.6 | 1.2 | 2014-12-22 | 13:00 | 1.8 | 36 | 10.68 | 0.5 | 1
2014-12-29 | 12:00 | 2.5 | 33.8 | 11.29 | 0.7 | 1.4 | 2014-12-29 | 12:00 | 1.8 | 31.8 | 11.7 | 0.6 | 1.2
2015-01-05 | 10:40 | 2.4 | 33.3 | 10.38 | 0.9 | 1.8 | 2015-01-05 | 10:40 | 1.8 | 33.9 | 10.84 | 1 | 2
2015-01-12 | 13:15 | 2.6 | 32.8 | 10.9 | 1 | 2 | 2015-01-12 | 13:15 | 1.8 | 32.7 | 9.43 | 1 | 2
2015-01-19 | 10:45 | 2.8 | 31.8 | 9.44 | 0.6 | 1.2 | 2015-01-19 | 10:45 | 1.8 | 31.7 | 8.84 | 0.8 | 1.6
2015-01-26 | 10:30 | 2.7 | 34.8 | 9.79 | 1.2 | 2.4 | 2015-01-26 | 10:30 | 1.8 | 33.9 | 9.45 | 0.8 | 1.6
2015-02-02 | 11:00 | 2.6 | 33.6 | 9.31 | 0.7 | 1.4 | 2015-02-02 | 11:00 | 1.8 | 31.6 | 10.31 | 0.8 | 1.6
2015-02-09 | 11:10 | 2.6 | 35.7 | 9.48 | 1 | 2 | 2015-02-09 | 11:10 | 1.8 | 34.9 | 9.34 | 1 | 2
2015-02-16 | 13:10 | 2.6 | 33.3 | 8.57 | 0.7 | 1.4 | 2015-02-16 | 13:10 | 1.8 | 33.5 | 8.32 | 1 | 2
2015-02-23 | 9:15 | 2.5 | 31.7 | 10.4 | 0.7 | 1.4 | 2015-02-23 | 9:15 | 1.8 | 30.9 | 12 | 1 | 2
2015-03-03 | 10:30 | 2.6 | 32.3 | 9.88 | 1 | 2 | 2015-03-02 | 9:20 | 1.9 | 31.1 | 10.03 | 0.8 | 1.6
2015-03-09 | 9:00 | 2.5 | 34.3 | 10.94 | 0.7 | 1.4 | 2015-03-09 | 9:00 | 1.8 | 33.9 | 9.55 | 1 | 2
2015-03-16 | 9:00 | 2.5 | 35 | 11.1 | 0.7 | 1.4 | 2015-03-16 | 9:00 | 1.9 | 33.8 | 10.8 | 0.7 | 1.4
2015-03-23 | 13:15 | 2.4 | 35.5 | 11 | 0.7 | 1.4 | 2015-03-23 | 13:15 | 1.9 | 34.4 | 11.2 | 0.8 | 1.6
2015-03-30 | 9:10 | 2.4 | 34.8 | 10.9 | 0.6 | 1.2 | 2015-03-30 | 9:10 | 1.8 | 32.7 | 10.5 | 0.6 | 1.2
2015-04-07 | 15:10 | 2.5 | 37.7 | 11.56 | 0.6 | 1.2 | 2015-04-07 | 15:10 | 1.9 | 37.8 | 11.8 | 1.2 | 2.4
2015-04-13 | 9:15 | 2.5 | 34.9 | 9.65 | 1 | 2 | 2015-04-13 | 9:15 | 1.9 | 34.8 | 10.51 | 0.7 | 1.4
2015-04-20 | 10:45 | 2.5 | 35.2 | 8.7 | 1.3 | 2.6 | 2015-04-20 | 10:45 | 1.9 | 38.2 | 8.8 | 1 | 2
2015-04-27 | 10:45 | 2.6 | 34.6 | 8.45 | 1.3 | 2.6 | 2015-04-27 | 10:45 | 1.9 | 35.6 | 8.95 | 0.9 | 1.8
2015-05-05 | 9:20 | 2.4 | 36.4 | 8.75 | 1 | 2 | 2015-05-05 | 9:20 | 1.9 | 39.7 | 10.5 | 0.8 | 1.6
2015-05-11 | 15:05 | 2.5 | 35.5 | 8.75 | 1 | 2 | 2015-05-11 | 15:05 | 2 | 36.5 | 10.5 | 0.5 | 1
2015-05-18 | 10:45 | 2.6 | 32.3 | 9.1 | 1 | 2 | 2015-05-18 | 10:45 | 2.2 | 37.1 | 8.95 | 1 | 2
2015-05-26 | 9:00 | 2.6 | 36.4 | 10.4 | 1.2 | 2.4 | 2015-05-26 | 9:00 | 2.2 | 39.2 | 9.45 | 0.9 | 1.8
2015-06-01 | 11:00 | 2.4 | 34.9 | 8.9 | 1.2 | 2.4 | 2015-06-01 | 11:00 | 2 | 38.3 | 9.1 | 1.1 | 2.2
2015-06-08 | 11:20 | 2.4 | 36.3 | 9.1 | 1.4 | 2.8 | 2015-06-08 | 11:20 | 2 | 38.6 | 9.55 | 0.8 | 1.6
2015-06-15 | 11:00 | 2.4 | 35.4 | 8.45 | 1.4 | 2.8 | 2015-06-15 | 11:00 | 1.9 | 38.6 | 9.55 | 1 | 2
2015-06-22 | 11:15 | 2.5 | 34.5 | 8.35 | 1 | 2 | 2015-06-22 | 11:15 | 2 | 38.2 | 8.6 | 1 | 2
2015-06-29 | 15:00 | 2.4 | 35.5 | 8.25 | 1 | 2 | 2015-06-22 | 15:00 | 2 | 37.2 | 8.7 | 1 | 2
2015-07-06 | 12:45 | 2.4 | 36 | 8.75 | 1 | 2 | 2015-07-06 | 12:45 | 2 | 35.8 | 9 | 1 | 2
2015-07-20 | 11:10 | 2.6 | 39.2 | 9.5 | 1 | 2 | 2015-07-20 | 11:10 | 2 | 39.7 | 9.25 | 0.9 | 1.8
2015-07-27 | 13:15 | 2.6 | 37.7 | 8.65 | 0.7 | 1.4 | 2015-07-27 | 13:15 | 2 | 37.9 | 9.45 | 0.9 | 1.8
2015-08-05 | 13:30 | 2.6 | 38.6 | 10.34 | 1.2 | 2.4 | 2015-08-03 | 15:30 | 2.2 | 40.4 | 10.67 | 1 | 2
2015-08-10 | 11:15 | 2.6 | 40.3 | 10.58 | 1.1 | 2.2 | 2015-05-10 | 11:15 | 1.95 | 40.4 | 10.2 | 0.9 | 1.8
2015-08-17 | 9:00 | 2.6 | 37.1 | 10.74 | 1 | 2 | 2015-08-17 | 9:00 | 2 | 39.1 | 9.45 | 1.1 | 2.2
2015-08-24 | 11:30 | 2.5 | 38.7 | 11.26 | 1.1 | 2.2 | 2015-08-24 | 11:30 | 2 | 40.2 | 8.11 | 1 | 2
2015-09-01 | 10:45 | 2.4 | 37.3 | 10.74 | 1 | 2 | 2015-09-01 | 10:45 | 1.95 | 38.2 | 9.1 | 1.1 | 2.2
2015-09-07 | 13:40 | 2.5 | 37.7 | 11 | 1 | 2 | 2015-09-07 | 13:40 | 2 | 38.3 | 9.2 | 1.1 | 2.2
2015-09-14 | 13:15 | 2.6 | 32.4 | 9.2 | 1.2 | 2.4 | 2015-09-14 | 13:15 | 2 | 37 | 9.8 | 1.2 | 2.4
2015-09-22 | 9:30 | 2.5 | 37 | 10.2 | 0.6 | 1.2 | 2015-09-22 | 9:30 | 1.9 | 38.5 | 10.3 | 1 | 2
2015-09-28 | 13:30 | 2.5 | 36.2 | 10.4 | 0.7 | 1.4 | 2015-09-28 | 13:30 | 2 | 37.3 | 9.55 | 0.9 | 1.8
2015-10-05 | 11:15 | 2.5 | 36.1 | 9.3 | 0.9 | 1.8 | 2015-10-05 | 11:15 | 2 | 36.6 | 9.4 | 1 | 2
2015-10-12 | 11:15 | 2.6 | 33.6 | 9.2 | 1 | 2 | 2015-10-12 | 11:15 | 2 | 37.5 | 9.55 | 0.9 | 1.8
2015-10-19 | 14:30 | 2.7 | 35.8 | 9.4 | 1 | 2 | 2015-10-19 | 14:30 | 2.1 | 36.9 | 9.3 | 0.75 | 1.5
2015-10-26 | 15:45 | 2.6 | 35.9 | 11.06 | 1 | 2 | 2015-10-26 | 15:45 | 2 | 30 | 9.06 | 0.8 | 1.6
2015-11-02 | 13:55 | 2.5 | 31.1 | 10.91 | 1 | 2 | 2015-11-02 | 13:55 | 2 | 32.6 | 11.09 | 0.7 | 1.4
2015-11-09 | 13:30 | 2.5 | 37 | 11.33 | 1 | 2 | 2015-11-09 | 13:30 | 2 | 31.6 | 11.17 | 0.7 | 1.4
2015-11-16 | 13:15 | 2.4 | 34.6 | 10.23 | 1.1 | 2.2 | 2015-11-16 | 13:15 | 2 | 35.1 | 10.35 | 0.7 | 1.4
2015-11-23 | 14:10 | 2.5 | 32.5 | 10.49 | 1 | 2 | 2015-11-23 | 14:10 | 2 | 31.2 | 9.09 | 0.7 | 1.4
2015-11-30 | 10:00 | 2.4 | 35.8 | 11.24 | 0.5 | 1 | 2015-11-30 | 10:00 | 2 | 34.8 | 11.09 | 0.5 | 1
2015-12-07 | 13:45 | 2.5 | 37.9 | 11.43 | 0.8 | 1.6 | 2015-12-07 | 13:45 | 2 | 28 | 10.21 | 0.6 | 1.2
2015-12-14 | 13:10 | 2.4 | 34.4 | 11.25 | 0.4 | 0.8 | 2015-12-14 | 13:10 | 1.8 | 32.6 | 10.8 | 0.8 | 1.6
2015-12-21 | 13:15 | 2.4 | 33.9 | 10.86 | 0.7 | 1.4 | 2015-12-21 | 13:15 | 1.8 | 30.9 | 10.51 | 0.7 | 1.4
2015-12-29 | [5 empty] | 0 | 2015-12-29 | 14:15 |  | 36.3 | 10.94 | 0.8 | 1.6
2016-01-04 | [5 empty] | 0 | 2016-01-04 | 11:15 | 1.95 | 27.5 | 10.04 | 0.7 | 1.4
2016-01-11 | 14:35 | 2.4 | 34.8 | 11.1 | 0.8 | 1.6 | 2016-01-11 | 14:35 | 1.95 | 28.1 | 8.01 | 1 | 2
2016-01-18 | 13:30 | 2.4 | 35.1 | 11.13 | 0.6 | 1.2 | 2016-01-18 | 13:30 | 1.8 | 34.2 | 10.59 | 0.8 | 1.6
2016-01-25 | 15:30 | 2.4 | 31.1 | 9.58 | 0.7 | 1.4 | 2016-01-25 | 15:30 | 1.8 | 32.9 | 8.53 | 0.7 | 1.4
2016-02-01 | 14:10 | 2.4 | 35.3 | 11.28 | 0.7 | 1.4 | 2016-02-01 | 14:10 | 1.95 | 34.8 | 10.27 | 1 | 2
2016-02-08 | 14:15 | 2.6 | 26.6 | 11.54 | 0.7 | 1.4 | 2016-02-08 | 14:15 | 1.95 | 31.6 | 8.92 | 0.6 | 1.2
2016-02-16 | 13:45 | 2.45 | 33.8 | 10.21 | 0.5 | 1 | 2016-02-16 | 13:45 | 1.95 | 32.1 | 10.12 | 0.6 | 1.2
2016-02-22 | 13:30 | 2.5 | 34.5 | 9.75 | 0.7 | 1.4 | 2016-02-22 | 13:30 | 2 | 33.1 | 10.14 | 0.7 | 1.4
2016-02-29 | 14:05 | 2.5 | 36.2 | 11.06 | 1 | 2 | 2016-02-29 | 14:05 | 2 | 31.7 | 8.34 | 0.8 | 1.6
2016-03-07 | 13:30 | 2.5 | 34.8 | 8.39 | 0.5 | 1 | 2016-03-07 | 13:30 | 1.9 | 30.8 | 8.88 | 0.5 | 1
2016-03-14 | 15:35 | 2.6 | 35.3 | 9.47 | 0.8 | 1.6 | 2016-03-14 | 15:35 | 2 | 35.1 | 10.47 | 0.7 | 1.4
2016-03-21 | 13:40 | 2.6 | 34.4 | 10.32 | 0.7 | 1.4 | 2016-03-21 | 13:40 | 2 | 33.6 | 10.98 | 0.8 | 1.6
2016-03-29 | 11:55 | 2.4 | 32.4 | 10.12 | 0.7 | 1.4 | 2016-03-29 | 11:55 | 1.9 | 33.9 | 10.6 | 1 | 2
2016-04-04 | 15:35 | 2.4 | 30.4 | 10.87 | 0.5 | 1 | 2016-04-04 | 15:35 | 2 | 34.8 | 8.01 | 0.7 | 1.4
2016-04-11 | 15:20 | 2.4 | 36 | 11.39 | 0.8 | 1.6 | 2016-04-11 | 15:20 | 1.95 | 34.5 | 10.72 | 0.8 | 1.6
2016-04-18 | 15:00 | 2.4 | 35 | 11 | 0.75 | 1.5 | 2016-04-18 | 15:00 | 2 | 36 | 10.5 | 0.75 | 1.5
2016-04-25 | 15:15 | 2.3 | 36.1 | 11.2 | 0.75 | 1.5 | 2016-04-25 | 15:15 | 2 | 36.6 | 10.8 | 0.75 | 1.5
2016-05-03 | 10:30 | 2.5 | 36.2 | 11.31 | 0.6 | 1.2 | 2016-05-03 | 10:30 | 1.9 | 36.8 | 10.33 | 0.7 | 1.4
2016-05-09 | 14:05 | 2.4 | 35.9 | 10.79 | 0.8 | 1.6 | 2016-05-09 | 14:05 | 1.9 | 30.9 | 9.24 | 1 | 2
2016-05-16 | 9:35 | 2.4 | 36.1 | 10.4 | 0.7 | 1.4 | 2016-05-16 | 9:35 | 2 | 34.6 | 10.07 | 0.9 | 1.8
2016-05-23 | 10:50 | 2.4 | 35 | 11.26 | 0.7 | 1.4 | 2016-05-23 | 10:50 | 2 | 33.1 | 9.82 | 1 | 2
2016-05-31 | 9:35 | 2.4 | 35.2 | 11.69 | 0.5 | 1 | 2016-05-31 | 9:40 | 1.9 | 35.1 | 10.1 | 0.4 | 0.8
2016-06-06 | 12:10 | 2.3 | 37.1 | 10.53 | 0.8 | 1.6 | 2016-06-06 | 12:10 | 1.8 | 37.4 | 10.26 | 0.8 | 1.6
2016-06-13 | 14:30 | 2.2 | 38.3 | 10.17 | 0.8 | 1.6 | 2016-06-13 | 14:30 | 1.8 | 39.2 | 8.91 | 1 | 2
2016-06-20 | 14:10 | 2.2 | 38.3 | 10.22 | 1 | 2 | 2016-06-20 | 14:10 | 1.8 | 39.6 | 9.48 | 1 | 2
2016-06-28 | 11:45 | 2.3 | 39.7 | 10.16 | 0.2 | 0.4 | 2016-06-28 | 11:45 | 1.8 | 39.6 | 10.12 | 0.25 | 0.5
2016-07-04 | 9:15 | 2.2 | 36.5 | 10.28 | 0.7 | 1.4 | 2016-07-04 | 9:15 | 1.8 | 33.4 | 9.2 | 0.8 | 1.6
2016-07-11 | 14:10 | 2.2 | 37.9 | 9.22 | 0.7 | 1.4 | 2016-07-11 | 14:10 | 1.8 | 33.4 | 10.07 | 0.8 | 1.6
2016-07-18 | 9:15 | 2.2 | 39.7 | 9.87 | 0.8 | 1.6 | 2016-07-18 | 9:15 | 1.8 | 39.7 | 9.93 | 0.9 | 1.8
2016-07-25 | 15:10 | 2.2 | 38.7 | 10.59 | 0.6 | 1.2 | 2016-07-25 | 15:10 | 1.8 | 37.9 | 9.65 | 0.5 | 1
2016-08-15 | 9:15 | 2.4 | 35.5 | 10.1 | 0.6 | 1.2 | 2016-08-15 | 9:15 | 1.8 | 31.2 | 10.07 | 0.5 | 1
2016-08-24 | 9:50 | 2.6 | 38.6 | 9.15 | 0.6 | 1.2 | 2016-08-22 | 9:20 | 1.9 | 36.1 | 9.55 | 0.25 | 0.5
2016-08-30 | 11:00 | 2 | 38 | 10.5 | 0.5 | 1 | 2016-08-31 | 9:20 | 2 | 37.8 | 9.45 | 0.4 | 0.8
2016-09-05 | 14:45 | 2.1 | 36.9 | 10.1 | 0.5 | 1 | 2016-09-05 | 14:45 | 1.9 | 37.2 | 9.75 | 0.5 | 1
2016-09-12 | 14:55 | 2.2 | 39.6 | 10.2 | 0.25 | 0.5 | 2016-09-12 | 14:55 | 2.2 | 39.3 | 8.3 | 0.5 | 1
2016-09-20 | 10:00 | 2.4 | 35.9 | 10.69 | 0.5 | 1 | 2016-09-20 | 10:00 | 2.2 | 37.6 | 10.22 | 0.6 | 1.2
2016-09-26 | 11:10 | 2.4 | 37.3 | 10.71 | 0.25 | 0.5 | 2016-09-26 | 11:10 | 2.2 | 37.9 | 10.05 | 0.26 | 0.52
2016-10-03 | 13:30 | 2.4 | 36.8 | 9.46 | 0.7 | 1.4 | 2016-10-03 | 13:30 | 2 | 37.5 | 10.95 | 0.7 | 1.4
2016-10-10 | 11:00 | 2.4 | 36.6 | 9.99 | 0.7 | 1.4 | 2016-10-10 | 11:00 | 2.1 | 31.1 | 10.54 | 0.5 | 1
2016-10-17 | 11:30 | 2.4 | 36.4 | 9.7 | 0.8 | 1.6 | 2016-10-17 | 11:30 | 2.1 | 31.7 | 9.34 | 0.35 | 0.7
2016-10-24 | 11:45 | 2.4 | 37.6 | 11 | 1 | 2 | 2016-10-24 | 11:45 | 2 | 36.9 | 9.1 | 1.2 | 2.4
2016-10-31 | 11:20 | 2.4 | 38.2 | 11.07 | 0.6 | 1.2 | 2016-10-31 | 11:20 | 2.1 | 37.6 | 9.8 | 1 | 2
2016-11-07 | 11:30 | 2.4 | 35 | 10.33 | 0.5 | 1 | 2016-11-07 | 11:30 | 2.1 | 35.9 | 11.4 | 0.6 | 1.2
2016-11-14 | 13:55 | 2.4 | 36.7 | 9.93 | 0.6 | 1.2 | 2016-11-14 | 13:55 | 2.2 | 37.6 | 10.33 | 0.7 | 1.4
2016-11-22 | 13:40 | 2.6 | 34.9 | 10.18 | 0.8 | 1.6 | 2016-11-21 | 9:50 | 2.2 | 34.3 | 10.95 | 1 | 2
2016-11-28 | 11:45 | 2.25 | 36.8 | 11.1 | 0.5 | 1 | 2016-11-28 | 11:45 | 2.05 | 38 | 10.65 | 0.75 | 1.5
2016-12-05 | 10:50 | 2.4 | 36.7 | 10.59 | 0.8 | 1.6 | 2016-12-05 | 10:55 | 2.1 | 35.9 | 10.5 | 1 | 2
2016-12-12 | 13:15 | 2.4 | 34.9 | 10.38 | 0.8 | 1.6 | 2016-12-12 | 13:15 | 2.2 | 34.1 | 10.22 | 1.1 | 2.2
2016-12-19 | 11:15 | 2.2 | 31.6 | 10.74 | 0.5 | 1 | 2016-12-19 | 11:15 | 2.1 | 36.3 | 10.98 | 0.8 | 1.6
2016-12-27 | 14:45 | 2.4 | 34.9 | 10.12 | 0.6 | 1.2 | 2016-12-30 | 13:45 | 2.2 | 34.3 | 9.81 | 0.8 | 1.6
2017-01-03 | 13:30 | 2.4 | 33.8 | 10.41 | 0.9 | 1.8 | 2017-01-04 | 12:20 | 2.1 | 34.4 | 9.8 | 0.5 | 1
2017-01-09 | 10:50 | 2.3 | 34.1 | 8.99 | 0.7 | 1.4 | 2017-01-09 | 10:50 | 2.2 | 33.1 | 8.82 | 0.6 | 1.2
2017-01-16 | 11:30 | 2.4 | 34.8 | 9.93 | 0.6 | 1.2 | 2017-01-16 | 11:30 | 2.2 | 35.2 | 9.95 | 0.6 | 1.2
2017-01-23 | 11:30 | 2.3 | 33.9 | 10.18 | 0.7 | 1.4 | 2017-01-23 | 11:30 | 2.2 | 33.6 | 10.8 | 0.6 | 1.2
2017-01-30 | 14:30 | 2.3 | 36.2 | 10.78 | 0.9 | 1.8 | 2017-01-30 | 14:30 | 2.2 | 35.9 | 11.28 | 1 | 2
2017-02-06 | 12:00 | 2.4 | 36.5 | 11.95 | 0.7 | 1.4 | 2017-02-06 | 12:00 | 2.4 | 34.8 | 11.8 | 0.4 | 0.8
2017-02-13 | 11:00 | 2.4 | 34.1 | 10.4 | 0.9 | 1.8 | 2017-02-13 | 11:00 | 2.2 | 34.6 | 11.2 | 1 | 2
2017-02-20 | 11:30 | 2.4 | 37.2 | 12.05 | 0.6 | 1.2 | 2017-02-20 | 11:30 | 2.2 | 36.7 | 11.8 | 0.7 | 1.4
2017-02-27 | 15:35 | 2.4 | 35.5 | 11.47 | 0.8 | 1.6 | 2017-02-27 | 15:35 | 2.2 | 31.8 | 10.57 | 0.7 | 1.4
2017-03-06 | 14:15 | 2.4 | 33.6 | 9.06 | 0.7 | 1.4 | 2017-03-08 | 15:30 | 2.2 | 35.8 | 11.07 | 0.6 | 1.2
2017-03-13 | 12:00 | 2.4 | 35.8 | 10.13 | 0.9 | 1.8 | 2017-03-13 | 12:00 | 2.2 | 37.1 | 10.61 | 1 | 2
2017-03-20 | 14:00 | 2.5 | 35.9 | 11 | 0.8 | 1.6 | 2017-03-13 | 14:00 | 2.2 | 35.2 | 10.8 | 1 | 2
2017-03-27 | 12:00 | 2.4 | 37.3 | 11.1 | 1 | 2 | 2017-03-27 | 12:00 | 2.1 | 35.7 | 12.1 | 0.6 | 1.2
2017-04-03 | 16:00 | 2.4 | 35.7 | 9.9 | 0.7 | 1.4 | 2017-04-04 | 11:00 | 2.1 | 35.3 | 11.02 | 1 | 2
2017-04-10 | 15:35 | 2.4 | 37.3 | 11.85 | 0.7 | 1.4 | 2017-04-10 | 15:35 | 2.1 | 34.4 | 12.13 | 0.8 | 1.6
2017-04-18 | 9:30 | 2.3 | 36.4 | 10.16 | 1 | 2 | 2017-04-18 | 19:30 | 2.2 | 32.2 | 12.17 | 1.1 | 2.2
2017-04-24 | 13:30 | 2.4 | 37.3 | 11.61 | 0.7 | 1.4 | 2017-04-24 | 13:30 | 2.2 | 34.2 | 12.97 | 0.7 | 1.4
2017-05-02 | 12:00 | 2.4 | 36.9 | 10.38 | 1.1 | 2.2 | 2017-05-02 | 12:00 | 2.2 | 36.9 | 13.18 | 1 | 2
2017-05-08 | 12:00 | 2.4 | 34.7 | 10.6 | 1.5 | 3 | 2017-05-08 | 12:00 | 2.2 | 33.4 | 11.1 | 0.75 | 1.5
2017-05-15 | 12:00 | 2.4 | 35.5 | 10.45 | 1 | 2 | 2017-05-15 | 12:00 | 2.2 | 33.8 | 11.5 | 1 | 2
2017-05-22 | 12:00 | 2.4 | 38.8 | 11.2 | 1 | 2 | 2017-05-22 | 12:00 | 2 | 38.1 | 10.7 | 1 | 2
2017-05-30 | 9:00 | 2.4 | 36.5 | 10.49 | 0.9 | 1.8 | 2017-05-30 | 9:00 | 2 | 37.4 | 11.24 | 0.7 | 1.4
2017-06-05 | 14:00 | 2.4 | 36.7 | 11.1 | 0.7 | 1.4 | 2017-06-05 | 14:00 | 2 | 37.6 | 12 | 1 | 2
2017-06-12 | 12:00 | 2 | 36.2 | 9.8 | 0.8 | 1.6 | 2017-06-12 | 14:00 | 1.9 | 39.8 | 10.52 | 1.1 | 2.2
2017-06-19 | 12:00 | 2.4 | 42.1 | 11.5 | 1 | 2 | 2017-06-19 | 12:00 | 1.8 | 41.6 | 9.9 | 1.1 | 2.2
2017-06-26 | 13:30 | 2.4 | 37.9 | 9.91 | 1 | 2 | 2017-06-26 | 13:30 | 1.9 | 36.9 | 12.48 | 0.9 | 1.8
2017-07-03 | 12:30 | 2.5 | 38.1 | 11.68 | 0.7 | 1.4 | 2017-06-03 | [5 empty] | 0
2017-07-10 | 12:00 | 2.6 | 37.8 | 10.6 | 1 | 2 | 2017-07-10 | 12:00 | 2 | 22.2 | 10.6 | 0.5 | 1
2017-07-17 | 12:00 | 2.5 | 39.7 | 12.4 | 1 | 2 | 2017-07-21 | 13:00 | 2 | 36.6 | 11.4 | 0.7 | 1.4
2017-07-24 | 14:00 | 2.5 | 37.8 | 12.5 | 1 | 2 | 2017-07-24 | 14:00 | 2 | 35.6 | 10.6 | 1.1 | 2.2
2017-07-31 | 14:00 | 2.6 | 40.3 | 11.8 | 0.75 | 1.5 | 2017-07-31 | 14:00 | 2 | 39.4 | 11.6 | 1.25 | 2.5
2017-08-07 | 12:00 | 1 | 40.1 | 10.8 | 1 | 2 | 2017-08-07 | 12:00 | 1 | 36.7 | 9.95 | 1.25 | 2.5
2017-08-14 | 11:30 | 2.4 | 39.4 | 10.9 | 1 | 2 | 2017-08-14 | 11:30 | 2.2 | 38.2 | 11 | 1.5 | 3
2017-08-21 | 13:50 | 2.4 | 38.8 | 10.59 | 1 | 2 | 2017-08-21 | 13:50 | 2.2 | 33.9 | 10.61 | 1 | 2
2017-08-29 | 9:30 | 2.4 | 38.4 | 11.86 | 1.1 | 2.2 | 2017-08-29 | 9:30 | 2 | 31.9 | 11.09 | 0.9 | 1.8
2017-09-04 | 12:00 | 2.6 | 37 | 11.2 | 1 | 2 | 2017-09-04 | 12:00 | 2 | 38.6 | 10.1 | 1 | 2
2017-09-11 | 11:30 | 2.4 | 35.8 | 11.1 | 1 | 2 | 2017-09-11 | 11:30 | 2.2 | 36.4 | 11.4 | 1 | 2
2017-09-18 | 14:00 | 2.7 | 38.5 | 12.6 | 1 | 2 | 2017-09-18 | 14:00 | 2 | 37.8 | 10.6 | 1 | 2
2017-09-25 | 14:00 | 2.6 | 38.4 | 10.71 | 1 | 2 | 2017-09-25 | 14:00 | 2 | 38.3 | 11.34 | 1.1 | 2.2
2017-10-02 | 14:00 | 2.6 | 36.2 | 11.2 | 1 | 2 | 2017-10-02 | 14:00 | 2 | 36.8 | 12 | 1 | 2
2017-10-09 | 11:00 | 2.6 | 35.4 | 11.5 | 1 | 2 | 2017-10-09 | 11:00 | 2 | 37.1 | 10.8 | 0.75 | 1.5
2017-10-16 | 11:00 | 2.6 | 37.1 | 11.4 | 1.1 | 2.2 | 2017-10-16 | 11:00 | 2 | 36.8 | 11.2 | 1.1 | 2.2
2017-10-24 | 15:00 | 2.7 | 37.5 | 12.3 | 1.1 | 2.2 | 2017-10-23 | 11:00 | 2 | 35.2 | 11.9 | 1 | 2
2017-10-30 | 12:00 | 2.6 | 35.1 | 11.1 | 1 | 2 | 2017-10-30 | 12:00 | 2 | 35.5 | 11.9 | 1 | 2
2017-11-06 | 12:00 | 2.6 | 35.7 | 10.8 | 1 | 2 | 2017-11-06 | 12:00 | 2 | 31.1 | 11.6 | 0.5 | 1
2017-11-13 | 14:00 | 2.6 | 34.7 | 12.7 | 0.75 | 1.5 | 2017-11-13 | 14:00 | 2 | 33.9 | 11.3 | 1 | 2
2017-11-20 | 12:00 | 2.6 | 35.6 | 11.7 | 0.7 | 1.4 | 2017-11-20 | 12:00 | 2 | 35.9 | 11 | 1 | 2
2017-11-27 | 12:00 | 2.6 | 35.4 | 12 | 0.5 | 1 | 2017-11-27 | 12:00 | 2 | 34.6 | 12.4 | 1 | 2
2017-12-04 | 15:30 | 2.6 | 36.1 | 10.25 | 0.9 | 1.8 | 2017-12-04 | 15:30 | 2.1 | 31.3 | 10.58 | 0.5 | 1
2017-12-11 | 11:15 | 2.6 | 34.3 | 11.4 | 0.8 | 1.6 | 2017-12-11 | 11:15 | 2.1 | 33.5 | 11.5 | 0.8 | 1.6
2017-12-18 | 13:30 | 2.3 | 35.8 | 12.2 | 0.8 | 1.6 | 2017-12-18 | 13:30 | 2 | 34.6 | 9.8 | 0.8 | 1.6
2017-12-27 | 14:15 | 2.4 | 34.9 | 12.96 | 0.7 | 1.4 | 2017-12-27 | 14:15 | 2.1 | 34.6 | 13.01 | 0.4 | 0.8
2018-01-02 | 11:45 | 2.4 | 32.5 | 10.8 | 0.6 | 1.2 | 2018-01-02 | 11:45 | 2 | 33.6 | 11.45 | 0.8 | 1.6
2018-01-08 | 11:45 | 2.4 | 33.7 | 11.2 | 0.8 | 1.6 | 2018-01-08 | 11:45 | 2 | 32.6 | 0.48958 | 0.8 | 1.6
2018-01-15 | 11:45 | 2.5 | 36.2 | 12.4 | 0.6 | 1.2 | 2018-01-15 | 11:45 | 2.1 | 36.2 | 11.2 | 0.7 | 1.4
2018-01-22 | 11:00 | 2.4 | 35.5 | 10.3 | 0.7 | 1.4 | 2018-01-22 | 11:00 | 2 | 35.5 | 11.5 | 1 | 2
2018-01-29 | 9:15 | 2.4 | 36.6 | 12.2 | 0.75 | 1.5 | 2018-01-29 | 9:15 | 2 | 35.4 | 10.6 | 1 | 2
2018-02-05 | 10:50 | 2.4 | 33 | 11.94 | 1.3 | 2.6 | 2018-02-05 | 10:50 | 2 | 33.1 | 12.03 | 1 | 2
2018-02-12 | 16:00 | 2.5 | 37.1 | 10.9 | 0.75 | 1.5 | 2018-02-12 | 16:00 | 2.1 | 36.8 | 11 | 0.9 | 1.8
2018-02-19 | 11:10 | 2.4 | 32.3 | 11.07 | 0.6 | 1.2 | 2018-02-19 | 11:10 | 2 | 35.2 | 12.87 | 0.7 | 1.4
2018-02-26 | 16:00 | 2.5 | 34.8 | 12.4 | 0.7 | 1.4 | 2018-02-26 | 16:00 | 2 | 33 | 11.7 | 0.8 | 1.6
2018-03-05 | 11:00 | 2.4 | 36.6 | 10.7 | 0.75 | 1.5 | 2018-03-05 | 11:00 | 2 | 36.2 | 12.2 | 0.6 | 1.2
2018-03-12 | 14:00 | 2.4 | 34.6 | 10.6 | 0.6 | 1.2 | 2018-03-12 | 14:00 | 2.4 | 34.6 | 11.6 | 1 | 2
2018-03-19 | 12:00 | 2.4 | 34.9 | 12.1 | 1 | 2 | 2018-03-19 | 12:00 | 2.3 | 35.1 | 11.8 | 1 | 2
2018-03-26 | 11:30 | 2.3 | 37.4 | 11.8 | 0.75 | 1.5 | 2018-03-26 | 11:30 | 2 | 35 | 11.2 | 0.75 | 1.5
2018-04-03 | 14:15 | 2.4 | 36.3 | 10.66 | 0.6 | 1.2 | 2018-04-03 | 14:15 | 1.9 | 37.9 | 10.24 | 0.5 | 1
2018-04-09 | 11:30 | 2.4 | 36.8 | 11.6 | 0.75 | 1.5 | 2018-04-09 | 11:30 | 1.9 | 36.9 | 12 | 0.75 | 1.5
2018-04-16 | 12:00 | 2.4 | 36.4 | 11 | 0.7 | 1.4 | 2018-04-16 | 12:00 | 1.8 | 38 | 10.9 | 0.7 | 1.4
2018-04-23 | 11:45 | 2.4 | 36.4 | 11.2 | 1 | 2 | 2018-04-23 | 11:45 | 1.9 | 36.9 | 11 | 1 | 2
2018-04-30 | 11:00 | 2.4 | 35.6 | 11.6 | 1 | 2 | 2018-04-30 | 11:00 | 1.8 | 35.3 | 10.2 | 1 | 2
2018-05-08 | 14:00 | 2.4 | 39.9 | 10.2 | 0.3 | 0.6 | 2018-05-08 | 14:00 | 1.9 | 42 | 10.1 | 1 | 2
2018-05-14 | 14:00 | 2.2 | 38.5 | 11.91 | 1 | 2 | 2018-05-14 | 14:00 | 1.9 | 39.1 | 10.41 | 1.1 | 2.2
2018-05-21 | 15:00 | 2.4 | 39 | 11.6 | 0.25 | 0.5 | 2018-05-21 | 15:00 | 1.9 | 39.1 | 11.8 | 1 | 2
2018-05-29 | 10:00 | 2.4 | 36.7 | 12.1 | 1 | 2 | 2018-05-29 | 10:00 | 1.8 | 37.4 | 11.1 | 1 | 2
2018-06-04 | 15:00 | 2.4 | 36.9 | 11.2 | 0.5 | 1 | 2018-06-04 | 15:00 | 1.8 | 37.8 | 10.8 | 0.5 | 1
2018-06-11 | 9:00 | 2.4 | 38.7 | 11.2 | 1.5 | 3 | 2018-06-11 | 9:00 | 1.8 | 39.9 | 11.4 | 1 | 2
2018-06-18 | 14:00 | 2.4 | 38.7 | 12.2 | 0.6 | 1.2 | 2018-06-18 | 14:00 | 2 | 38.7 | 10.8 | 0.7 | 1.4
2018-06-25 | 13:30 | 2.4 | 35.8 | 10.8 | 0.25 | 0.5 | 2018-06-25 | 13:30 | 1.8 | 41.2 | 10.4 | 1 | 2
2018-07-02 | 11:30 | 2.4 | 40 | 11.6 | 1 | 2 | 2018-07-02 | 11:30 | 2 | 40.2 | 11.2 | 1.1 | 2.2
2018-07-09 | 11:00 | 2.4 | 38.8 | 11 | 1 | 2 | 2018-07-09 | 11:00 | 2 | 40 | 10.8 | 1.2 | 2.4
2018-07-16 | 14:00 | 2.4 | 40.4 | 11.4 | 0.4 | 0.8 | 2018-07-16 | 14:00 | 2 | 40.2 | 12 | 0.5 | 1
2018-07-23 | 13:15 | 2.3 | 42.2 | 11.25 | 0.6 | 1.2 | 2018-07-23 | 13:15 | 2 | 43.6 | 10.73 | 1 | 2
2018-07-30 | 11:50 | 2.4 | 39.7 | 12.2 | 0.5 | 1 | 2018-07-30 | 11:50 | 2 | 40.6 | 11.1 | 0.5 | 1
2018-08-06 | 14:30 | 2.4 | 39.6 | 11.9 | 0.5 | 1 | 2018-08-06 | 14:30 | 2 | 42.5 | 10.2 | 0.5 | 1
2018-08-13 | 12:15 | 2.4 | 39.1 | 11.3 | 0.75 | 1.5 | 2018-08-13 | 12:15 | 2 | 40.1 | 12.2 | 0.5 | 1
2018-08-20 | 10:45 | 2.4 | 33.8 | 11.94 | 0.7 | 1.4 | 2018-08-20 | 10:45 | 2 | 39.7 | 12.32 | 1 | 2
2018-08-28 | 15:50 | 2.4 | 38.5 | 12.05 | 1.1 | 2.2 | 2018-08-28 | 15:50 | 2 | 39.5 | 11.45 | 1 | 2
2018-09-03 | 15:15 | 2.4 | 36.6 | 11.49 | 1 | 2 | 2018-09-03 | 15:15 | 2 | 38.8 | 11.64 | 0.9 | 1.8
2018-09-10 | 14:30 | 2.4 | 36.3 | 11.9 | 0.75 | 1.6 | 2018-09-10 | 14:30 | 2 | 35.8 | 10.8 | 0.5 | 1
2018-09-17 | 14:00 | 2 | 39.2 | 10.6 | 0.5 | 1 | 2018-09-17 | 14:00 | 2 | 39.4 | 11.2 | 1 | 2
2018-09-24 | 14:00 | 2.4 | 37.3 | 12 | 0.5 | 1 | 2018-09-24 | 14:00 | 2 | 38.2 | 11.5 | 1 | 2
2018-10-01 | 12:15 | 2.4 | 36 | 12.2 | 0.7 | 1.4 | 2018-10-01 | 12:15 | 2 | 37.2 | 11.7 | 0.6 | 1.2
2018-10-08 | 12:30 | 2.4 | 36.3 | 11.9 | 1 | 2 | 2018-10-08 | 12:30 | 2 | 35.8 | 10.8 | 0.75 | 1.5
2018-10-15 | 14:45 | 2.4 | 36.6 | 13.3 | 0.7 | 1.4 | 2018-10-15 | 14:45 | 2 | 33.6 | 10.5 | 0.7 | 1.4
2018-10-22 | 14:30 | 2.4 | 36.4 | 13.2 | 0.6 | 1.2 | 2018-10-22 | 14:30 | 2 | 38.2 | 9.95 | 1 | 2
2018-10-29 | 12:00 | 2.4 | 35.6 | 13.5 | 1 | 2 | 2018-10-29 | 12:00 | 2 | 31.3 | 11.58 | 0.5 | 1
2018-11-05 | 14:00 | 2.4 | 36.2 | 12.5 | 0.75 | 1.5 | 2018-11-05 | 14:00 | 2 | 33.6 | 12 | 1 | 2
2018-11-12 | 12:00 | 2.4 | 34.2 | 12.8 | 0.7 | 1.4 | 2018-11-12 | 12:00 | 2 | 37.5 | 12.3 | 0.7 | 1.4
2018-11-18 | 12:00 | 2.4 | 33.5 | 12 | 0.6 | 1.2 | 2018-11-19 | 12:00 | 2 | 31.6 | 12.1 | 0.6 | 1.2
2018-11-26 | 13:30 | 2.4 | 35.3 | 13.04 | 1 | 2 | 2018-11-26 | 13:30 | 2 | 35 | 11.46 | 1.1 | 2.2
2018-12-03 | 11:45 | 2.4 | 35.1 | 11.2 | 0.6 | 1.2 | 2018-12-03 | 11:45 | 1.8 | 29.9 | 10.1 | 0.5 | 1
2018-12-10 | 14:00 | 2.4 | 34.7 | 13.6 | 0.5 | 1 | 2018-12-10 | 14:00 | 1.8 | 27 | 9.9 | 0.5 | 1
2018-12-17 | 14:00 | 2.4 | 36.1 | 13.8 | 1 | 2 | 2018-12-17 | 14:00 | 1.8 | 36.6 | 9.9 | 0.7 | 1.5
2018-12-24 | 10:30 | 2.5 | 34.6 | 12.4 | 0.8 | 1.6 | 2018-12-24 | 10:30 | 1.8 | 35.8 | 10.4 | 0.6 | 1.2
2018-12-31 | 12:45 | 2.5 | 32.4 | 11.78 | 1.1 | 2.2 | 2018-12-31 | 12:45 | 1.8 | 36.8 | 10.32 | 0.7 | 1.4
2019-01-07 | 14:10 | 2.4 | 33.8 | 11.37 | 0.8 | 1.6 | 2019-01-07 | 14:10 | 1.8 | 34.7 | 10.12 | 1 | 2
2019-01-14 | 11:30 | 2.6 | 34.1 | 12.5 | 1 | 2 | 2019-01-14 | 11:30 | 1.8 | 37.4 | 9.85 | 1 | 2
2019-01-21 | 13:00 | 2.6 | 32.6 | 11.6 | 1 | 2 | 2019-01-21 | 13:00 | 1.8 | 34.8 | 10 | 0.5 | 1
2019-01-28 | 12:00 | 2.4 | 32.5 | 14.4 | 0.5 | 1 | 2019-01-28 | 12:00 | 1.8 | 28.2 | 10.3 | 0.25 | 0.6
2019-02-04 | 13:30 | 2.5 | 34.7 | 11.8 | 0.5 | 1 | 2019-02-04 | 13:30 | 1.8 | 36.7 | 10 | 1 | 2
2019-02-11 | 10:00 | 2.6 | 33.9 | 12.6 | 0.75 | 1.5 | 2019-02-11 | 10:00 | 1.8 | 36.7 | 10.7 | 0.75 | 1.5
2019-02-18 | 12:00 | 2.4 | 34.4 | 11.4 | 0.5 | 1 | 2019-02-18 | 12:00 | 1.8 | 37.7 | 11.1 | 1 | 2
2019-02-25 | 11:20 | 2.4 | 37.5 | 13.54 | 1 | 2 | 2019-02-25 | 11:20 | 1.8 | 36.2 | 11.8 | 1 | 2
2019-03-04 | 11:45 | 2.4 | 32.8 | 12.9 | 0.75 | 1.5 | 2019-03-04 | 11:45 | 1.8 | 32.4 | 1.8 | 0.75 | 1.5
2019-03-11 | 13:55 | 2.4 | 33.9 | 11.61 | 0.8 | 1.6 | 2019-03-11 | 13:55 | 1.8 | 35.4 | 12.89 | 1 | 2
2019-03-18 | 11:30 | 2.5 | 35.6 | 12 | 0.75 | 1.5 | 2019-03-18 | 11:30 | 1.7 | 37 | 10.8 | 1 | 2
2019-03-25 | 14:15 | 2.4 | 35.4 | 12.75 | 1.1 | 2.2 | 2019-03-25 | 14:15 | 1.8 | 33.8 | 10.75 | 0.9 | 1.8
2019-04-01 | 9:15 | 2.4 | 29.7 | 13.1 | 0.5 | 1 | 2019-04-01 | 9:15 | 1.6 | 34.8 | 12.1 | 0.5 | 1
2019-04-08 | 11:30 | 2.4 | 34.2 | 12.95 | 0.25 | 0.5 | 2019-04-08 | 11:30 | 1.7 | 37 | 10.3 | 0.75 | 1.5
2019-04-15 | 13:30 | 2.4 | 34.1 | 13.6 | 0.75 | 1.5 | 2019-04-15 | 13:30 | 1.7 | 29.7 | 8.8 | 0.25 | 0.5
2019-04-23 | 12:05 | 2.3 | 35.8 | 35.53 | 0.9 | 1.8 | 2019-04-23 | 12:05 | 1.7 | 36.4 | 12.36 | 0.9 | 1.8
2019-04-29 | 11:10 | 2.4 | 35.8 | 12.59 | 1 | 2 | 2019-04-29 | 11:10 | 1.7 | 35.5 | 12.34 | 1 | 2
2019-05-07 | 11:00 | 2.4 | 31 | 12 | 0.5 | 1 | 2019-05-07 | 11:00 | 1.8 | 37.8 | 11 | 1 | 2
2019-05-13 | 13:15 | 2.3 | 37.2 | 12.66 | 1 | 2 | 2019-05-13 | 13:15 | 1.8 | 38.7 | 11.76 | 1 | 2
2019-05-20 | 9:45 | 2.3 | 35.8 | 13.1 | 1.2 | 2.4 | 2019-05-20 | 9:45 | 1.7 | 38.1 | 12.23 | 1 | 2
2019-05-28 | 13:30 | 2.3 | 36 | 12.07 | 0.8 | 1.6 | 2019-05-28 | 13:30 | 1.8 | 37.2 | 11.43 | 0.6 | 1.2
2019-06-03 | 11:30 | 2.4 | 37.6 | 12.1 | 0.75 | 1.5 | 2019-06-03 | 11:30 | 1.7 | 39.1 | 10.9 | 0.75 | 1.5
2019-06-10 | 14:30 | 2.4 | 34.6 | 10.68 | 0.9 | 1.8 | 2019-06-10 | 14:30 | 1.6 | 33.6 | 19.8 | 1 | 2
2019-06-17 | 13:30 | 2.4 | 35.9 | 11.9 | 0.5 | 1 | 2019-06-17 | 14:00 | 1.7 | 32.9 | 10.8 | 0.75 | 1.5
2019-06-24 | 15:00 | 2.4 | 36.1 | 9.7 | 0.8 | 1.6 | 2019-06-24 | 15:30 | 1.7 | 39.2 | 10.87 | 1.2 | 2.4
2019-07-01 | 11:20 | 2.4 | 34.3 | 11.42 | 1.2 | 2.4 | 2019-07-01 | 11:30 | 1.7 | 37.3 | 11.09 | 0.5 | 1
2019-07-08 | 13:15 | 2.3 | 36.7 | 10.36 | 1.2 | 2.4 | 2019-07-08 | 13:15 | 1.6 | 35.4 | 10.26 | 0.5 | 1
2019-07-15 | 9:45 | 2.3 | 36.6 | 11.9 | 1.2 | 2.4 | 2019-07-15 | 9:45 | 1.7 | 35.9 | 10.91 | 0.5 | 1
2019-07-22 | 13:30 | 2.3 | 38.7 | 10.31 | 1.1 | 2.2 | 2019-07-22 | 13:30 | 1.6 | 40.1 | 10.98 | 0.5 | 1
2019-07-29 | 12:00 | 2.2 | 38.8 | 11.54 | 0.5 | 1 | 2019-07-29 | 12:00 | 1.6 | 37.9 | 10.53 | 1 | 2
2019-08-06 | 13:25 | 2.3 | 36.8 | 10.47 | 1 | 2 | 2019-08-05 | 12:00 | 1.7 | 39.4 | 10.81 | 0.5 | 1
2019-08-12 | 15:30 | 2.3 | 35.2 | 11.61 | 1.1 | 2.2 | 2019-08-12 | 15:30 | 1.7 | 37.4 | 10.92 | 0.7 | 1.4
2019-08-19 | 13:30 | 2.2 | 38.3 | 11.2 | 0.6 | 1.2 | 2019-08-19 | 13:30 | 1.7 | 39.6 | 11.02 | 0.25 | 0.5
2019-08-28 | 14:00 | 2.2 | 39.2 | 10.94 | 0.5 | 1 | 2019-08-28 | 14:00 | 1.6 | 39.4 | 10.9 | 0.5 | 1
2019-09-02 | 15:35 | 2.2 | 36.4 | 11.27 | 1 | 2 | 2019-09-02 | 15:35 | 1.6 | 38 | 11.28 | 0.6 | 1.2
2019-09-10 | 11:15 | 2.4 | 37.9 | 10.8 | 1 | 2 | 2019-09-10 | 11:15 | 1.6 | 38.9 | 11.7 | 0.5 | 1
2019-09-16 | 15:30 | 2.2 | 37.8 | 12.6 | 1 | 2 | 2019-09-16 | 15:30 | 1.6 | 39.1 | 12 | 0.6 | 1.2
2019-09-23 | 13:45 | 2.2 | 37.9 | 12.58 | 0.7 | 1.4 | 2019-09-23 | 13:45 | 1.7 | 38.1 | 10.5 | 1 | 2
2019-09-30 | 13:45 | 2.2 | 37.9 | 12.58 | 0.7 | 1.4 | 2019-09-30 | 13:45 | 1.7 | 38.1 | 10.5 | 1 | 2
2019-10-07 | 11:45 | 2.2 | 35.2 | 11.5 | 0.75 | 1.5 | 2019-10-07 | 11:45 | 1.8 | 36.3 | 10.6 | 0.75 | 1.5
2019-10-14 | 13:45 | 2.2 | 32.2 | 10.9 | 0.5 | 1 | 2019-10-16 | 11:00 | 1.8 | 36.6 | 10.1 | 0.75 | 1.5
2019-10-21 | 14:05 | 2.4 | 35.5 | 13.2 | 0.75 | 1.5 | 2019-10-21 | 14:15 | 1.8 | 36.9 | 9.6 | 0.75 | 1.5
2019-10-28 | 13:15 | 2.2 | 34.3 | 12 | 0.5 | 1 | 2019-10-28 | 13:15 | 1.8 | 36.4 | 11.2 | 0.5 | 1
2019-11-04 | 13:30 | 2.2 | 36 | 11.1 | 0.5 | 1 | 2019-11-04 | 13:30 | 1.8 | 31.1 | 10.2 | 0.5 | 1
2019-11-11 | 11:45 | 2.2 | 32.4 | 11.67 | 0.5 | 1 | 2019-11-11 | 11:45 | 1.7 | 31.9 | 10.73 | 1 | 2
2019-11-18 | 13:15 | 2.2 | 34.5 | 13.25 | 1 | 2 | 2019-11-18 | 13:15 | 1.7 | 31.2 | 10.99 | 0.75 | 1.5
2019-11-25 | 14:15 | 2.4 | 36.4 | 14.4 | 0.5 | 1 | 2019-11-25 | 14:15 | 1.6 | 37.9 | 10.1 | 0.5 | 1
2019-12-02 | 14:30 | 2.2 | 34.9 | 12.35 | 0.5 | 1 | 2019-12-02 | 14:30 | 1.8 | 35.6 | 10.36 | 0.25 | 0.5
2019-12-10 | 14:10 | 2.4 | 33.1 | 12.9 | 0.6 | 1.2 | 2019-12-10 | 14:10 | 1.6 | 34.4 | 10.8 | 0.5 | 1
2019-12-16 | 15:10 | 2.2 | 34.4 | 14 | 0.75 | 1.5 | 2019-12-16 | 15:10 | 1.6 | 35.3 | 10.7 | 0.5 | 1
2019-12-23 | 13:30 | 2.2 | 34.6 | 13.48 | 1 | 2 | 2019-12-23 | 13:30 | 1.6 | 31.2 | 10.46 | 0.6 | 1.2
2019-12-31 | 9:00 | 2.2. | 34.9 | 12.3 | 0.3 | 0.6 | 2019-12-31 | 9:00 | 1.6 | 36.3 | 11.7 | 0.5 | 1
2020-01-06 | 15:45 | 2.2 | 34 | 13.6 | 0.5 | 1 | 2020-01-06 | 15:45 | 1.6 | 31.1 | 9.1 | 0.5 | 1
2020-01-13 | 10:45 | 2.2 | 33.1 | 12.4 | 0.75 | 1.5 | 2020-01-13 | 10:45 | 1.7 | 34.8 | 10.4 | 0.6 | 1.2
2020-01-20 | 13:20 | 2.3 | 34.8 | 12.37 | 0.9 | 1.8 | 2020-01-20 | 13:20 | 1.7 | 35.1 | 11.37 | 1 | 2
2020-01-27 | 11:00 | 2.2 | 28.5 | 10.1 | 0.5 | 1 | 2020-01-27 | 11:00 | 1.7 | 36 | 10.8 | 0.5 | 1
2020-02-03 | 9:30 | 2.4 | 33.6 | 11.3 | 0.75 | 1.5 | 2020-02-03 | 9:30 | 1.7 | 35.1 | 10.5 | 0.75 | 1.5
2020-02-12 | 11:30 | 2.4 | 31.3 | 12.3 | 0.5 | 1 | 2020-02-12 | 11:30 | 1.7 | 34.2 | 11.1 | 0.5 | 1
2020-02-17 | 10:00 | 2.4 | 33.2 | 11.2 | 0.7 | 1.5 | 2020-02-17 | 10:00 | 1.7 | 34.4 | 10.4 | 0.25 | 0.5
2020-02-24 | 14:00 | 2.4 | 34.7 | 12.7 | 0.5 | 1 | 2020-02-24 | 14:00 | 1.6 | 36.2 | 10.7 | 0.5 | 1
2020-03-02 | 14:00 | 2.4 | 34.7 | 10.6 | 1 | 2 | 2020-03-02 | 14:00 | 0.5 | 36.4 | 10.8 | 0.5 | 1
2020-03-09 | 13:30 | 2.4 | 32.5 | 11 | 0.5 | 1 | 2020-03-09 | 13:30 | 1.6 | 31 | 10 | 0.5 | 1
2020-03-16 | 11:40 | 2.3 | 35.7 | 12.8 | 0.75 | 1.5 | 2020-03-06 | 11:40 | 1.7 | 37.7 | 11.7 | 0.5 | 1
2020-03-23 | 10:30 | 2.2 | 33.8 | 11.2 | 0.5 | 1 | 2020-03-23 | 10:30 | 1.6 | 37.2 | 10.1 | 0.6 | 1.2
2020-03-30 | 14:10 | 2.2 | 33.2 | 11.5 | 0.6 | 1.2 | 2020-03-30 | 14:10 | 1.6 | 36 | 9.8 | 0.5 | 1
2020-04-06 | 11:45 | 2 | 37.2 | 10.4 | 0.75 | 1.5 | 2020-04-06 | 11:45 | 1.4 | 38.3 | 10.7 | 0.5 | 1
2020-04-16 | 9:50 | 2.4 | 36 | 11.88 | 0.75 | 1.5 | 2020-04-16 | 9:50 | 1.6 | 38.2 | 10.15 | 0.75 | 1.5
2020-04-20 | 11:40 | 2.3 | 35.5 | 12.5 | 0.8 | 1.6 | 2020-04-20 | 11:40 | 1.65 | 34.2 | 10.85 | 0.5 | 1
2020-04-27 | 13:30 | 2.1 | 36.8 | 12.11 | 0.75 | 1.5 | 2020-04-27 | 13:30 | 1.85 | 38.1 | 10.3 | 0.75 | 1.5
2020-05-04 | 14:10 | 2.2 | 34.9 | 12.68 | 0.6 | 1.2 | 2020-05-04 | 14:10 | 1.6 | 35.3 | 11.13 | 0.5 | 1
2020-05-11 | 14:00 | 2.1 | 29.7 | 14.47 | 0.75 | 1.5 | 2020-05-11 | 14:00 | 1.6 | 32.1 | 12.39 | 0.8 | 1.6
2020-05-18 | 14:20 | 2.2 | 37.9 | 12.8 | 0.8 | 1.16 | 2020-05-18 | 14:20 | 1.4 | 38.1 | 11.11 | 0.5 | 1
2020-05-26 | 10:00 | 2.1 | 34.8 | 11.51 | 0.65 | 1.3 | 2020-05-26 | 10:00 | 1.4 | 38.5 | 11.01 | 0.55 | 1.1
2020-06-01 | 10:45 | 2.4 | 38.4 | 11.2 | 0.6 | 1.2 | 2020-06-01 | 10:45 | 1.5 | 40 | 10.46 | 0.25 | 0.5
2020-06-08 | 11:45 | 2.1 | 33.8 | 12.27 | 0.5 | 1 | 2020-06-08 | 11:45 | 1.4 | 37.9 | 12.36 | 0.75 | 1.5
2020-06-15 | 9:30 | 2.2 | 37.9 | 13.15 | 0.8 | 1.6 | 2020-06-15 | 9:30 | 1.5 | 40 | 10.91 | 0.8 | 1.6
2020-06-22 | 14:15 | 2.2 | 38.7 | 11.35 | 1 | 2 | 2020-06-22 | 14:15 | 1.3 | 40.1 | 9.6 | 0.9 | 1.8
2020-06-29 | 11:10 | 2.2 | 35.6 | 12.39 | 0.4 | 0.8 | 2020-06-29 | 11:10 | 1.5 | 35.7 | 10.17 | 0.5 | 1
2020-07-06 | 11:30 | 2 | 35.4 | 13.21 | 0.75 | 1.5 | 2020-07-06 | 11:30 | 1.1 | 38.7 | 12.13 | 0.75 | 1.5
2020-07-13 | 15:35 | 2.2 | 36.4 | 11.1 | 0.5 | 1 | 2020-07-13 | 15:35 | 1.4 | 38.8 | 10.95 | 0.75 | 1.5
2020-07-20 | 14:20 | 2 | 37.1 | 12.61 | 0.75 | 1.5 | 2020-07-20 | 14:20 | 1.4 | 37.4 | 11.77 | 0.6 | 1.2
2020-07-27 | 11:00 | 2.4 | 35.8 | 12.3 | 0.25 | 0.5 | 2020-07-27 | 11:00 | 1.6 | 35.7 | 9.8 | 0.4 | 0.8
2020-08-03 | 12:00 | 2.2 | 37.9 | 12.12 | 0.9 | 1.8 | 2020-08-03 | 12:00 | 1.4 | 38.3 | 11.57 | 0.6 | 1.2
2020-08-10 | 14:05 | 2.2 | 39.1 | 12.65 | 0.75 | 1.5 | 2020-08-10 | 14:05 | 1.4 | 40.1 | 10.6 | 0.75 | 1.5
2020-08-17 | 10:45 | 2.2 | 36.8 | 10.9 | 0.6 | 1.2 | 2020-08-17 | 10:45 | 1.4 | 38.6 | 9.5 | 0.6 | 1.2
2020-08-24 | 11:00 | 2.1 | 32.9 | 11.66 | 0.8 | 1.6 | 2020-08-24 | 11:00 | 1.2 | 36.7 | 10.48 | 0.75 | 1.5
2020-09-01 | 14:00 | 2.2 | 36.8 | 11.55 | 0.75 | 1.5 | 2020-09-01 | 14:00 | 1.4 | 39.6 | 11.05 | 0.25 | 0.5
2020-09-07 | 11:45 | 2.2 | 36.4 | 11.05 | 0.75 | 1.5 | 2020-09-07 | 11:45 | 1.4 | 37.3 | 9.15 | 0.75 | 1.5
2020-09-14 | 11:50 | 2.3 | 38.6 | 11.4 | 0.75 | 1.5 | 2020-09-14 | 11:50 | 1.5 | 40.4 | 10.2 | 0.75 | 1.5
2020-09-21 | 9:30 | 2.1 | 35.4 | 12.12 | 1 | 2 | 2020-09-21 | 223:12 | 1.5 | 37.9 | 12.28 | 0.9 | 1.8
2020-09-28 | 11:00 | 2 | 36.1 | 12.3 | 0.5 | 1 | 2020-09-28 | 11:00 | 1.6 | 38.4 | 10.6 | 0.75 | 1.5
2020-10-05 | 13:45 | 2 | 35.1 | 11.6 | 1 | 2 | 2020-10-05 | 13:45 | 1.6 | 38.1 | 9.98 | 0.9 | 1.8
2020-10-12 | 13:50 | 2 | 35.1 | 12.55 | 1 | 2 | 2020-10-12 | 13:50 | 1.4 | 36.3 | 10.44 | 0.9 | 1.8
2020-10-19 | 11:30 | 2.2 | 33.5 | 11.2 | 0.5 | 1 | 2020-10-19 | 11:30 | 1.6 | 31.2 | 9.95 | 0.25 | 0.5
2020-10-26 | 13:00 | 2 | 34.9 | 10.9 | 0.8 | 1.6 | 2020-10-26 | 13:00 | 1.5 | 37.2 | 11 | 0.5 | 1
2020-11-03 | 11:45 | 2 | 33.9 | 11 | 0.75 | 1.5 | 2020-11-03 | 11:45 | 1.5 | 37.6 | 9.4 | 0.5 | 1
2020-11-09 | 9:45 | 2.1 | 34.6 | 13.27 | 0.9 | 1.8 | 2020-11-09 | 9:45 | 1.9 | 36.7 | 12.16 | 1.1 | 2.2
2020-11-16 | 13:30 | 2.6 | 33.6 | 14.04 | 0.75 | 1.5 | 2020-11-16 | 13:30 | 2 | 37.7 | 12.63 | 0.9 | 1.8
2020-11-23 | 13:45 | 2.1 | 34.1 | 10.5 | 0.6 | 1.2 | 2020-11-23 | 13:45 | 1.8 | 36.4 | 11 | 0.25 | 0.5
2020-11-30 | 14:00 | 2.1 | 34.6 | 11.7 | 0.75 | 1.5 | 2020-11-30 | 14:00 | 1.8 | 36.2 | 9.7 | 0.5 | 1
2020-12-08 | 13:45 | 2 | 33.8 | 10.32 | 0.75 | 1.5 | 2020-12-08 | 13:45 | 1.2 | 25 | 6.25 | 1.1 | 2.2
2020-12-14 | 11:10 | 2.2 | 36.1 | 13.51 | 0.75 | 1.5 | 2020-12-14 | 11:10 | 1.2 | 38.1 | 12.61 | 0.5 | 1
2020-12-21 | 13:50 | 2.2 | 35.4 | 10.68 | 0.7 | 1.4 | 2020-12-21 | 13:50 | 1.2 | 32.6 | 9.43 | 0.3 | 0.6
2020-12-29 | 14:00 | 2.1 | 35.5 | 11.65 | 0.6 | 1.2 | 2020-12-29 | 14:00 | 1 | 33.4 | 9.24 | 0.5 | 1
2021-01-04 | 14:50 | 2 | 33.7 | 12.47 | 0.6 | 1.2 | 2021-01-04 | 14:50 | 1 | 34 | 10.67 | 0.6 | 1.2
2021-01-11 | 14:05 | 2.2 | 33.5 | 12.5 | 0.8 | 1.6 | 2021-01-11 | 14:05 | 1 | 32.9 | 10 | 0.6 | 1.2
2021-01-18 | 11:00 | 2.3 | 32.4 | 13.54 | 0.5 | 1 | 2021-01-18 | 11:00 | 1.1 | 34.9 | 13.29 | 0.5 | 1
2021-01-25 | 13:30 | 2.2 | 32.5 | 11.32 | 0.8 | 1.6 | 2021-01-25 | 13:30 | 0.9 | 36.2 | 11.27 | 0.9 | 1.8
2021-02-01 | 14:15 | 2.1 | 34.6 | 12.68 | 0.6 | 1.2 | 2021-02-01 | 14:15 | 1 | 37.1 | 12.81 | 0.75 | 1.5
2021-02-08 | 14:00 | 2.2 | 32.5 | 13.3 | 0.75 | 1.5 | 2021-02-08 | 14:00 | 1.2 | 28.8 | 10.01 | 0.6 | 1.2
2021-02-15 | 14:00 | 2.1 | 35.5 | 12.03 | 0.9 | 1.8 | 2021-02-15 | 14:00 | 1.1 | 37.5 | 11.02 | 0.8 | 1.6
2021-02-22 | 12:00 | 2.1 | 34.3 | 11.5 | 0.8 | 1.6 | 2021-02-22 | 12:00 | 1.1 | 37 | 13.4 | 0.5 | 1
2021-03-01 | 9:00 | 2.2 | 33.3 | 12.03 | 0.5 | 1 | 2021-03-01 | 9:00 | 1.2 | 36 | 10.75 | 0.7 | 1.4
2021-03-08 | 9:45 | 2.2 | 32.6 | 11.45 | 1 | 2 | 2021-03-08 | 9:45 | 1.2 | 35.9 | 9.8 | 1 | 2
2021-03-15 | 14:30 | 2 | 36.4 | 12.51 | 0.75 | 1.5 | 2021-03-15 | 14:30 | 0.9 | 34.3 | 12.57 | 0.5 | 1
2021-03-22 | 14:00 | 2 | 37.6 | 12.2 | 1.25 | 2.5 | 2021-03-22 | 14:00 | 0.9 | 39.9 | 8.9 | 1.25 | 2.5
2021-03-29 | 9:00 | 2 | 22.7 | 6.8 | 0 | 0 | 2021-03-29 | 9:00 | 0.9 | 38.7 | 11.4 | 0.8 | 1.6
2021-03-31 | 9:00 | 2 | 29.8 | 10.2 | 0.25 | 0.5 | 2021-03-29 | 9:00 | 0.9 | 38.7 | 11.4 | 0.8 | 1.6
2021-04-06 | 13:45 | 1.9 | 33.7 | 13.11 | 0.75 | 1.5 | 2021-04-06 | 13:45 | 0.9 | 36.6 | 12.77 | 0.8 | 1.6
2021-04-13 | 14:20 | 1.9 | 36.7 | 10.52 | 0.9 | 1.8 | 2021-04-13 | 14:20 | 0.8 | 39.6 | 11.2 | 1.1 | 2.2
2021-04-19 | 12:00 | 2 | 36.8 | 12.5 | 0.8 | 1.6 | 2021-04-19 | 12:00 | 0.85 | 39.9 | 10.4 | 1 | 2
2021-04-26 | 12:15 | 1.9 | 35.3 | 13.03 | 0.75 | 1.5 | 2021-04-26 | 12:15 | 0.85 | 39.3 | 12.85 | 0.6 | 1.2
2021-05-05 | 11:15 | 1.9 | 34.4 | 12.56 | 0.6 | 1.2 | 2021-05-05 | 11:15 | 0.9 | 39.2 | 10.84 | 0.6 | 1.2
2021-05-10 | 10:45 | 1.9 | 36.9 | 11.4 | 0.8 | 1.6 | 2021-05-10 | 10:45 | 1 | 39.6 | 10.6 | 0.6 | 1.2
2021-05-17 | 14:15 | 1.8 | 36.4 | 12.94 | 0.9 | 1.8 | 2021-05-17 | 14:15 | 0.8 | 53.7 | 12.5 | 0.5 | 1
2021-05-24 | 14:00 | 1.8 | 38.8 | 12.35 | 1 | 2 | 2021-05-24 | 14:00 | 0.8 | 38.2 | 10.69 | 1.1 | 2.2
2021-06-01 | 15:00 | 1.7 | 37.1 | 11.25 | 0.6 | 1.2 | 2021-06-01 | 15:00 | 0.8 | 39.1 | 11.75 | 0.5 | 1
2021-06-07 | 14:15 | 1.8 | 37.6 | 10.28 | 1.8 | 2.6 | 2021-06-07 | 14:15 | 0.8 | 38.6 | 10.87 | 1 | 2
2021-06-14 | 12:30 | 1.9 | 38.4 | 12 | 0.75 | 1.5 | 2021-06-14 | 12:30 | 0.8 | 38.7 | 11.8 | 0.5 | 1
2021-06-21 | 11:45 | 1.8 | 39.9 | 11.4 | 0.5 | 1 | 2021-06-21
2021-06-28 | 14:50 | 1.8 | 38.4 | 10.2 | 0.75 | 1.5 | 2021-06-28 | 14:50 | 0.8 | 1.2 | 0 | 0 | 0
2021-07-05 | 14:00 | 1.9 | 40.4 | 10.72 | 0.8 | 1.6 | 2021-07-05 | 14:00 | 0 | 24.7 | 1.24 | 0 | 0
2021-07-12 | 13:30 | 1.9 | 39.5 | 9.98 | 0.75 | 1.5 | 2021-07-12 | 13:30 | 0 | 22 | 1.2 | 0 | 0
2021-07-19 | 14:35 | 2 | 39.4 | 11.8 | 0.5 | 1 | 2021-07-19 | 14:35 | 0 | 24 | 1 | 0 | 0
2021-07-26 | 15:45 | 1.9 | 40.4 | 11.9 | 0.75 | 1.5 | 2021-07-26 | 15:45 | 0.9 | 23.8 | 0.69 | 0 | 0
2021-08-16 | 11:00 | 2.1 | 19.1 | 4.59 | 0 | 0 | 2021-08-16 | 11:00 | 1.2 | 15.5 | 1.31 | 0 | 0
2021-08-23 | 14:15 | 2 | 38.9 | 11 | 0.75 | 1.5 | 2021-08-23 | 14:15 | 1.2 | 20.9 | 1.2 | 0 | 0
2021-08-31 | 13:40 | 2.2 | 38.3 | 12.41 | 1.2 | 2.4 | 2021-08-31 | 13:40 | 1.2 | 17.7 | 1.29 | 0 | 0
2021-09-06 | 14:00 | 2.2 | 39.3 | 10.8 | 1.25 | 2.5 | 2021-09-06 | 14:00 | 1.1 | 19.5 | 1.3 | 0 | 0
2021-09-13 | 14:15 | 2.1 | 38 | 11.96 | 1 | 2 | 2021-09-13 | 14:15 | 1.2 | 17.4 | 0.95 | 0 | 0
2021-09-20 | 14:30 | 2.1 | 32.1 | 10.35 | 0.5 | 1 | 2021-09-20 | 14:30 | 1.3 | 21 | 0.54 | 0 | 0
2021-09-27 | 9:00 | 2 | 35.8 | 11.15 | 0.75 | 1.5 | 2021-09-27 | 9:00 | 1.2 | 32.7 | 9.95 | 0.25 | 0.6
2021-10-04 | 15:00 | 1.9 | 36.6 | 11.19 | 0.25 | 0.5 | 2021-10-04 | 15:00 | 1.8 | 37.9 | 11.84 | 0.75 | 1.5
2021-10-11 | 9:45 | 2 | 35 | 12.1 | 0.75 | 1.5 | 2021-10-11 | 9:45 | 1.8 | 38.3 | 11.4 | 0.6 | 1.25
2021-10-18 | 14:15 | 2 | 35.9 | 12.7 | 1 | 2 | 2021-10-18 | 14:15 | 1.8 | 36.5 | 9.66 | 0.75 | 1.5
2021-10-28 | 9:00 | 2 | 33.8 | 10.6 | 0.6 | 1.2 | 2021-10-28 | 9:00 | 1.9 | 37 | 11.1 | 0.5 | 1
2021-11-01 | 15:15 | 1.9 | 32.7 | 10.77 | 0.5 | 1 | 2021-11-01 | 15:15 | 1.8 | 33.2 | 9.55 | 0.75 | 1.5
2021-11-08 | 9:30 | 2 | 34.8 | 12.2 | 1 | 2 | 2021-11-08 | 9:30 | 1.8 | 37.8 | 10.95 | 1 | 2
2021-11-15 | 12:40 | 1.9 | 35.9 | 11.73 | 0.5 | 1 | 2021-11-15 | 12:40 | 1.8 | 38 | 10.84 | 1 | 2
2021-11-22 | 9:20 | 2 | 34.4 | 12.67 | 0.7 | 1.4 | 2021-11-22 | 9:20 | 1.8 | 35.5 | 10.31 | 0.9 | 1.8
2021-11-29 | 10:50 | 1.8 | 33.1 | 12.55 | 0.5 | 1 | 2021-11-29 | 10:50 | 1.8 | 34.9 | 10.71 | 0.75 | 1.5
2021-12-07 | 9:00 | 2 | 33.8 | 12.48 | 0.9 | 1.8 | 2021-12-07 | 9:00 | 1.8 | 30.1 | 10.52 | 0.5 | 1
2021-12-13 | 14:50 | 2 | 35.8 | 11.86 | 0.6 | 1.2 | 2021-12-13 | 14:50 | 1.8 | 37.1 | 10.01 | 0.8 | 1.6
2021-12-20 | 14:40 | 2 | 35.8 | 10.73 | 0.7 | 1.4 | 2021-12-20 | 14:40 | 1.8 | 33.2 | 8.99 | 0.8 | 1.6
2021-12-29 | 14:20 | 1.8 | 36.4 | 11.6 | 0.6 | 1.2 | 2021-12-29 | 14:20 | 1.8 | 36.7 | 10.5 | 0.7 | 1.4
2022-01-03 | 13:45 | 2 | 35.6 | 12.38 | 1 | 2 | 2022-01-03 | 13:45 | 1.7 | 36.6 | 10.7 | 1 | 2
2022-01-10 | 14:20 | 1.7 | 34.6 | 11.4 | 0.6 | 1.2 | 2022-01-10 | 14:20 | 1.7 | 35.2 | 9.75 | 1 | 2
2022-01-17 | 13:30 | 2 | 34 | 12.1 | 0.75 | 1.5 | 2022-01-17 | 13:30 | 2 | 35.9 | 10 | 0.25 | 0.5
2022-01-24 | 14:45 | 2 | 35.2 | 11.92 | 0.5 | 1 | 2022-01-24 | 14:45 | 1.7 | 36.7 | 10.76 | 0.75 | 1.5
2022-01-31 | 12:15 | 2 | 34.6 | 10.47 | 0.8 | 1.6 | 2022-01-31 | 12:15 | 1.8 | 31.3 | 11.73 | 1 | 2
2022-02-07 | 13:30 | 2 | 33.2 | 10.5 | 0.75 | 1.5 | 2022-02-07 | 13:30 | 1.7 | 31.5 | 11.05 | 0.6 | 1.2
2022-02-14 | 14:25 | 2.2 | 29.6 | 11.89 | 0.7 | 1.4 | 2022-02-14 | 14:25 | 1.8 | 35.6 | 12.05 | 0.6 | 1.2
2022-02-23 | 9:30 | 1.9 | 34.6 | 12.5 | 0.9 | 1.8 | 2022-02-23 | 9:30 | 1.7 | 37.4 | 12 | 0.8 | 1.6
2022-02-28 | 14:00 | 1.9 | 34.8 | 12.39 | 0.7 | 1.4 | 2022-02-28 | 14:00 | 1.7 | 36.8 | 11.77 | 1 | 2
2022-03-07 | 14:30 | 1.9 | 35.6 | 12.7 | 0.6 | 1.2 | 2022-03-07 | 14:30 | 1.7 | 36.5 | 11.2 | 0.8 | 1.6
2022-03-14 | 12:00 | 1.9 | 37.6 | 12.7 | 1 | 2 | 2022-03-14 | 12:00 | 1.8 | 38.9 | 11.11 | 0.7 | 1.4
2022-03-25 | 14:45 | 1.9 | 37.5 | 11.35 | 0.75 | 1.5 | 2022-03-25 | 45:36 | 1.9 | 38.5 | 10.81 | 1 | 2
2022-03-28 | 11:15 | 2 | 35.7 | 11.78 | 1 | 2 | 2022-03-28 | 11:15 | 1.7 | 37.5 | 11.23 | 0.8 | 1.6
2022-04-04 | 14:45 | 2 | 35.5 | 10.2 | 0.8 | 1.6 | 2022-04-04 | 14:45 | 1.7 | 38.1 | 11.4 | 1 | 2
2022-04-11 | 13:45 | 1.9 | 36.6 | 11.35 | 0.6 | 1.2 | 2022-04-11 | 13:45 | 1.8 | 38 | 10.36 | 0.7 | 1.4
2022-04-20 | 14:15 | 1.8 | 36.9 | 10.7 | 0.75 | 1.5 | 2022-04-20 | 1:15 | 1.7 | 39.7 | 11.32 | 1 | 2
2022-04-25 | 13:30 | 1.9 | 36.6 | 12.06 | 1.1 | 2.2 | 2022-04-25 | 13:30 | 1.7 | 36.7 | 11.18 | 0.7 | 1.4
2022-05-03 | 11:00 | 1.8 | 35.8 | 11.65 | 1 | 2 | 2022-05-03 | 11:00 | 1.7 | 37.7 | 10.3 | 1.1 | 2.2
2022-05-10 | 14:45 | 1.5 | 38.4 | 10.5 | 1 | 2 | 2022-05-10 | 14:45 | 1.7 | 39.8 | 10.9 | 1 | 2
2022-05-16 | 14:15 | 1.6 | 38.4 | 10.4 | 0.75 | 1.5 | 2022-05-16 | 14:15 | 1.7 | 41.2 | 9.8 | 0.8 | 1.6
2022-05-23 | 11:40 | 1.6 | 39.1 | 11.86 | 0.6 | 1.2 | 2022-05-23 | 11:40 | 1.7 | 41.2 | 10.85 | 1.2 | 2.2
2022-05-31 | 12:15 | 1.9 | 36.6 | 11.25 | 0.7 | 1.4 | 2022-05-31 | 12:15 | 1.7 | 40 | 11.8 | 1 | 2
2022-06-06 | 13:15 | 1.9 | 36.3 | 11.52 | 0.8 | 1.6 | 2022-06-06 | 13:15 | 1.7 | 39.3 | 11.45 | 1.1 | 2.2
2022-06-13 | 10:50 | 1.8 | 37.1 | 11.82 | 0.75 | 1.5 | 2022-06-13 | 10:50 | 1.7 | 33.2 | 9.92 | 0.5 | 1
2022-06-20 | 14:30 | 1.8 | 38.3 | 10.46 | 1 | 2 | 2022-06-20 | 14:30 | 1.8 | 39.6 | 10.49 | 1.1 | 2.2
2022-06-28 | 15:20 | 1.9 | 37.7 | 11.11 | 1 | 2 | 2022-06-28 | 15:20 | 1.7 | 39.4 | 10.66 | 1 | 2
2022-07-04 | 14:00 | 1.9 | 37.1 | 10.75 | 1 | 2 | 2022-07-04 | 14:00 | 1.8 | 39.3 | 11.52 | 1 | 2
2022-07-11 | 14:30 | 1.9 | 35.5 | 10.37 | 1 | 2 | 2022-07-11 | 14:30 | 1.7 | 41.9 | 10.43 | 1 | 2
2022-07-19 | 9:30 | 1.95 | 34.3 | 10.55 | 0.7 | 1.4 | 2022-07-19 | shutdown
2022-07-25 | 15:00 | 2 | 36.9 | 10.8 | 0.7 | 1.4 | 2022-07-25 | 15:00 | 1.6 | 27.6 | 3.06 | 0 | 0
2022-08-01 | 12:20 | 2 | 37.9 | 10.56 | 1 | 2 | 2022-08-01 | 12:20 | 1.5 | 40.9 | 9.74 | 1.1 | 2.2
2022-08-08 | 14:00 | 2 | 38.2 | 10.8 | 1 | 2 | 2022-08-08 | 14:00 | 1.5 | 40.5 | 11.8 | 1 | 2
2022-08-15 | 14:05 | 2 | 39.6 | 11.5 | 0.9 | 1.8 | 2022-08-15 | 14:05 | 1.6 | 40 | 11.5 | 0.6 | 1.2
2022-08-22 | 14:00 | 1.8 | 37.3 | 9.75 | 0.8 | 1.6 | 2022-08-22 | 14:00 | 1.6 | 34.6 | 10 | 0.6 | 1.2
2022-08-31 | 15:45 | 1.9 | 39.2 | 11.54 | 1 | 2 | 2022-08-31 | 15:45 | 1.6 | 40.4 | 11.21 | 1 | 2
2022-09-05 | 16:00 | 1.9 | 40.2 | 11.2 | 1 | 2 | 2022-09-05 | 16:00 | 1.6 | 41.2 | 10.7 | 1 | 2
2022-09-12 | 11:30 | 2 | 38.5 | 11.91 | 1.1 | 2.2 | 2022-09-12 | 11:30 | 1.3 | 38.8 | 10.08 | 0.9 | 1.8
2022-09-20 | 15:00 | 2 | 37.3 | 12.37 | 1 | 2 | 2022-09-20 | 15:00 | 1.3 | 35.5 | 9.23 | 1 | 2
2022-09-26 | 13:30 | 2 | 35.6 | 11.46 | 1 | 2 | 2022-09-26 | 13:30 | 1.3 | 37.7 | 10.66 | 0.9 | 1.8
2022-10-03 | 14:10 | 1.8 | 36.4 | 10 | 1 | 2 | 2022-10-03 | 14:10 | 1.2 | 38.7 | 10.6 | 1 | 1
2022-10-10 | 13:45 | 1.8 | 36.7 | 11.94 | 1 | 2 | 2022-10-12 | 15:20 | 1.2 | 37.6 | 10.75 | 1.2 | 2.4
2022-10-18 | 10:35 | 1.9 | 36.2 | 12.4 | 0.9 | 1.8 | 2022-10-18 | 10:35 | 1.2 | 38.2 | 11 | 1 | 2
2022-10-24 | 13:30 | 2 | 36.4 | 12.86 | 0.9 | 1.8 | 2022-10-24 | 13:30 | 1.3 | 38.1 | 11.41 | 0.8 | 1.6
2022-10-31 | 13:55 | 1.9 | 32.4 | 10.6 | 0.7 | 1.4 | 2022-10-31 | 13:55 | 1.2 | 37.8 | 10.9 | 0.9 | 1.8
2022-11-07 | 11:35 | 2 | 36.1 | 12.09 | 1 | 2 | 2022-11-07 | 11:35 | 1.2 | 37.4 | 11.24 | 0.8 | 1.6
2022-11-14 | 14:15 | 2 | 36.6 | 12.6 | 1 | 2 | 2022-11-14 | 14:15 | 1.2 | 37.3 | 11.5 | 0.9 | 1.8
2022-11-21 | 13:35 | 1.8 | 35.6 | 12.53 | 0..8 | 1.6 | 2022-11-21 | 13:35 | 1.2 | 35.1 | 10.96 | 0.7 | 1.4
2022-11-28 | 15:00 | 1.9 | 34.6 | 12.47 | 1 | 2 | 2022-11-28 | 15:00 | 1.2 | 34.4 | 9.21 | 1.1 | 2.2
2022-12-05 | 11:05 | 2 | 35 | 11.94 | 1.1 | 2.2 | 2022-12-05 | 11:05 | 1.2 | 35.7 | 11.57 | 1.1 | 2.2
2022-12-12 |  | power cut |  |  |  |  | 2022-12-12 |  | power cut
2022-12-19 | 11:10 | 1.8 | 36.1 | 12.64 | 1 | 2 | 2022-12-19 | 11:10 | 1.1 | 37.6 | 11.54 | 1 | 2
2022-12-29 | 14:45 | 2.2 | 34.2 | 12.85 | 0.75 | 1.5 | 2022-12-29 | 14:45 | 1.2 | 36.1 | 11.94 | 0.75 | 1.5
2023-01-04 | 15:10 | 1.8 | 33.3 | 10 | 0.6 | 1.2 | 2023-01-04 | 15:10 | 1.4 | 35.4 | 9.5 | 1 | 2
2023-01-09 | 14:45 | 2 | 33.3 | 9.94 | 2 | 4 | 2023-01-09 | 14:45 | 1.6 | 35.9 | 11.24 | 1 | 2
2023-01-17 | 11:00 | wrap |  |  |  |  | 2023-01-17 | 11:00 | 1.7 | 35.3 | 10.37 | 1.2 | 2.2
2023-01-23 | 14:45 | 2 | 33.9 | 10.64 | 0.8 | 1.6 | 2023-01-23 | 14:45 | 1.4 | 36.7 | 11.25 | 1 | 2
2023-01-30 | 13:30 | [5 empty] | 2023-01-30 | 13:30 | 0.65 | 37.8 | 10.78 | 1 | 2
2023-02-07 | 11:00 | 2 | 34.6 | 11.67 | 1.2 | 2.4 | 2023-02-07 | 11:00 | 1.5 | 37.8 | 10.88 | 1 | 2
2023-02-13 | 13:00 | 2 | 34.7 | 11.14 | 1.1 | 2.2 | 2023-02-13 | 13:00 | 1.7 | 36.7 | 10.94 | 1 | 2
2023-02-20 | 14:50 | 2 | 36.8 | 9.68 | 1 | 2 | 2023-02-20 | 14:50 | 1.5 | 36.7 | 11.34 | 1 | 2
2023-02-27 | 11:15 | 2 | 37 | 10.2 | 0.5 | 1 | 2023-02-27 | 11:15 | 1.4 | 36.8 | 11.1 | 0.25 | 0.5
2023-03-06 | 15:30 | 1.9 | 35.2 | 10.91 | 1 | 2 | 2023-03-06 | 15:30 | 1.6 | 37.6 | 11.06 | 1 | 2
2023-03-13 | 14:00 | 1.9 | 35.2 | 10.8 | 1 | 2 | 2023-03-13 | 14:00 | 1.5 | 35.7 | 9.5 | 0.6 | 1.2
2023-03-20 | 14:45 | 1.9 | 32.6 | 10.58 | 0.5 | 1 | 2023-03-20 | 14:45 | 1.4 | 39.4 | 10.5 | 1 | 2
2023-03-27 | 15:15 | 1.9 | 36.3 | 11.68 | 1.2 | 2.4 | 2023-03-27 |  | R&M
2023-04-03 | 14:05 | 2 | 34.8 | 10.3 | 0.8 | 1.6 | 2023-04-03 | 14:05 | 1.2 | 37 | 10 | 0.9 | 1.8
2023-04-11 | 13:45 | 2 | 37.7 | 12.22 | 0.8 | 1.6 | 2023-04-11 | 13:45 | 1.2 | 38.5 | 9.45 | 0.8 | 1.6
2023-04-17 | 14:30 | 2 | 37.2 | 12.2 | 0.8 | 1.6 | 2023-04-17 | 14:30 | 1.3 | 38.4 | 10.1 | 1 | 2
2023-04-24 | 13:20 | 2 | 33.8 | 11.94 | 1 | 2 | 2023-04-24 | 13:20 | 1.3 | 35.2 | 8.58 | 0.9 | 1.8
2023-05-02 | 10:15 | 1.9 | 37.2 | 11.73 | 1 | 2 | 2023-05-02 | 10:15 | 1.3 | 39.2 | 11.27 | 1 | 2
2023-05-09 | 14:15 | 2 | 38.4 | 11 | 0.5 | 1 | 2023-05-09 | 14:15 | 1.2 | 41.9 | 11.7 | 1 | 2
2023-05-15 | 11:00 | 2 | 36.8 | 11.01 | 0.75 | 1.5 | 2023-05-15 | 11:00 | 1.3 | 38.4 | 10.92 | 0.75 | 1.5
2023-05-22 | 11:15 | 2 | 36.8 | 12.2 | 0.75 | 1.5 | 2023-05-22 | 11:15 | 1.2 | 39.7 | 11.01 | 0.75 | 1.5
2023-05-30 | 14:30 | 2 | 37.7 | 10.84 | 0.75 | 1.5 | 2023-05-30 | 14:30 | 1.2 | 34.7 | 10.25 | 0.5 | 1
2023-06-05 | 13:20 | 2 | 37.6 | 12.1 | 0.8 | 1.6 | 2023-06-05 | 13:20 | 1.2 | 38.3 | 10.87 | 0.7 | 1.4
2023-06-12 | 14:00 | [5 empty] | 2023-06-12 | 14:00
2023-06-19 | 14:00 | [5 empty] | 2023-06-19 | 14:00 | 1 | 41.9 | 10.89 | 1 | 2
2023-06-27 | 14:30 | [5 empty] | 2023-06-27 | 14:30 | 1 | 39.6 | 9.58 | 0.75 | 1.6
2023-07-03 | 15:30 | 2.1 | 35.7 | 11.29 | 1 | 2 | 2023-07-04 | 14:00 | 1.1 | 39.8 | 10.56 | 1 | 2
2023-07-10 | 16:15 | 2 | 38.7 | 10.09 | 1 | 2 | 2023-07-10 | 16:15 | 1 | 41.7 | 10.17 | 0.75 | 1.6
2023-07-17 | 14:00 | 2 | 38.1 | 10 | 1 | 2 | 2023-07-17 | 14:00 | 1.2 | 40.2 | 9.9 | 0.6 | 1.2
2023-07-24 | 14:00 | 2 | 35.9 | 10.2 | 1 | 2 | 2023-07-24 | 14:00 | 1.1 | 39.6 | 11.5 | 1.1 | 2.2
2023-08-02 | 14:45 | 2.1 | 38.4 | 11.31 | 0.75 | 1.5 | 2023-07-31 | 14:30 | 1.1 | 38.2 | 10.31 | 0.75 | 1.6
2023-08-07 | 14:00 | 2 | 37.2 | 10.3 | 1 | 2 | 2023-08-07 | 14:00 | 1.21 | 40.1 | 40.4 | 1 | 2
2023-08-14 | 14:05 | 2 | 37.6 | 11.52 | 0.8 | 1.6 | 2023-08-17 | 13:00 | 1.2 | 40.7 | 9.52 | 0.8 | 1.6
2023-08-21 | 14:00 | 2 | 38.1 | 9.96 | 1 | 2 | 2023-08-21 | 14:00 | 1.2 | 41 | 10.12 | 0.75 | 1.6
2023-08-29 | 11:00 | 2 | 37.9 | 10.73 | 1 | 2 | 2023-08-29 | 11:00 | 1.2 | 40.4 | 10.27 | 1 | 2
2023-09-04 | 15:30 | 2 | 38.7 | 10.94 | 0.75 | 1.6 | 2023-09-04 | 15:30 | 1.2 | 40.4 | 10.75 | 0.5 | 1
2023-09-11 | 13:30 | 2 | 36.9 | 10.26 | 0.75 | 1.6 | 2023-09-11 | 13:30 | 1.2 | 41.6 | 9.81 | 0.8 | 1.6
2023-09-18 | 11:00 | 2 | 37.6 | 10.4 | 0.6 | 1.2 | 2023-09-18 | 11:00 | 1.2 | 39.9 | 10 | 1 | 2
2023-09-25 | 10:30 | 2.1 | 38.1 | 10.96 | 1 | 2 | 2023-09-25 | 10:30 | 1.2 | 40.3 | 11.15 | 0.75 | 1.6
2023-10-02 | 14:45 | 2 | 38.1 | 10.85 | 1 | 2 | 2023-10-02 | 14:45 | 1.2 | 41.3 | 10.56 | 1 | 2
2023-10-09 | 12:40 | 2 | 38.9 | 11.09 | 1 | 2 | 2023-10-09 | 12:40 | 1.4 | 38.8 | 11.22 | 0.8 | 1.6
2023-10-16 | 14:20 | 2 | 17.1 | 10.2 | 1.2 | 2.4 | 2023-10-16 | 14:20 | 1.4 | 15.2 | 11.1 | 1 | 2
2023-10-23 | 13:30 | 2 | 38.2 | 11.6 | 0.8 | 1.6 | 2023-10-23 | 13:30 | 1.4 | 32.9 | 10.91 | 0.7 | 1.4
2023-10-30 | 14:30 | 1.9 | 38.4 | 11.24 | 1.2 | 2.4 | 2023-10-30 | 14:30 | 0.62 | 36.8 | 10.15 | 0.5 | 1
2023-11-06 | 14:15 | 1.9 | 37.3 | 9.1 | 0.75 | 1.5 | 2023-11-06 | 14:15 | 0.8 | 32.3 | 9.75 | 1 | 2
2023-11-15 | 11:20 | 2 | 33.1 | 10.57 | 0.75 | 1.6 | 2023-11-15 | 11:20 | 1.1 | 32.7 | 11.87 | 1.1 | 2.2
2023-11-20 | 13:30 | 2 | 36.6 | 12.14 | 0.7 | 1.4 | 2023-11-20 | 13:30 | 1.2 | 38.4 | 9.35 | 0.5 | 1
2023-11-28 | 11:20 | 2.2 | 34.7 | 11.8 | 0.6 | 1.2 | 2023-11-28 | 11:20 | 1.5 | 34.5 | 11.7 | 0.8 | 1.6
2023-12-08 | 13:40 | 2 | 35.7 | 11.23 | 1 | 2 | 2023-12-08 | [6 empty] | Stream 4 down
2023-12-14 | 9:30 | 2.2 | 35 | 11.79 | 1 | 2 | 2023-12-14 | [6 empty] | STREAM DOWN
2023-12-18 | 14:00 | 2.5 | 35.7 | 11.5 | 0.6 | 1.2 | 2023-12-22 | 14:00 | 1 | 38.1 | 10.59 | 0.75 | 1.5
2023-12-27 | 14:00 | 2.4 | 35.5 | 10.52 | 1 | 2 | 2023-12-27 | 14:00 | 1 | 36.6 | 11.3 | 1.3 | 2.6
2024-01-03 | 9:30 | 2.2 | 35.1 | 11.37 | 1 | 2 | 2024-01-03 | 9:30 | 1 | 37.2 | 10.93 | 1 | 2
2024-01-08 | 15:45 | 2.3 | 33 | 12.03 | 1 | 2 | 2024-01-08 | 15:45 | 1 | 34.5 | 10.82 | 1 | 2
2024-01-15 | 13:10 | 2.2 | 33.9 | 11.4 | 0.75 | 1.5 | 2024-01-15 | 13:10 | 1.1 | 33.7 | 10.36 | 0.75 | 1.5
2024-01-22 | 14:00 | 2.1 | 35 | 10.87 | 0.75 | 1.5 | 2024-01-22 | 14:00 | 1 | 36.2 | 11.24 | 1 | 2
2024-01-31 | [6 empty] | 2024-01-31 | 13:45 | 1.1 | 34.8 | 10.75 | 0.5 | 1
2024-02-05 | 14:10 | 2 | 35.6 | 10.95 | 1.5 | 3 | 2024-02-05 | 14:10 | 1.1 | 37.6 | 10.97 | 0.6 | 1.2
2024-02-12 | 13:30 | 2 | 34.3 | 11.31 | 0.7 | 1.4 | 2024-02-12 | 13:30 | 0.8 | 35.6 | 11.79 | 1 | 2
2024-02-19 | 14:00 | 2.1 | 35.8 | 10.9 | 0.9 | 1.8 | 2024-02-19 | 14:20 | 0.8 | 37.9 | 10.7 | 0.75 | 1.5
2024-02-26 | 14:30 | 2.2 | 34.1 | 10.75 | 0.5 | 1 | 2024-02-26 | 14:30 | 0.8 | 36.6 | 11.5 | 0.75 | 1.5
2024-03-05 | 14:50 | 2.1 | 34.1 | 9.21 | 0.9 | 1.8 | 2024-03-07 | 14:00 | 0.8 | 35.6 | 11.8 | 1 | 2
2024-03-11 | 13:55 | 2.2 | 34.6 | 10.74 | 0.5 | 1 | 2024-03-12 | 13:30 | 0.8 | 37.3 | 10.68 | 0.25 | 0.5
2024-03-18 | 14:20 | 2 | 37.2 | 10.5 | 1.2 | 2.4 | 2024-03-18 | 14:20 | 0.9 | 39.8 | 11.5 | 1 | 2
2024-03-25 | 14:20 | 2 | 35.5 | 9.54 | 0.75 | 1.5 | 2024-03-25 | 14:20 | 1 | 37.2 | 11.55 | 0.75 | 1.5
2024-04-02 | 14:10 | 2.1 | 37.2 | 10.4 | 0.75 | 1.5 | 2024-04-04 | 14:10 | 1 | 38.2 | 9.13 | 0.7 | 1.4
2024-04-08 | 14:05 | 2.5 | 36.8 | 9.8 | 0.8 | 1.6 | 2024-04-08 | 14:05 | 1 | 37.9 | 9.3 | 0.6 | 1.2
2024-04-17 | 12:10 | 2.3 | 35.1 | 10.9 | 1 | 2 | 2024-04-17 | 12:10 | 1 | 34.4 | 10.77 | 0.6 | 1.2
2024-04-22 | 15:45 | 2.3 | 36.9 | 10.97 | 1 | 2 | 2024-04-22 | 15:45 | 1 | 37.2 | 11.42 | 0.6 | 1.2
2024-04-30 | 14:00 | 2.1 | 37.8 | 10.81 | 0.7 | 1.4 | 2024-04-30 | 14:00 | 0.9 | 39.7 | 11.61 | 1 | 2
2024-05-07 | 14:30 | 2.2 | 36.7 | 9.8 | 0.5 | 1 | 2024-05-07 | 14:30 | 1 | 40.3 | 11.2 | 1 | 2
2024-05-13 | 14:10 | 2.4 | 39.6 | 10.74 | 1 | 2 | 2024-05-13 | 14:10 | 0.9 | 41.2 | 11.42 | 1 | 2
2024-05-22 | 16:00 | 2.5 | 38.2 | 11.2 | 0.5 | 1 | 2023-05-20 | 13:50 | 1 | 35.8 | 10.05 | 1.8 | 3.6
2024-05-29 | 14:00 | 2.6 | 38.1 | 11.5 | 0.75 | 1.5 | 2024-05-29 | 14:00 | 1 | 40.5 | 11.75 | 1 | 2
2024-06-03 | 15:45 | 2.3 | 36.2 | 9.23 | 0.75 | 1.5 | 2024-06-03 | 15:45 | 1 | 36.8 | 10.91 | 0.75 | 1.5
2024-06-11 | 14:00 | 1.3 | 37 | 11.28 | 0.6 | 1.2 | 2024-06-10 | 14:00 | 1 | 38.4 | 10.02 | 0.6 | 1.2
2024-06-17 | 13:45 | 2.4 | 38.6 | 11.2 | 0.25 | 0.5 | 2024-06-17 | 13:45 | 1 | 39.1 | 10.5 | 0.6 | 1.2
2024-06-24 | 14:00 | 2.2 | 39.6 | 10.8 | 0.7 | 1.4 | 2024-06-24 | 14:00 | 1 | 40.5 | 10.8 | 1 | 2
2024-07-02 | 13:40 | 2 | 36.7 | 10.25 | 1 | 2 | 2024-07-02 | 13:40 | 1 | 39.2 | 10.31 | 0.4 | 0.8
2024-07-08 | 14:10 | 2.2 | 38 | 11.09 | 0.8 | 1.6 | 2024-07-08 | 14:10 | 1 | 39.8 | 11.27 | 0.6 | 1.2
2024-07-15 | 15:40 | 2.3 | 35.7 | 9.25 | 0.8 | 1.6 | 2024-07-15 | 15:40 | 1 | 38.9 | 10.2 | 1 | 2
2024-07-22 | 14:15 | 2.3 | 39 | 11.28 | 0.8 | 1.6 | 2024-07-22 | 14:15 | 1 | 42.2 | 11.58 | 1 | 2
2024-07-31 | 15:50 | [5 empty] | 2024-07-31 | 15:50 | 1.1 | 37.8 | 10.3 | 1 | 2
2024-08-05 | [6 empty] | 2024-08-05 | 13:55 | 1 | 40.9 | 11.37 | 1 | 2
2024-08-16 | 9:15 | 2.4 | 36.7 | 12.46 | 1 | 2 | 2024-08-12 | 14:00 | 1 | 41.8 | 11.21 | 1.25 | 2.5
2024-08-19 | 14:00 | 2.4 | 38.5 | 10.19 | 2.1 | 4.2 | 2024-08-19 | 14:00 | 1 | 40.8 | 11.12 | 1.1 | 2.2
2024-08-27 | 14:00 | 2.5 | 38.2 | 10.8 | 0.75 | 1.5 | 2024-08-27 | 14:00 | 1 | 40.7 | 11.46 | 0.6 | 1.2
2024-09-02 | 13:50 | 2.5 | 39.8 | 10.3 | 1 | 2 | 2024-09-02 | 13:50 | 1 | 40.6 | 11.1 | 1 | 2
2024-09-09 | 13:50 | 2.6 | 37.1 | 10.39 | 1 | 2 | 2024-09-09 | 13:50 | 1 | 39.4 | 11.1 | 0.75 | 1.5
2024-09-16 | [6 empty] | 2024-09-16
2024-09-23 | 14:15 | 1.9 | 37.2 | 10.5 | 0.75 | 1.5 | 2024-09-24 | 14:00 | 1 | 31.9 | 9.98 | 0.75 | 1.5
Note on A38: SL3Lab: stream 3 down
Note on A189: SL3Lab: Stream 3 not in operation due to repairs to failed bearing,
Note on A484: lfllab: time test carried out 1415
Note on A562: lfllab: Plant has been on shutdown all week
Note on A566: lfllab: No readings on stream 3 System bypass in operation. All week.
Note on A567: lfllab: Bypass in operation, no result possible other than demister flow.
Note on A568: lfllab: sample taken from new bypass sampling point
Note on A569: lfllab: sample taken from spare fan sampling point
Note on A571: lfllab: just started up
Note on A599: lfllab: reading taken from spare fan sample point
Note on A600: Lab Sl3 - LGL: Reading taken from spare samlple point
Note on A686: Lab Sl3 - LGL: Line down
Note on A687: Lab Sl3 - LGL: Line down
Note on A717: Lab Sl3 - LGL: First check after shutdown
Note on A1072: Lab Sl3 - LGL: Stream down due to power cut.
Note on A1073: Lab Sl3 - LGL: stream 3 not running
Note on A1074: Lab Sl3 - LGL: Stream 3 down
Note on A1097: Lab Sl3 - LGL: (Stream down Mon 4th- Weds 6th)
Note on A1105: Lab Sl3 - SHUTDOWN STREAM 3
Note on A1121: Lab Sl3 - LGL: Line down on Monday
Note on A1131: Lab Sl3 - LGL: Line down since 24/07/2024. Filmtruder bearing issues.
Note on A1132: Lab Sl3 - LGL: Stream Still Down
Note on A1138: Lab Sl3 - LGL: Stream down
Note on B958: Lab Sl3 - LGL: repeat tomorrow!
Note on C89: SL3Lab: average flow due to fluctuation on demister valve reported to control room for check (0-3)
Note on C107: SL3Lab: demister readings fluctuating - no accurate reading can be made - estimated at 2
Note on C248: LFLLAB: demister fluctuating between these two figures, control room informed.
Note on C340: LFLLAB: check next week to see if broken
Note on C343: LFLLAB: created a work order to correct fault
Note on C519: lfllab: flow meter very erratic, reported
Note on C527: lfllab: Flow meter not working, reported
Note on D50: SL3Lab: temp taken on 14/10/2003 as thermometer was broken on 13/10/2003
Note on E286: lfllab: meter being serviced
Note on E287: lfllab: meter being serviced
Note on E651: Lab Sl3 - LGL: 2-112Q109 used
Note on E652: Lab Sl3 - LGL: 2-112Q109 used
Note on E653: Lab Sl3 - LGL: 2-112Q109 used
Note on E654: Lab Sl3 - LGL: 2-112Q109 used
Note on E655: Lab Sl3 - LGL: 2-112Q109 used
Note on E656: Lab Sl3 - LGL: 2-112Q109 used
Note on E657: Lab Sl3 - LGL: 2-112Q109 used
Note on E658: Lab Sl3 - LGL: 2-112Q109 used
Note on E659: Lab Sl3 - LGL: 2-112Q109 used
Note on E660: Lab Sl3 - LGL: 2-112Q109 used
Note on E661: lfllab: 2-112Q109 used
Note on E662: lfllab: 2-112Q109 used
Note on E663: lfllab: 2-112Q109 used
Note on E664: lfllab: 2-112Q109 used
Note on E670: lfllab: 2-112Q109 used
Note on E671: lfllab: 2-112Q109 used
Note on E672: lfllab: 2-112Q109 used
Note on E673: lfllab: 2-112Q109 used
Note on E674: lfllab: 2-112Q109 used
Note on E675: lfllab: 2-112Q109 used
Note on I23: AHalford: str 4 shutdown for 1 week
Note on I484: lfllab: time test carried out 1415 hrs
Note on I562: lfllab: Plant shutdown all week
Note on I603: Lab Sl3 - LGL: Stream 4 down on 20/05/14
Note on I717: Lab Sl3 - LGL: First check after shutdown
Note on I736: Lab Sl3 - LGL: Tested after spin up
Note on I750: Lab Sl3 - LGL: Spare sample point
Note on I866: Lab Sl3 - LGL: taken from spare sampling point
Note on I971: Lab Sl3 - LGL: Extractor fan off - retest 22/6
Note on I972: Lab Sl3 - LGL: Extractor fan off
Note on I973: Lab Sl3 - LGL: No extraction fan
Note on I974: Lab Sl3 - LGL: Extractor Fan "off"
Note on I975: Lab Sl3 - LGL: No extraxction fan
Note on I976: Lab Sl3 - LGL: No extraxction fan
Note on I977: Lab Sl3 - LGL: no extraction fan
Note on I978: Lab Sl3 - LGL: no extraction fan
Note on I979: Lab Sl3 - LGL: no extaction fan
Note on I980: Lab Sl3 - LGL: no extraction fan
Note on I981: Lab Sl3 - LGL: no extraction fan
Note on I982: Lab Sl3 - LGL: no extraction fan
Note on I983: Lab Sl3 - LGL: New Fan back on
Note on I986: Lab Sl3 - LGL: New Fan still running ok
Note on I1072: Lab Sl3 - LGL: Stream down due to power cut.
Note on I1110: Lab Sl3 - LGL: line down beginning of week
Note on I1114: Lab Sl3 - LGL: lines down at beginning of week
Note on I1138: Lab Sl3 - LGL: Stream down
Note on J496: lfllab: shut down on the 30/4/12
Note on K89: SL3Lab: average flow due to fluctuation on demister valve reported to control room (0-3)
Note on K107: SL3Lab: demister readings fluctuating - no accurate reading can be made - estimated at 0.63
Note on K272: lfllab: faulty meter?
Note on K273: lfllab: faulty meter?
Note on K276: LFLLAB: faulty meter ?
Note on K494: lfllab: unable to take any furthur measyrements as cross draught flow diverted proir to shutdown
Note on K519: lfllab: flow meter very erratic, reported
Note on K527: lfllab: flow meter not working, reported
Note on K686: Lab Sl3 - LGL: fluctuating gauge so unable to take reading. Ops manager informed.
Note on L50: SL3Lab: temperature was taken on 14/10/2003 as thermometer was broken on 13/10/2003
Note on M286: lfllab: meter being serviced
Note on M287: lfllab: meter being serviced
Note on M321: LFLLAB: read Friday 19 Dec
Note on M452: lflsll: It wasn't possible to measure the true air flow. The standby fan was operating and there was no suitable point to measure the true air flow.. This value has been estimated from the fan speed and fan curve (+10%, -0%).
Note on M453: lflsll: Air velocity measured in cross over ducting to standby fan. Note : This has the same cross section as the main stream 4 fan (viz : 130 x 130 cm). The low result was due to stream 4 being in slowdown when the measurement was taken.
Note on M586: lfllab: Tested 21-01-14 Issue with stream 4
Note on M651: Lab Sl3 - LGL: 2-112Q109 used
Note on M652: Lab Sl3 - LGL: 2-112Q109 used
Note on M653: Lab Sl3 - LGL: 2-112Q109 used
Note on M654: Lab Sl3 - LGL: 2-112Q109 used
Note on M655: Lab Sl3 - LGL: 2-112Q109 used
Note on M656: Lab Sl3 - LGL: 2-112Q109 used
Note on M657: Lab Sl3 - LGL: 2-112Q109 used
Note on M658: Lab Sl3 - LGL: 2-112Q109 used
Note on M659: Lab Sl3 - LGL: 2-112Q109 used
Note on M660: Lab Sl3 - LGL: 2-112Q109 used
Note on M661: lfllab: 2-112Q109 used
Note on M662: lfllab: 2-112Q109 used
Note on M663: lfllab: 2-112Q109 used
Note on M664: lfllab: 2-112Q109 used
Note on M669: Lab Sl3 - LGL: 2-112Q109 used
Note on M670: Lab Sl3 - LGL: 2-112Q109 used
Note on M671: Lab Sl3 - LGL: 2-112Q109 used
Note on M672: Lab Sl3 - LGL: 2-112Q109 used
Note on M673: Lab Sl3 - LGL: 2-112Q109 used
Note on M674: Lab Sl3 - LGL: 2-112Q109 used
Note on M675: Lab Sl3 - LGL: 2-112Q109 used

## Effluent loading
| minutes/week | 10080
| AMINE | [14 empty] | COD
| TUESDAY SAMPLING |  |  |  |  | LAST FRIDAY SAMPLING: |  | Total flow discharge(m3) | Total minutes | Total minutes | Total flow discharged(m3) | Total Amines (Kg/m3) | Total amines discharged (Kg) | Total amines discharged (T) | WEEKLY EXTRAPOLATION (T) Limit = 8.00 | TUESDAY SAMPLING |  |  |  | COD mg/l | COD (Kg/m3) | Total COD discharged (T) | Total COD discharged (Kg/minute) | WEEKLY EXTRAPOLATION (T) Limit = 30.00
| Date and Time of sampling | Total flow m3 | Morpholine | NMMO | N-methylmorpholine | Date and Time of sampling | Total flow m3 | [8 empty] | COD test 1 | COD test 2 | Average COD (mg/L) | COD std
| 2018-12-11 09:38 | 58920 | 10.7 | 206.09 | 205.07 | 2018-12-07 09:21 | 51390 | 7530 | 4.0118 | 5777 | 7530 | 0.42186 | 3176.6058 | 3.1766 | 5.5427 | 844 | 849 | 846.5 | 736 | 1725.2038 | 1.7252 | 12.9908 | 2.2487 | 22.667
| 2018-12-18 09:00 | 73670 | 21.3 | 317.7 | 254.6 | 2018-12-14 09:23 | 64220 | 9450 | 3.984 | 5737 | 9450 | 0.5936 | 5609.52 | 5.6095 | 9.856 | 1046 | 1048 | 1047 | 766 | 2050.2611 | 2.0503 | 19.375 | 3.3772 | 34.0421
| 2018-12-19 07:40 | 75880 | 16.9 | 312 | 247.4 | 2018-12-14 09:23 | 64220 | 11660 | 4.9285 | 7097 | 11660 | 0.5763 | 6719.658 | 6.7197 | 9.5441 | 1049 | 1070 | 1059.5 | 757 | 2099.4055 | 2.0994 | 24.4791 | 3.4492 | 34.7681
| 2018-12-20 07:45 | 77840 | 17 | 305.6 | 249.7 | 2018-12-14 09:23 | 64220 | 13620 | 5.9319 | 8542 | 13620 | 0.5723 | 7794.726 | 7.7947 | 9.1982 | 978 | 989 | 983.5 | 767 | 1923.4029 | 1.9234 | 26.1967 | 3.0668 | 30.9135
| 2018-12-24 07:48 | 86660 | 21.42 | 313.55 | 252.23 | 2018-12-21 | 79340 | 7320 | 3.325 | 4788 | 7320 | 0.5872 | 4298.304 | 4.2983 | 9.0491 | 1055 | 1057 | 1056 | 766 | 2067.8851 | 2.0679 | 15.1369 | 3.1614 | 31.8672
| 2018-12-31 09:00 | 101300 | 48.6 | 259.7 | 235.65 | 2018-12-28 09:00 | 94070 | 7230 | 3 | 4320 | 7230 | 0.54395 | 3932.7585 | 3.9328 | 9.1764 | 971 | 976 | 973.5 | 745 | 1960.0671 | 1.9601 | 14.1713 | 3.2804 | 33.0663
| 2019-01-07 08:20 | 114070 | 13.42 | 229.96 | 162.88 | 2019-01-04 09:17 | 107770 | 6300 | 2.9604 | 4263 | 6300 | 0.40626 | 2559.438 | 2.5594 | 6.0519 | 908 | 912 | 910 | 763 | 1788.9908 | 1.789 | 11.2706 | 2.6438 | 26.6498
| 2019-01-08 08:20 | 116070 | 14.68 | 215.13 | 188.22 | 2019-01-04 09:17 | 107770 | 8300 | 3.9604 | 5703 | 8300 | 0.41803 | 3469.649 | 3.4696 | 6.1326 | 890 | 895 | 892.5 | 747 | 1792.1687 | 1.7922 | 14.875 | 2.6083 | 26.2914
| 2019-01-09 08:00 | 117900 | 9.36 | 198.64 | 215 | 2019-01-04 09:17 | 107770 | 10130 | 4.9465 | 7123 | 10130 | 0.423 | 4284.99 | 4.285 | 6.0638 | 888 | 901 | 894.5 | 749 | 1791.3885 | 1.7914 | 18.1468 | 2.5476 | 25.6801
| 2019-01-10 08:10 | 119760 | 17.65 | 191.5 | 223.91 | 2019-01-04 09:17 | 107770 | 11990 | 5.9535 | 8573 | 11990 | 0.43306 | 5192.3894 | 5.1924 | 6.1051 | 892 | 888 | 890 | 747 | 1787.1486 | 1.7871 | 21.4279 | 2.4995 | 25.1946
| 2019-01-14 08:30 | 127110 | 21.41 | 128.63 | 218.05 | 2019-01-11 09:04 | 121560 | 5550 | 2.9764 | 4286 | 5550 | 0.36809 | 2042.8995 | 2.0429 | 4.8046 | 921 | 914 | 917.5 | 739 | 1862.3139 | 1.8623 | 10.3358 | 2.4115 | 24.3083
| 2019-01-16 08:50 | 130630 | 21.56 | 119.82 | 250.53 | 2019-01-11 09:04 | 121560 | 9070 | 4.9903 | 7186 | 9070 | 0.39191 | 3554.6237 | 3.5546 | 4.9862 | 934 | 927 | 930.5 | 755 | 1848.6755 | 1.8487 | 16.7675 | 2.3334 | 23.5202
| 2019-01-22 08:35 | 141690 | 64.3 | 198.4 | 153.4 | 2019-01-18 08:53 | 134070 | 7620 | 3.9875 | 5742 | 7620 | 0.4161 | 3170.682 | 3.1707 | 5.5661 | 909 | 906 | 907.5 | 734 | 1854.564 | 1.8546 | 14.1318 | 2.4611 | 24.8081
| 2019-01-23 07:52 | 143640 | 70.4 | 262 | 141.8 | 2019-01-18 08:53 | 134070 | 9570 | 4.9576 | 7139 | 9570 | 0.4742 | 4538.094 | 4.5381 | 6.4076 | 999 | 1001 | 1000 | 762 | 1968.5039 | 1.9685 | 18.8386 | 2.6388 | 26.5994
| 2019-01-24 07:39 | 145980 | 81.1 | 258.1 | 151.3 | 2019-01-18 08:53 | 134070 | 11910 | 5.9486 | 8566 | 11910 | 0.4905 | 5841.855 | 5.8419 | 6.8744 | 1043 | 1013 | 1028 | 776 | 1987.1134 | 1.9871 | 23.6665 | 2.7628 | 27.8495
| 2019-01-28 09:02 | 153550 | 58.8 | 353.64 | 220.95 | 2019-01-25 09:09 | 147830 | 5720 | 2.9951 | 4313 | 5720 | 0.63339 | 3622.9908 | 3.623 | 8.4674 | 991 | 1040 | 1015.5 | 781 | 1950.3841 | 1.9504 | 11.1562 | 2.5866 | 26.0734
| 2019-01-30 08:16 | 157440 | 78.56 | 311.26 | 219.62 | 2019-01-25 09:09 | 147830 | 9610 | 4.9632 | 7147 | 9610 | 0.60944 | 5856.7184 | 5.8567 | 8.2602 | 985 | 963 | 974 | 733 | 1993.1787 | 1.9932 | 19.1544 | 2.6801 | 27.0151
| 2019-01-31 09:16 | 159573 | 83.6 | 268.09 | 215.58 | 2019-01-25 09:09 | 147830 | 11743 | 6.0049 | 8647 | 11743 | 0.56727 | 6661.4516 | 6.6615 | 7.7654 | 989 | 996 | 992.5 | 746 | 1995.6434 | 1.9956 | 23.4348 | 2.7102 | 27.3185
| 2019-02-04 08:40 | 166580 | 68.23 | 157.08 | 132.43 | 2019-02-01 08:30 | 160990 | 5590 | 3.0069 | 4330 | 5590 | 0.35774 | 1999.7666 | 1.9998 | 4.6553 | 953 | 952 | 952.5 | 765 | 1867.6471 | 1.8676 | 10.4401 | 2.4111 | 24.3041
| 2019-02-05 11:02 | 168670 | 22.68 | 177.78 | 153.39 | 2019-02-01 08:30 | 160990 | 7680 | 4.1056 | 5912 | 7680 | 0.35385 | 2717.568 | 2.7176 | 4.6335 | 920 | 909 | 914.5 | 744 | 1843.75 | 1.8438 | 14.16 | 2.3951 | 24.1429
| 2019-02-06 08:46 | 170580 | 31 | 189.92 | 151.42 | 2019-02-01 08:30 | 160990 | 9590 | 5.0111 | 7216 | 9590 | 0.37234 | 3570.7406 | 3.5707 | 4.988 | 921 | 924 | 922.5 | 744 | 1859.879 | 1.8599 | 17.8362 | 2.4718 | 24.9154
| 2019-02-12 09:00 | 181920 | 54.07 | 268.95 | 123.55 | 2019-02-08 08:55 | 174260 | 7660 | 4.0035 | 5765 | 7660 | 0.44657 | 3420.7262 | 3.4207 | 5.9811 | 908 | 903 | 905.5 | 758 | 1791.8865 | 1.7919 | 13.7259 | 2.3809 | 23.9994
| 2019-02-19 09:22 | 195410 | 63.05 | 176.04 | 128.52 | 2019-02-15 09:00 | 187850 | 7560 | 4.0153 | 5782 | 7560 | 0.36761 | 2779.1316 | 2.7791 | 4.845 | 847 | 840 | 843.5 | 737 | 1716.7571 | 1.7168 | 12.9787 | 2.2447 | 22.6263
| 2019-02-26 | 207480 | 8.65 | 86.237 | 135 | 2019-02-22 09:08 | 201280 | 6200 | 3.6194 | 5212 | 6200 | 0.22989 | 1425.2994 | 1.4253 | 2.7565 | 638 | 639 | 638.5 | 729 | 1313.786 | 1.3138 | 8.1455 | 1.5628 | 15.7533
| 2019-03-05 09:00 | 220550 | 0 | 298.91 | 128.71 | 2019-03-01 09:06 | 212130 | 8420 | 3.9958 | 5753 | 8420 | 0.42762 | 3600.5604 | 3.6006 | 6.3086 | 983 | 1003 | 993 | 770 | 1934.4156 | 1.9344 | 16.2878 | 2.8312 | 28.5383
| 2019-03-06 08:35 | 222200 | 0 | 276.24 | 150.33 | 2019-03-01 09:06 | 212130 | 10070 | 4.9785 | 7169 | 10070 | 0.42657 | 4295.5599 | 4.2956 | 6.0398 | 961 | 965 | 963 | 738 | 1957.3171 | 1.9573 | 19.7102 | 2.7494 | 27.7136
| 2019-03-07 08:48 | 223960 | 0 | 248.65 | 157.35 | 2019-03-01 09:06 | 212130 | 11830 | 5.9875 | 8622 | 11830 | 0.406 | 4802.98 | 4.803 | 5.6152 | 957 | 954 | 955.5 | 737 | 1944.7083 | 1.9447 | 23.0059 | 2.6683 | 26.8962
| 2019-03-12 08:53 | 233350 | 6.11 | 147.56 | 108.64 | 2019-03-08 09:04 | 225870 | 7480 | 3.9924 | 5749 | 7480 | 0.26231 | 1962.0788 | 1.9621 | 3.4402 | 911 | 904 | 907.5 | 754 | 1805.3714 | 1.8054 | 13.5042 | 2.349 | 23.6775
| 2019-03-18 08:12 | 245960 | 5.31 | 300.39 | 120.24 | 2019-03-15 08:58 | 239090 | 6870 | 2.9681 | 4274 | 6870 | 0.42594 | 2926.2078 | 2.9262 | 6.9013 | 1008 | 1010 | 1009 | 737 | 2053.5957 | 2.0536 | 14.1082 | 3.3009 | 33.2734
| 2019-03-19 08:00 | 247871 | 0 | 266.87 | 125.39 | 2019-03-15 08:58 | 239090 | 8781 | 3.9597 | 5702 | 8781 | 0.39226 | 3444.4351 | 3.4444 | 6.0891 | 996 | 1002 | 999 | 745 | 2011.4094 | 2.0114 | 17.6622 | 3.0975 | 31.2232
| 2019-03-20 07:48 | 250098 | 4.16 | 281.1 | 123.63 | 2019-03-15 08:58 | 239090 | 11008 | 4.9514 | 7130 | 11008 | 0.40889 | 4501.0611 | 4.5011 | 6.3634 | 951 | 957 | 954 | 733 | 1952.251 | 1.9523 | 21.4904 | 3.0141 | 30.3819
| 2019-03-21 07:58 | 252020 | 0 | 277.81 | 121.67 | 2019-03-15 08:58 | 239090 | 12930 | 5.9583 | 8580 | 12930 | 0.39948 | 5165.2764 | 5.1653 | 6.0683 | 986 | 992 | 989 | 730 | 2032.1918 | 2.0322 | 26.2762 | 3.0625 | 30.87
| 2019-03-26 08:55 | 261150 | 14.1 | 344.78 | 178.31 | 2019-03-22 08:55 | 253130 | 8020 | 4 | 5760 | 8020 | 0.53719 | 4308.2638 | 4.3083 | 7.5395 | 1102 | 1117 | 1109.5 | 760 | 2189.8026 | 2.1898 | 17.5622 | 3.049 | 30.7339
| 2019-03-27 08:57 | 262450 | 13.11 | 308.7 | 203.55 | 2019-03-22 08:55 | 253130 | 9320 | 5.0014 | 7202 | 9320 | 0.52536 | 4896.3552 | 4.8964 | 6.853 | 1068 | 1068 | 1068 | 762 | 2102.3622 | 2.1024 | 19.594 | 2.7206 | 27.424
| 2019-03-28 08:42 | 263800 | 4.96 | 252.13 | 210.6 | 2019-03-22 08:55 | 253130 | 10670 | 5.991 | 8627 | 10670 | 0.46769 | 4990.2523 | 4.9903 | 5.8307 | 1028 | 1023 | 1025.5 | 734 | 2095.7084 | 2.0957 | 22.3612 | 2.592 | 26.1274
| 2019-04-01 12:25 | 272010 | 3.79 | 163.02 | 151.8 | 2019-03-29 08:59 | 265180 | 6830 | 3.1431 | 4526 | 6830 | 0.31861 | 2176.1063 | 2.1761 | 4.8465 | 977 | 974 | 975.5 | 742 | 1972.035 | 1.972 | 13.469 | 2.9759 | 29.9972
| 2019-04-02 09:04 | 273940 | 7.62 | 154.1 | 154.37 | 2019-03-29 08:59 | 265180 | 8760 | 4.0035 | 5765 | 8760 | 0.31609 | 2768.9484 | 2.7689 | 4.8415 | 834 | 831 | 832.5 | 760 | 1643.0921 | 1.6431 | 14.3935 | 2.4967 | 25.1668
| 2019-04-03 08:58 | 276160 | 7.45 | 144.48 | 154.18 | 2019-03-29 08:59 | 265180 | 10980 | 4.9993 | 7199 | 10980 | 0.30611 | 3361.0878 | 3.3611 | 4.7062 | 867 | 858 | 862.5 | 761 | 1700.0657 | 1.7001 | 18.6667 | 2.593 | 26.137
| 2019-04-04 09:10 | 278230 | 0 | 151.9 | 152.1 | 2019-03-29 08:59 | 265180 | 13050 | 6.0076 | 8651 | 13050 | 0.304 | 3967.2 | 3.9672 | 4.6225 | 872 | 875 | 873.5 | 755 | 1735.4305 | 1.7354 | 22.6474 | 2.6179 | 26.3883
| 2019-04-09 08:59 | 287840 | 7.98 | 126.95 | 97.6 | 2019-04-05 08:48 | 280080 | 7760 | 4.0076 | 5771 | 7760 | 0.23253 | 1804.4328 | 1.8044 | 3.1517 | 789 | 791 | 790 | 737 | 1607.8697 | 1.6079 | 12.4771 | 2.162 | 21.7933
| 2019-04-16 09:13 | 300760 | 4.25 | 96.65 | 133.65 | 2019-04-12 09:03 | 293700 | 7060 | 4.0069 | 5770 | 7060 | 0.23455 | 1655.923 | 1.6559 | 2.8928 | 696 | 694 | 695 | 774 | 1346.8992 | 1.3469 | 9.5091 | 1.648 | 16.6121
| 2019-04-23 08:58 | 316680 | 4.88 | 207.46 | 153.13 | 2019-04-18 08:45 | 304350 | 12330 | 5.009 | 7213 | 12330 | 0.36547 | 4506.2451 | 4.5062 | 6.2974 | 940 | 936 | 938 | 749 | 1878.5047 | 1.8785 | 23.162 | 3.2111 | 32.3683
| 2019-04-24 09:05 | 319170 | 0 | 190.81 | 179.87 | 2019-04-18 08:45 | 304350 | 14820 | 6.0139 | 8660 | 14820 | 0.37068 | 5493.4776 | 5.4935 | 6.3943 | 929 | 937 | 933 | 748 | 1870.9893 | 1.871 | 27.7281 | 3.2019 | 32.2747
| 2019-04-25 08:42 | 321190 | 0 | 183.92 | 165.66 | 2019-04-18 08:45 | 304350 | 16840 | 6.9979 | 10077 | 16840 | 0.34958 | 5886.9272 | 5.8869 | 5.8887 | 884 | 884 | 884 | 724 | 1831.4917 | 1.8315 | 30.8423 | 3.0607 | 30.8515
| 2019-04-30 09:02 | 331040 | 7.35 | 112.41 | 115.21 | 2019-04-26 09:01 | 322940 | 8100 | 4.0007 | 5761 | 8100 | 0.23497 | 1903.257 | 1.9033 | 3.3301 | 765 | 760 | 762.5 | 727 | 1573.2462 | 1.5732 | 12.7433 | 2.212 | 22.2969
| 2019-05-01 08:30 | 332930 | 4.51 | 102.9 | 125.16 | 2019-04-26 09:01 | 322940 | 9990 | 4.9785 | 7169 | 9990 | 0.23257 | 2323.3743 | 2.3234 | 3.2668 | 781 | 790 | 785.5 | 760 | 1550.3289 | 1.5503 | 15.4878 | 2.1604 | 21.7767
| 2019-05-07 09:00 | 344250 | 3.79 | 136.21 | 139.29 | 2019-05-03 | 336730 | 7520 | 4.375 | 6300 | 7520 | 0.27929 | 2100.2608 | 2.1003 | 3.3604 | 890 | 897 | 893.5 | 765 | 1751.9608 | 1.752 | 13.1747 | 2.0912 | 21.0796
| 2019-05-14 09:00 | 358240 | 13.64 | 79.02 | 88.05 | 2019-05-10 08:55 | 350990 | 7250 | 4.0035 | 5765 | 7250 | 0.18071 | 1310.1475 | 1.3101 | 2.2908 | 775 | 778 | 776.5 | 750 | 1553 | 1.553 | 11.2592 | 1.953 | 19.6866
| 2019-05-21 08:31 | 371470 | 0 | 99.44 | 107.87 | 2019-05-17 09:05 | 363730 | 7740 | 3.9764 | 5726 | 7740 | 0.20731 | 1604.5794 | 1.6046 | 2.8247 | 760 | 756 | 758 | 733 | 1551.1596 | 1.5512 | 12.006 | 2.0967 | 21.1352
| 2019-05-28 08:38 | 383280 | 4.38 | 122.82 | 118.24 | 2019-05-24 09:02 | 375700 | 7580 | 3.9833 | 5736 | 7580 | 0.24544 | 1860.4352 | 1.8604 | 3.2694 | 744 | 743 | 743.5 | 737 | 1513.2293 | 1.5132 | 11.4703 | 1.9997 | 20.157
| 2019-05-30 09:06 | 387770 | 9.93 | 149.46 | 135.77 | 2019-05-24 09:02 | 375700 | 12070 | 6.0028 | 8644 | 12070 | 0.29516 | 3562.5812 | 3.5626 | 4.1544 | 804 | 801 | 802.5 | 751 | 1602.8628 | 1.6029 | 19.3466 | 2.2381 | 22.5605
| 2019-06-04 08:50 | 397300 | 0 | 61.16 | 125.69 | 2019-05-31 09:05 | 389850 | 7450 | 3.9896 | 5745 | 7450 | 0.18685 | 1392.0325 | 1.392 | 2.4424 | 732 | 727 | 729.5 | 723 | 1513.4855 | 1.5135 | 11.2755 | 1.9627 | 19.7836
| 2019-06-10 08:20 | 408480 | 9.34 | 354.81 | 136.85 | 2019-06-07 09:02 | 403150 | 5330 | 2.9708 | 4278 | 5330 | 0.501 | 2670.33 | 2.6703 | 6.2919 | 835 | 833 | 834 | 724 | 1727.9006 | 1.7279 | 9.2097 | 2.1528 | 21.7003
| 2019-06-11 09:01 | 410610 | 0 | 306.77 | 145.92 | 2019-06-07 09:02 | 403150 | 7460 | 3.9993 | 5759 | 7460 | 0.45269 | 3377.0674 | 3.3771 | 5.9109 | 894 | 894 | 894 | 750 | 1788 | 1.788 | 13.3385 | 2.3161 | 23.3464
| 2019-06-12 08:45 | 412700 | 5.55 | 264.73 | 155.57 | 2019-06-07 09:02 | 403150 | 9550 | 4.9882 | 7183 | 9550 | 0.42585 | 4066.8675 | 4.0669 | 5.7071 | 859 | 859 | 859 | 739 | 1743.5724 | 1.7436 | 16.6511 | 2.3181 | 23.3667
| 2019-06-13 08:27 | 414226 | 8.13 | 224.56 | 146.45 | 2019-06-07 09:02 | 403150 | 11076 | 5.9757 | 8605 | 11076 | 0.37914 | 4199.3546 | 4.1994 | 4.9192 | 792 | 793 | 792.5 | 738 | 1610.7724 | 1.6108 | 17.8409 | 2.0733 | 20.8991
| 2019-06-18 08:47 | 422870 | 4.81 | 73.14 | 141.83 | 2019-06-14 09:01 | 415810 | 7060 | 3.9903 | 5746 | 7060 | 0.21978 | 1551.6468 | 1.5516 | 2.722 | 752 | 750 | 751 | 743 | 1516.1507 | 1.5162 | 10.704 | 1.8629 | 18.7777
| 2019-06-24 08:29 | 435500 | 6.67 | 191.09 | 122.19 | 2019-06-21 08:44 | 429110 | 6390 | 2.9896 | 4305 | 6390 | 0.31995 | 2044.4805 | 2.0445 | 4.7871 | 877 | 870 | 873.5 | 740 | 1770.6081 | 1.7706 | 11.3142 | 2.6282 | 26.4918
| 2019-06-25 08:42 | 437580 | 3.84 | 183.32 | 145.2 | 2019-06-21 08:44 | 429110 | 8470 | 3.9986 | 5758 | 8470 | 0.33236 | 2815.0892 | 2.8151 | 4.9281 | 896 | 914 | 905 | 755 | 1798.0132 | 1.798 | 15.2292 | 2.6449 | 26.6603
| 2019-06-26 08:05 | 439620 | 6.41 | 177.29 | 137.75 | 2019-06-21 08:44 | 429110 | 10510 | 4.9729 | 7161 | 10510 | 0.32145 | 3378.4395 | 3.3784 | 4.7556 | 836 | 835 | 835.5 | 733 | 1709.7544 | 1.7098 | 17.9695 | 2.5094 | 25.2943
| 2019-06-27 08:25 | 442030 | 6 | 178.04 | 146.29 | 2019-06-21 08:44 | 429110 | 12920 | 5.9868 | 8621 | 12920 | 0.33033 | 4267.8636 | 4.2679 | 4.9901 | 885 | 879 | 882 | 740 | 1787.8378 | 1.7878 | 23.0989 | 2.6794 | 27.0081
| 2019-07-02 08:28 | 452420 | 7.41 | 65.28 | 171.72 | 2019-06-28 08:45 | 444200 | 8220 | 3.9882 | 5743 | 8220 | 0.24441 | 2009.0502 | 2.0091 | 3.5262 | 882 | 888 | 885 | 753 | 1762.9482 | 1.7629 | 14.4914 | 2.5233 | 25.4351
| 2019-07-09 08:40 | 462970 | 13.56 | 100.17 | 157.71 | 2019-07-05 08:52 | 456940 | 6030 | 3.9917 | 5748 | 6030 | 0.27144 | 1636.7832 | 1.6368 | 2.8704 | 759 | 761 | 760 | 744 | 1532.2581 | 1.5323 | 9.2395 | 1.6074 | 16.2029
| 2019-07-16 09:10 | 475450 | 12.16 | 57.99 | 187.89 | 2019-07-12 09:08 | 468280 | 7170 | 4.0014 | 5762 | 7170 | 0.25804 | 1850.1468 | 1.8501 | 3.2366 | 811 | 801 | 806 | 737 | 1640.4342 | 1.6404 | 11.7619 | 2.0413 | 20.5762
| 2019-07-23 09:05 | 488188 | 25.11 | 67.54 | 172.91 | 2019-07-19 08:59 | 480920 | 7268 | 4.0042 | 5766 | 7268 | 0.26556 | 1930.0901 | 1.9301 | 3.3741 | 837 | 820 | 828.5 | 736 | 1688.519 | 1.6885 | 12.2722 | 2.1284 | 21.4539
| 2019-07-30 09:02 | 498180 | 26.8 | 80.42 | 206.76 | 2019-07-26 09:08 | 491760 | 6420 | 3.9958 | 5754 | 6420 | 0.31398 | 2015.7516 | 2.0158 | 3.5312 | 759 | 755 | 757 | 726 | 1564.0496 | 1.564 | 10.0412 | 1.7451 | 17.5904
| 2019-08-06 08:57 | 11300 | 20.1 | 110.67 | 221.65 | 2019-08-02 08:56 | 3920 | 7380 | 4.0007 | 5761 | 7380 | 0.35242 | 2600.8596 | 2.6009 | 4.5507 | 826 | 812 | 819 | 760 | 1616.4474 | 1.6164 | 11.9294 | 2.0707 | 20.8728
| 2019-08-13 09:05 | 18710 | 18.66 | 69.63 | 171.47 | 2019-08-09 08:58 | 13600 | 5110 | 4.0049 | 5767 | 5110 | 0.25976 | 1327.3736 | 1.3274 | 2.3201 | 755 | 767 | 761 | 755 | 1511.9205 | 1.5119 | 7.7259 | 1.3397 | 13.5039
| 2019-08-20 09:05 | 30790 | 0 | 202.95 | 200.69 | 2019-08-16 09:05 | 23230 | 7560 | 4 | 5760 | 7560 | 0.40364 | 3051.5184 | 3.0515 | 5.3402 | 928 | 922 | 925 | 714 | 1943.2773 | 1.9433 | 14.6912 | 2.5506 | 25.7096
| 2019-08-21 00:09 | 32370 | 4.36 | 195.4 | 194.7 | 2019-08-16 09:05 | 23230 | 9140 | 4.6278 | 7209 | 9140 | 0.39446 | 3605.3644 | 3.6054 | 5.0412 | 982 | 997 | 989.5 | 762 | 1947.8346 | 1.9478 | 17.8032 | 2.4696 | 24.8934
| 2019-08-27 08:47 | 44500 | 8.44 | 90.48 | 243.5 | 2019-08-23 08:55 | 37010 | 7490 | 3.9944 | 5752 | 7490 | 0.34242 | 2564.7258 | 2.5647 | 4.4945 | 709 | 709 | 709 | 744 | 1429.4355 | 1.4294 | 10.7065 | 1.8613 | 18.7624
| 2019-08-29 08:40 | 49170 | 12.8 | 16.72 | 319.29 | 2019-08-23 08:55 | 37010 | 12160 | 5.9896 | 8625 | 12160 | 0.34881 | 4241.5296 | 4.2415 | 4.9571 | 784 | 806 | 795 | 775 | 1538.7097 | 1.5387 | 18.7107 | 2.1694 | 21.8671
| 2019-09-03 08:40 | 58540 | 0 | 88 | 172.51 | 2019-08-30 09:04 | 51010 | 7530 | 3.9833 | 5736 | 7530 | 0.26051 | 1961.6403 | 1.9616 | 3.4472 | 773 | 773 | 773 | 735 | 1577.551 | 1.5776 | 11.879 | 2.0709 | 20.8752
| 2019-09-10 08:55 | 70920 | 7.23 | 218.36 | 225.44 | 2019-09-06 09:15 | 63050 | 7870 | 3.9861 | 5740 | 7870 | 0.45103 | 3549.6061 | 3.5496 | 6.2335 | 955 | 954 | 954.5 | 739 | 1937.4154 | 1.9374 | 15.2475 | 2.6564 | 26.776
| 2019-09-11 09:00 | 73220 | 9.68 | 200.32 | 235.73 | 2019-09-06 09:15 | 63050 | 10170 | 4.9896 | 7185 | 10170 | 0.44573 | 4533.0741 | 4.5331 | 6.3596 | 1025 | 1015 | 1020 | 757 | 2021.1361 | 2.0211 | 20.555 | 2.8608 | 28.837
| 2019-09-12 07:56 | 75585 | 11.36 | 184.07 | 232.99 | 2019-09-06 09:15 | 63050 | 12535 | 5.9451 | 8561 | 12535 | 0.42842 | 5370.2447 | 5.3702 | 6.3231 | 1006 | 989 | 997.5 | 774 | 1933.1395 | 1.9331 | 24.2319 | 2.8305 | 28.5314
| 2019-09-18 09:30 | 87860 | 4.73 | 63.72 | 210.47 | 2019-09-13 08:59 | 77790 | 10070 | 5.0215 | 7231 | 10070 | 0.27892 | 2808.7244 | 2.8087 | 3.9154 | 906 | 917 | 911.5 | 762 | 1794.2913 | 1.7943 | 18.0685 | 2.4988 | 25.1875
| 2019-09-19 07:55 | 89600 | 11.28 | 46.33 | 210.64 | 2019-09-13 08:59 | 77790 | 11810 | 5.9556 | 8576 | 11810 | 0.26825 | 3168.0325 | 3.168 | 3.7236 | 853 | 881 | 867 | 781 | 1665.1729 | 1.6652 | 19.6657 | 2.2931 | 23.1145
| 2019-09-23 08:45 | 99330 | 8.72 | 125.93 | 180.64 | 2019-09-20 08:58 | 91670 | 7660 | 2.991 | 4307 | 7660 | 0.31529 | 2415.1214 | 2.4151 | 5.6523 | 820 | 821 | 820.5 | 737 | 1669.9457 | 1.6699 | 12.7918 | 2.97 | 29.9376
| 2019-09-24 08:46 | 102250 | 6.33 | 89.05 | 192.27 | 2019-09-20 08:58 | 91670 | 10580 | 3.9917 | 5748 | 10580 | 0.28765 | 3043.337 | 3.0433 | 5.337 | 796 | 804 | 800 | 736 | 1630.4348 | 1.6304 | 17.25 | 3.001 | 30.2505
| 2019-09-25 09:42 | 105650 | 6.21 | 69.81 | 213.77 | 2019-09-20 08:58 | 91670 | 13980 | 5.0306 | 7244 | 13980 | 0.28979 | 4051.2642 | 4.0513 | 5.6373 | 829 | 840 | 834.5 | 754 | 1660.1459 | 1.6601 | 23.2088 | 3.2039 | 32.295
| 2019-09-26 08:00 | 107680 | 4.4 | 56.86 | 214.27 | 2019-09-20 08:58 | 91670 | 16010 | 5.9597 | 8582 | 16010 | 0.27553 | 4411.2353 | 4.4112 | 5.1812 | 735 | 733 | 734 | 727 | 1514.4429 | 1.5144 | 24.2462 | 2.8252 | 28.4784
| 2019-09-30 08:05 | 117170 | 6.26 | 137.01 | 137.01 | 2019-09-27 08:56 | 109430 | 7740 | 2.9646 | 4269 | 7740 | 0.28028 | 2169.3672 | 2.1694 | 5.1223 | 779 | 760 | 769.5 | 769 | 1500.9753 | 1.501 | 11.6175 | 2.7214 | 27.4315
| 2019-10-01 08:17 | 119770 | 0 | 145.27 | 165.33 | 2019-09-27 08:17 | 109430 | 10340 | 4 | 5760 | 10340 | 0.3106 | 3211.604 | 3.2116 | 5.6203 | 719 | 730 | 724.5 | 760 | 1429.9342 | 1.4299 | 14.7855 | 2.5669 | 25.8747
| 2019-10-02 07:45 | 122080 | 0 | 141.2 | 200.64 | 2019-09-27 08:17 | 109430 | 12650 | 4.9778 | 7168 | 12650 | 0.34184 | 4324.276 | 4.3243 | 6.081 | 732 | 754 | 743 | 766 | 1454.9608 | 1.455 | 18.4053 | 2.5677 | 25.8824
| 2019-10-08 09:09 | 135510 | 5.22 | 38.82 | 179.56 | 2019-10-04 08:54 | 126170 | 9340 | 4.0104 | 5775 | 9340 | 0.2236 | 2088.424 | 2.0884 | 3.6452 | 745 | 758 | 751.5 | 776 | 1452.6418 | 1.4526 | 13.5677 | 2.3494 | 23.6818
| 2019-10-22 08:55 | 165710 | 3.8696 | 63.5368 | 150.2827 | 2019-10-18 09:02 | 156810 | 8900 | 3.9951 | 5753 | 8900 | 0.21769 | 1937.4333 | 1.9374 | 3.3946 | 678 | 682 | 680 | 727 | 1403.0261 | 1.403 | 12.4869 | 2.1705 | 21.8787
| 2019-10-24 | 171390 | 0 | 98.131 | 175.706 | 2019-10-18 09:02 | 156810 | 14580 | 5.6236 | 8098 | 14580 | 0.27384 | 3992.5435 | 3.9925 | 4.9697 | 700 | 741 | 720.5 | 727 | 1486.5887 | 1.4866 | 21.6745 | 2.6765 | 26.9793
| 29/10/2019 0853 | 180700 | 7.059 | 90.541 | 122.076 | 2019-10-25 08:56 | 173270 | 7430 | 5697 | 5697 | 7430 | 0.21968 | 1632.1927 | 1.6322 | 2.8879 | 840 | 838 | 839 | 787 | 1599.1105 | 1.5991 | 11.8814 | 2.0856 | 21.0224
| 2019-10-31 08:50 | 184950 | 6.56 | 113.52 | 147.48 | 2019-10-25 08:56 | 173270 | 11680 | 5.9958 | 8634 | 11680 | 0.26756 | 3125.1008 | 3.1251 | 3.6485 | 824 | 756 | 790 | 782 | 1515.3453 | 1.5153 | 17.6992 | 2.0499 | 20.6635
| 2019-11-07 | 198800 | 5.698 | 52.142 | 213.7 | 2019-11-01 00:09 | 187040 | 11760 | 5.9938 | 8631 | 11760 | 0.27154 | 3193.3104 | 3.1933 | 3.7294 | 823 | 851 | 837 | 748 | 1678.4759 | 1.6785 | 19.7389 | 2.287 | 23.0527
| 2019-11-12 08:52 | 209230 | 7.273 | 78.897 | 146.568 | 2019-11-08 09:00 | 201570 | 7660 | 3.9944 | 5752 | 7660 | 0.23274 | 1782.7731 | 1.7828 | 3.1242 | 737 | 734 | 735.5 | 775 | 1423.5484 | 1.4235 | 10.9044 | 1.8958 | 19.1092
| 2019-11-14 08:58 | 212820 | 3.7608 | 35.094 | 74.9339 | 2019-11-08 09:00 | 201570 | 11250 | 5.9986 | 8638 | 11250 | 0.11379 | 1280.1221 | 1.2801 | 1.4938 | 701 | 706 | 703.5 | 723 | 1459.5436 | 1.4595 | 16.4199 | 1.9009 | 19.1609
| 2019-11-19 08:59 | 222570 | 3.1269 | 43.4505 | 94.1694 | 2019-11-15 08:59 | 214270 | 8300 | 4 | 5760 | 8300 | 0.14075 | 1168.1986 | 1.1682 | 2.0443 | 730 | 766 | 748 | 746 | 1504.0214 | 1.504 | 12.4834 | 2.1673 | 21.8459
| 2019-11-20 08:30 | 225160 | 6.69 | 78.48 | 189.36 | 2019-11-15 08:59 | 214270 | 10890 | 4.9799 | 7171 | 10890 | 0.27453 | 2989.6317 | 2.9896 | 4.2024 | 817 | 789 | 803 | 760 | 1584.8684 | 1.5849 | 17.2592 | 2.4068 | 24.2606
| 2019-11-21 07:55 | 227650 | 8.08 | 74.93 | 198.47 | 2019-11-15 08:59 | 214270 | 13380 | 5.9556 | 8576 | 13380 | 0.28148 | 3766.2024 | 3.7662 | 4.4267 | 791 | 808 | 799.5 | 774 | 1549.4186 | 1.5494 | 20.7312 | 2.4174 | 24.3669
| 2019-11-26 09:05 | 238750 | 6.04 | 117.43 | 170.66 | 2019-11-22 08:58 | 230220 | 8530 | 4.0049 | 5767 | 8530 | 0.29413 | 2508.9289 | 2.5089 | 4.3853 | 820 | 822 | 821 | 781 | 1576.8246 | 1.5768 | 13.4503 | 2.3323 | 23.5095
| 2019-12-03 08:51 | 253500 | 10 | 75.07 | 186.94 | 2019-11-29 08:58 | 246030 | 7470 | 3.9951 | 5753 | 7470 | 0.27201 | 2031.9147 | 2.0319 | 3.5602 | 822 | 847 | 834.5 | 772 | 1621.4378 | 1.6214 | 12.1121 | 2.1054 | 21.222
| 2019-12-10 09:10 | 267420 | 6.81 | 75.55 | 154.01 | 2019-12-06 08:54 | 259530 | 7890 | 4.0111 | 5776 | 7890 | 0.23637 | 1864.9593 | 1.865 | 3.2546 | 738 | 728 | 733 | 761 | 1444.8095 | 1.4448 | 11.3995 | 1.9736 | 19.8939
| 2019-12-17 08:54 | 283560 | 0 | 138.48 | 181.43 | 2019-12-13 09:03 | 273360 | 10200 | 3.9937 | 5751 | 10200 | 0.31991 | 3263.082 | 3.2631 | 5.7193 | 782 | 748 | 765 | 782 | 1467.3913 | 1.4674 | 14.9674 | 2.6026 | 26.2339
| 2019-12-19 09:26 | 288170 | 13.32 | 136.56 | 222.49 | 2019-12-13 09:03 | 273360 | 14810 | 6.016 | 8663 | 14810 | 0.37237 | 5514.7997 | 5.5148 | 6.4169 | 744 | 735 | 739.5 | 737 | 1505.0882 | 1.5051 | 22.2904 | 2.5731 | 25.9364
| 2019-12-23 08:40 | 298010 | 4.08 | 171.83 | 137.46 | 2019-12-20 09:06 | 290290 | 7720 | 2.9819 | 4294 | 7720 | 0.31337 | 2419.2164 | 2.4192 | 5.679 | 743 | 780 | 761.5 | 738 | 1547.7642 | 1.5478 | 11.9487 | 2.7827 | 28.0492
| 2019-12-24 07:50 | 300740 | 4.82 | 149.12 | 150.98 | 2019-12-20 09:06 | 290290 | 10450 | 3.9472 | 5684 | 10450 | 0.30492 | 3186.414 | 3.1864 | 5.6508 | 759 | 759 | 759 | 742 | 1534.3666 | 1.5344 | 16.0341 | 2.8209 | 28.4349
| 2019-12-31 08:18 | 318930 | 14.51 | 110.73 | 154.25 | 2019-12-27 08:45 | 307820 | 11110 | 3.9813 | 5733 | 11110 | 0.27949 | 3105.1339 | 3.1051 | 5.4596 | 726 | 759 | 742.5 | 757 | 1471.2682 | 1.4713 | 16.3458 | 2.8512 | 28.7398
| 2020-01-02 09:18 | 324110 | 11.38 | 104.58 | 154.93 | 2019-12-27 08:45 | 307820 | 16290 | 6.0229 | 8673 | 16290 | 0.27089 | 4412.7981 | 4.4128 | 5.1287 | 762 | 760 | 761 | 721 | 1583.2178 | 1.5832 | 25.7906 | 2.9737 | 29.9746
| 2020-01-07 08:59 | 334560 | 10.59 | 140.44 | 131.2 | 2020-01-03 08:57 | 326090 | 8470 | 4.0014 | 5762 | 8470 | 0.28223 | 2390.4881 | 2.3905 | 4.1819 | 745 | 794 | 769.5 | 770 | 1499.026 | 1.499 | 12.6967 | 2.2035 | 22.2116
| 2020-01-14 08:45 | 349610 | 6.18 | 51.6 | 149.65 | 2020-01-10 09:04 | 341300 | 8310 | 3.9868 | 5741 | 8310 | 0.20743 | 1723.7433 | 1.7237 | 3.0265 | 592 | 583 | 587.5 | 782 | 1126.9182 | 1.1269 | 9.3647 | 1.6312 | 16.4424
| 2020-01-21 08:55 | 366460 | 22.89 | 100.46 | 155.43 | 2020-01-17 08:55 | 356370 | 10090 | 4 | 5760 | 10090 | 0.27878 | 2812.8902 | 2.8129 | 4.9226 | 695 | 728 | 711.5 | 728 | 1466.0027 | 1.466 | 14.792 | 2.568 | 25.8859
| 2020-01-22 08:48 | 368590 | 28.01 | 190.01 | 85.66 | 2020-01-17 08:55 | 356370 | 12220 | 4.9951 | 7193 | 12220 | 0.30368 | 3710.9696 | 3.711 | 5.2004 | 684 | 696 | 690 | 759 | 1363.6364 | 1.3636 | 16.6636 | 2.3166 | 23.3518
| 2020-01-28 09:07 | 383380 | 10.45 | 176.41 | 220.55 | 2020-01-24 08:50 | 373070 | 10310 | 4.0118 | 5777 | 10310 | 0.40741 | 4200.3971 | 4.2004 | 7.3291 | 849 | 871 | 860 | 758 | 1701.847 | 1.7018 | 17.546 | 3.0372 | 30.6152
| 2020-01-29 08:58 | 385880 | 9.3 | 160.32 | 237.49 | 2020-01-24 08:50 | 373070 | 12810 | 5.0056 | 7208 | 12810 | 0.40711 | 5215.0791 | 5.2151 | 7.293 | 863 | 858 | 860.5 | 766 | 1685.0522 | 1.6851 | 21.5855 | 2.9947 | 30.1862
| 2020-01-30 09:01 | 388320 | 12.33 | 137.11 | 241.43 | 2020-01-24 08:50 | 373070 | 15250 | 6.0076 | 8651 | 15250 | 0.39087 | 5960.7675 | 5.9608 | 6.9454 | 816 | 843 | 829.5 | 762 | 1632.874 | 1.6329 | 24.9013 | 2.8784 | 29.0146
| 2020-02-04 08:57 | 398900 | 20.1 | 105.02 | 211.08 | 2020-01-31 08:00 | 389660 | 9240 | 4.0396 | 5817 | 9240 | 0.3362 | 3106.488 | 3.1065 | 5.3831 | 747 | 740 | 743.5 | 727 | 1534.044 | 1.534 | 14.1746 | 2.4367 | 24.5624
| 2020-02-11 08:51 | 415270 | 0 | 38.99 | 149.51 | 2020-02-07 08:55 | 405740 | 9530 | 3.9972 | 5756 | 9530 | 0.1885 | 1796.405 | 1.7964 | 3.1459 | 612 | 590 | 601 | 748 | 1205.2139 | 1.2052 | 11.4857 | 1.9954 | 20.1139
| 2020-02-18 09:02 | 434710 | 12.37 | 101.33 | 143.95 | 2020-02-14 09:07 | 423340 | 11370 | 3.9965 | 5755 | 11370 | 0.25765 | 2929.4805 | 2.9295 | 5.131 | 702 | 718 | 710 | 768 | 1386.7188 | 1.3867 | 15.767 | 2.7397 | 27.6162
| 2020-02-19 10:59 | 437820 | 9.37 | 84.774 | 163.72 | 2020-02-14 09:07 | 423340 | 14480 | 5.0778 | 7312 | 14480 | 0.25786 | 3733.8707 | 3.7339 | 5.1473 | 745 | 721 | 733 | 775 | 1418.7097 | 1.4187 | 20.5429 | 2.8095 | 28.3196
| 2020-02-20 10:07 | 439990 | 18.34 | 70.95 | 184.18 | 2020-02-14 09:07 | 423340 | 16650 | 6.0417 | 8700 | 16650 | 0.27347 | 4553.2755 | 4.5533 | 5.2755 | 712 | 701 | 706.5 | 712 | 1488.4129 | 1.4884 | 24.7821 | 2.8485 | 28.713
| 2020-02-25 08:55 | 452930 | 10.45 | 66.08 | 175.94 | 2020-02-21 08:55 | 441980 | 10950 | 4 | 5760 | 10950 | 0.25247 | 2764.5465 | 2.7645 | 4.838 | 725 | 687 | 706 | 749 | 1413.8852 | 1.4139 | 15.482 | 2.6879 | 27.0936
| 2020-02-26 08:52 | 455430 | 4.35 | 59.87 | 147.13 | 2020-02-21 08:55 | 441980 | 13450 | 4.9979 | 7197 | 13450 | 0.21135 | 2842.6575 | 2.8427 | 3.9814 | 679 | 683 | 681 | 721 | 1416.7822 | 1.4168 | 19.0557 | 2.6477 | 26.6891
| 2020-02-27 10:02 | 458210 | 0 | 60.17 | 153.88 | 2020-02-21 08:55 | 441980 | 16230 | 6.0465 | 8707 | 16230 | 0.21405 | 3474.0315 | 3.474 | 4.0218 | 713 | 713 | 713 | 774 | 1381.7829 | 1.3818 | 22.4263 | 2.5757 | 25.9627
| 2020-03-03 09:13 | 470120 | 77.09 | 96.89 | 119.37 | 2020-02-28 09:00 | 460430 | 9690 | 4.009 | 5773 | 9690 | 0.29335 | 2842.5615 | 2.8426 | 4.9633 | 668 | 654 | 661 | 746 | 1329.0885 | 1.3291 | 12.8789 | 2.2309 | 22.4873
| 2020-03-10 09:08 | 486310 | 79.06 | 32.35 | 125.71 | 2020-03-06 09:00 | 476120 | 10190 | 4.0056 | 5768 | 10190 | 0.23712 | 2416.2528 | 2.4163 | 4.2226 | 627 | 644 | 635.5 | 773 | 1233.1824 | 1.2332 | 12.5661 | 2.1786 | 21.9602
| 2020-03-17 08:56 | 4860 | 96.81 | 54.14 | 180.69 | 2020-03-13 08:55 | 493490 | 11370 | 4.0007 | 5761 | 11370 | 0.33164 | 3770.7468 | 3.7707 | 6.5977 | 816 | 803 | 809.5 | 761 | 1595.5979 | 1.5956 | 18.1419 | 3.1491 | 31.7429
| 2020-03-18 08:50 | 7200 | 93.19 | 34.97 | 199.96 | 2020-03-13 08:55 | 493490 | 13710 | 4.9965 | 7195 | 13710 | 0.32812 | 4498.5252 | 4.4985 | 6.3023 | 742 | 769 | 755.5 | 757 | 1497.0277 | 1.497 | 20.5243 | 2.8526 | 28.7539
| 2020-03-19 08:56 | 9610 | 75.87 | 14.69 | 191.97 | 2020-03-13 08:55 | 493490 | 16120 | 6.0007 | 8641 | 16120 | 0.28253 | 4554.3836 | 4.5544 | 5.3128 | 758 | 753 | 755.5 | 764 | 1483.3115 | 1.4833 | 23.911 | 2.7672 | 27.8929
| 2020-03-24 08:50 | 21780 | 92.35 | 106.25 | 194.74 | 2020-03-20 09:00 | 12130 | 9650 | 3.9931 | 5750 | 9650 | 0.39334 | 3795.731 | 3.7957 | 6.6541 | 744 | 739 | 741.5 | 781 | 1424.1357 | 1.4241 | 13.7429 | 2.3901 | 24.0919
| 2020-03-31 09:00 | 38400 | 68.16 | 103.04 | 45.33 | 2020-03-27 09:00 | 28790 | 9610 | 4 | 5760 | 9610 | 0.21653 | 2080.8533 | 2.0809 | 3.6415 | 548 | 520 | 534 | 765 | 1047.0588 | 1.0471 | 10.0622 | 1.7469 | 17.6089
| 2020-04-07 09:00 | 56490 | 13.29 | 36.75 | 129.95 | 2020-04-03 08:55 | 46130 | 10360 | 4.0035 | 5765 | 10360 | 0.17999 | 1864.6964 | 1.8647 | 3.2604 | 555 | 544 | 549.5 | 756 | 1090.2778 | 1.0903 | 11.2953 | 1.9593 | 19.7496
| 2020-04-14 09:00 | 73280 | 31.88 | 30.88 | 112.92 | 2020-04-09 09:00 | 61360 | 11920 | 5 | 7200 | 11920 | 0.17568 | 2094.1056 | 2.0941 | 2.9317 | 564 | 562 | 563 | 772 | 1093.9119 | 1.0939 | 13.0394 | 1.811 | 18.2552
| 2020-04-21 08:57 | 90340 | 30.78 | 33.83 | 123.88 | 2020-04-17 09:03 | 80770 | 9570 | 3.9958 | 5754 | 9570 | 0.18849 | 1803.8493 | 1.8038 | 3.16 | 553 | 557 | 555 | 790 | 1053.7975 | 1.0538 | 10.0848 | 1.7527 | 17.6669
| 2020-04-28 08:55 | 106110 | 37.13 | 201.42 | 138.69 | 2020-04-24 09:00 | 96880 | 9230 | 3.9965 | 5755 | 9230 | 0.37724 | 3481.9252 | 3.4819 | 6.0987 | 713 | 714 | 713.5 | 770 | 1389.9351 | 1.3899 | 12.8291 | 2.2292 | 22.4704
| 2020-05-05 08:56 | 122180 | 28.71 | 56.07 | 143.45 | 2020-05-01 09:02 | 112080 | 10100 | 3.9958 | 5754 | 10100 | 0.22823 | 2305.123 | 2.3051 | 4.0382 | 597 | 602 | 599.5 | 779 | 1154.3646 | 1.1544 | 11.6591 | 2.0263 | 20.4247
| 2020-05-12 08:53 | 138670 | 22.53 | 72.99 | 153.71 | 2020-05-07 08:57 | 126200 | 12470 | 4.9972 | 7196 | 12470 | 0.24923 | 3107.8981 | 3.1079 | 4.3535 | 656 | 617 | 636.5 | 747 | 1278.1124 | 1.2781 | 15.9381 | 2.2149 | 22.3257
| 2020-05-19 08:55 | 154790 | 34.54 | 179.13 | 65.06 | 2020-05-15 08:55 | 145220 | 9570 | 4 | 5760 | 9570 | 0.27873 | 2667.4461 | 2.6674 | 4.668 | 754 | 752 | 753 | 761 | 1484.2313 | 1.4842 | 14.2041 | 2.466 | 24.8572
| 2020-05-26 08:54 | 170080 | 34.63 | 49.72 | 135.87 | 2020-05-22 08:57 | 161240 | 8840 | 3.9979 | 5757 | 8840 | 0.22022 | 1946.7448 | 1.9467 | 3.4086 | 654 | 664 | 659 | 774 | 1277.1318 | 1.2771 | 11.2898 | 1.9611 | 19.7675
| 2020-06-02 08:55 | 186880 | 38.62 | 19.37 | 152.76 | 2020-05-29 08:47 | 177210 | 9670 | 4.0056 | 5768 | 9670 | 0.21075 | 2037.9525 | 2.038 | 3.5615 | 573 | 565 | 569 | 769 | 1109.883 | 1.1099 | 10.7326 | 1.8607 | 18.7559
| 2020-06-09 08:58 | 204420 | 32.75 | 120.93 | 169.43 | 2020-06-05 08:57 | 193800 | 10620 | 4.0007 | 5761 | 10620 | 0.32311 | 3431.4282 | 3.4314 | 6.004 | 757 | 753 | 755 | 759 | 1492.0949 | 1.4921 | 15.846 | 2.7506 | 27.7258
| 2020-06-10 08:50 | 207110 | 12.71 | 104.15 | 165.15 | 2020-06-05 08:57 | 193800 | 13310 | 4.9951 | 7193 | 13310 | 0.28201 | 3753.5531 | 3.7536 | 5.2601 | 700 | 778 | 739 | 754 | 1470.1592 | 1.4702 | 19.5678 | 2.7204 | 27.4216
| 2020-06-11 08:55 | 209750 | 31.91 | 86.86 | 176.65 | 2020-06-05 08:57 | 193800 | 15950 | 5.9986 | 8638 | 15950 | 0.29542 | 4711.949 | 4.7119 | 5.4985 | 655 | 663 | 659 | 765 | 1292.1569 | 1.2922 | 20.6099 | 2.386 | 24.0505
| 2020-06-16 08:54 | 223550 | 22.71 | 85.27 | 190.11 | 2020-06-12 08:48 | 212610 | 10940 | 4.0042 | 5766 | 10940 | 0.29809 | 3261.1046 | 3.2611 | 5.701 | 773 | 813 | 793 | 768 | 1548.8281 | 1.5488 | 16.9442 | 2.9386 | 29.6215
| 2020-06-17 08:49 | 226390 | 21.2 | 85.3 | 197.8 | 2020-06-12 08:48 | 212610 | 13780 | 5.0007 | 7201 | 13780 | 0.3043 | 4193.254 | 4.1933 | 5.8697 | 801 | 814 | 807.5 | 773 | 1566.947 | 1.5669 | 21.5925 | 2.9985 | 30.2253
| 2020-06-18 09:26 | 228610 | 18.48 | 59.35 | 212.1 | 2020-06-12 08:48 | 212610 | 16000 | 6.0264 | 8678 | 16000 | 0.28993 | 4638.88 | 4.6389 | 5.3883 | 708 | 746 | 727 | 735 | 1483.6735 | 1.4837 | 23.7388 | 2.7355 | 27.574
| 2020-06-23 08:52 | 240610 | 38.16 | 66.34 | 188.17 | 2020-06-19 08:46 | 230480 | 10130 | 4.0042 | 5766 | 10130 | 0.29267 | 2964.7471 | 2.9647 | 5.1829 | 658 | 660 | 659 | 754 | 1311.008 | 1.311 | 13.2805 | 2.3032 | 23.2167
| 2020-06-24 08:50 | 242890 | 36.9 | 34.59 | 195.57 | 2020-06-19 08:46 | 230480 | 12410 | 5.0028 | 7204 | 12410 | 0.26706 | 3314.2146 | 3.3142 | 4.6373 | 630 | 647 | 638.5 | 737 | 1299.5251 | 1.2995 | 16.1271 | 2.2386 | 22.5654
| 2020-06-30 08:50 | 256880 | 194.12 | 36.61 | 141.7 | 2020-06-26 08:47 | 247840 | 9040 | 4.0021 | 5763 | 9040 | 0.37243 | 3366.7672 | 3.3668 | 5.8888 | 521 | 536 | 528.5 | 787 | 1007.3062 | 1.0073 | 9.106 | 1.5801 | 15.9273
| 2020-07-07 08:57 | 273960 | 23 | 33.93 | 135.37 | 2020-07-03 08:55 | 264600 | 9360 | 4.0014 | 5762 | 9360 | 0.1923 | 1799.928 | 1.7999 | 3.1488 | 552 | 524 | 538 | 730 | 1105.4795 | 1.1055 | 10.3473 | 1.7958 | 18.1015
| 2020-07-14 09:00 | 291140 | 31.96 | 102.37 | 140.07 | 2020-07-10 08:50 | 280910 | 10230 | 4.0069 | 5770 | 10230 | 0.2744 | 2807.112 | 2.8071 | 4.9039 | 689 | 724 | 706.5 | 751 | 1411.1185 | 1.4111 | 14.4357 | 2.5019 | 25.2188
| 2020-07-21 08:55 | 308030 | 37.75 | 150.97 | 29.3 | 2020-07-17 08:50 | 298700 | 9330 | 4.0035 | 5765 | 9330 | 0.21802 | 2034.1266 | 2.0341 | 3.5566 | 573 | 551 | 562 | 779 | 1082.1566 | 1.0822 | 10.0965 | 1.7513 | 17.6536
| 2020-07-28 08:57 | 322286 | 31.2314 | 51.3023 | 152.688 | 2020-07-24 08:52 | 312500 | 9786 | 4.0035 | 5765 | 9786 | 0.23522 | 2301.879 | 2.3019 | 4.0248 | 576 | 569 | 572.5 | 756 | 1135.9127 | 1.1359 | 11.116 | 1.9282 | 19.4362
| 2020-08-04 08:51 | 339370 | 34.88 | 54.86 | 112.45 | 2020-07-31 08:56 | 329360 | 10010 | 3.9965 | 5755 | 10010 | 0.20219 | 2023.9219 | 2.0239 | 3.5449 | 556 | 568 | 562 | 750 | 1124 | 1.124 | 11.2512 | 1.955 | 19.7068
| 2020-08-11 08:54 | 356490 | 36.03 | 82.17 | 224.45 | 2020-08-07 08:52 | 346470 | 10020 | 4.0014 | 5762 | 10020 | 0.34265 | 3433.353 | 3.4334 | 6.0063 | 751 | 752 | 751.5 | 760 | 1483.2237 | 1.4832 | 14.8619 | 2.5793 | 25.9993
| 2020-08-12 08:45 | 359090 | 29.2 | 47.15 | 228.64 | 2020-08-07 08:52 | 346470 | 12620 | 4.9951 | 7193 | 12620 | 0.30499 | 3848.9738 | 3.849 | 5.3938 | 786 | 783 | 784.5 | 760 | 1548.3553 | 1.5484 | 19.5402 | 2.7166 | 27.383
| 2020-08-13 08:38 | 361400 | 27.2 | 12.3 | 237.1 | 2020-08-07 08:52 | 346470 | 14930 | 5.9903 | 8626 | 14930 | 0.2766 | 4129.638 | 4.1296 | 4.8257 | 749 | 726 | 737.5 | 740 | 1494.9324 | 1.4949 | 22.3193 | 2.5874 | 26.0815
| 2020-08-18 09:27 | 374990 | 21.9 | 118.21 | 152.2 | 2020-08-14 08:55 | 363940 | 11050 | 4.0222 | 5792 | 11050 | 0.29231 | 3230.0255 | 3.23 | 5.6213 | 721 | 730 | 725.5 | 735 | 1480.6122 | 1.4806 | 16.3608 | 2.8247 | 28.4732
| 2020-08-19 08:50 | 377410 | 23.69 | 94.189 | 201.26 | 2020-08-14 08:55 | 363940 | 13470 | 4.9965 | 7195 | 13470 | 0.31914 | 4298.8023 | 4.2988 | 6.0225 | 680 | 693 | 686.5 | 751 | 1371.1718 | 1.3712 | 18.4697 | 2.567 | 25.8755
| 2020-08-20 08:45 | 380020 | 25.57 | 62.8 | 222.87 | 2020-08-14 08:55 | 363940 | 16080 | 5.9931 | 8630 | 16080 | 0.31124 | 5004.7392 | 5.0047 | 5.8456 | 768 | 754 | 761 | 772 | 1478.6269 | 1.4786 | 23.7763 | 2.7551 | 27.7712
| 2020-08-25 08:40 | 392810 | 46.46 | 226.79 | 231.29 | 2020-08-21 08:45 | 382840 | 9970 | 3.9965 | 5755 | 9970 | 0.50454 | 5030.2638 | 5.0303 | 8.8106 | 756 | 771 | 763.5 | 741 | 1545.5466 | 1.5455 | 15.4091 | 2.6775 | 26.9894
| 2020-08-26 08:15 | 395130 | 43.17 | 189.11 | 224.09 | 2020-08-21 08:45 | 382840 | 12290 | 4.9792 | 7170 | 12290 | 0.45637 | 5608.7873 | 5.6088 | 7.8852 | 750 | 778 | 764 | 783 | 1463.6015 | 1.4636 | 17.9877 | 2.5087 | 25.2881
| 2020-08-27 07:50 | 397650 | 36.76 | 142.83 | 214.83 | 2020-08-21 08:45 | 382840 | 14810 | 5.9618 | 8585 | 14810 | 0.39442 | 5841.3602 | 5.8414 | 6.8586 | 728 | 686 | 707 | 759 | 1397.2332 | 1.3972 | 20.693 | 2.4104 | 24.2965
| 2020-09-01 08:35 | 409850 | 84.38 | 130.14 | 154.82 | 2020-08-28 08:41 | 400330 | 9520 | 3.9958 | 5754 | 9520 | 0.36934 | 3516.1168 | 3.5161 | 6.1596 | 639 | 616 | 627.5 | 774 | 1216.0853 | 1.2161 | 11.5771 | 2.012 | 20.2811
| 2020-09-08 08:35 | 427490 | 83.99 | 260.88 | 217.08 | 2020-09-04 09:00 | 417330 | 10160 | 3.9826 | 5735 | 10160 | 0.56195 | 5709.412 | 5.7094 | 10.035 | 809 | 839 | 824 | 773 | 1598.9651 | 1.599 | 16.2455 | 2.8327 | 28.5535
| 2020-09-08 13:33 | 427840 | 82.01 | 263.14 | 219.72 | 2020-09-04 09:00 | 417330 | 10510 | 4.1896 | 6033 | 10510 | 0.56487 | 5936.7837 | 5.9368 | 9.9192 | 809 | 839 | 824 | 773 | 1598.9651 | 1.599 | 16.8051 | 2.7855 | 28.0782
| 2020-09-09 08:30 | 429620 | 83.03 | 186.59 | 243.82 | 2020-09-04 09:00 | 417330 | 12290 | 4.9792 | 7170 | 12290 | 0.51344 | 6310.1776 | 6.3102 | 8.8712 | 684 | 695 | 689.5 | 754 | 1371.6844 | 1.3717 | 16.858 | 2.3512 | 23.7
| 2020-09-10 08:20 | 431910 | 68.91 | 138.58 | 256.2 | 2020-09-04 09:00 | 417330 | 14580 | 5.9722 | 8600 | 14580 | 0.46369 | 6760.6002 | 6.7606 | 7.9241 | 702 | 697 | 699.5 | 785 | 1336.6242 | 1.3366 | 19.488 | 2.266 | 22.8417
| 2020-09-15 08:30 | 445410 | 105.24 | 105.28 | 147.78 | 2020-09-11 08:48 | 434530 | 10880 | 3.9875 | 5742 | 10880 | 0.3583 | 3898.304 | 3.8983 | 6.8434 | 686 | 688 | 687 | 780 | 1321.1538 | 1.3212 | 14.3742 | 2.5033 | 25.2336
| 2020-09-16 08:35 | 447750 | 76 | 69.31 | 160.25 | 2020-09-11 08:48 | 434530 | 13220 | 4.991 | 7187 | 13220 | 0.30556 | 4039.5032 | 4.0395 | 5.6655 | 688 | 667 | 677.5 | 797 | 1275.0941 | 1.2751 | 16.8567 | 2.3454 | 23.6421
| 2020-09-22 08:50 | 463980 | 63.33 | 76.38 | 186.13 | 2020-09-18 08:45 | 452910 | 11070 | 4.0035 | 5765 | 11070 | 0.32584 | 3607.0488 | 3.607 | 6.3069 | 739 | 704 | 721.5 | 763 | 1418.4142 | 1.4184 | 15.7018 | 2.7237 | 27.4544
| 2020-09-23 08:30 | 466790 | 59.03 | 74.86 | 163.07 | 2020-09-18 08:45 | 452910 | 13880 | 4.9896 | 7185 | 13880 | 0.29696 | 4121.8048 | 4.1218 | 5.7826 | 710 | 729 | 719.5 | 766 | 1408.9426 | 1.4089 | 19.5561 | 2.7218 | 27.4357
| 2020-09-24 08:29 | 469330 | 59.98 | 69.83 | 183.91 | 2020-09-18 08:45 | 452910 | 16420 | 5.9889 | 8624 | 16420 | 0.31372 | 5151.2824 | 5.1513 | 6.021 | 716 | 719 | 717.5 | 760 | 1416.1184 | 1.4161 | 23.2527 | 2.6963 | 27.1784
| 2020-09-29 09:07 | 482660 | 73.64 | 73.23 | 214.98 | 2020-09-25 08:35 | 472200 | 10460 | 4.0222 | 5792 | 10460 | 0.36185 | 3784.951 | 3.785 | 6.5871 | 605 | 601 | 603 | 746 | 1212.4665 | 1.2125 | 12.6824 | 2.1896 | 22.0716
| 2020-09-30 08:45 | 485550 | 57.97 | 53.6 | 186.85 | 2020-09-25 08:35 | 472200 | 13350 | 5.0069 | 7210 | 13350 | 0.29842 | 3983.907 | 3.9839 | 5.5697 | 526 | 553 | 539.5 | 737 | 1098.0326 | 1.098 | 14.6587 | 2.0331 | 20.4938
| 2020-10-06 08:46 | 800 | 35.65 | 100.91 | 223.5 | 2020-10-02 08:36 | 15250 | 15250 | 4.0069 | 5770 | -14450 | 0.36006 | -5202.867 | -5.2029 | -9.0892 | 629 | 648 | 638.5 | 767 | 1248.6962 | 1.2487 | 19.0426 | 3.3003 | 33.2668
| 2020-10-13 08:50 | 17660 | 51.39 | 167.01 | 275.61 | 2020-10-09 08:50 | 7600 | 10060 | 4 | 5760 | 10060 | 0.49401 | 4969.7406 | 4.9697 | 8.697 | 869 | 897 | 883 | 756 | 1751.9841 | 1.752 | 17.625 | 3.0599 | 30.8437
| 2020-10-14 08:48 | 20100 | 36.2 | 152.31 | 279.32 | 2020-10-09 08:50 | 7600 | 12500 | 4.9986 | 7198 | 12500 | 0.46783 | 5847.875 | 5.8479 | 8.1893 | 828 | 832 | 830 | 754 | 1651.1936 | 1.6512 | 20.6399 | 2.8675 | 28.9039
| 2020-10-15 09:13 | 22450 | 32.62 | 113.13 | 294.69 | 2020-10-09 08:50 | 7600 | 14850 | 6.016 | 8663 | 14850 | 0.44044 | 6540.534 | 6.5405 | 7.6104 | 795 | 791 | 793 | 783 | 1519.1571 | 1.5192 | 22.5595 | 2.6041 | 26.2495
| 2020-10-20 08:59 | 31830 | 48.13 | 93.16 | 243.51 | 2020-10-16 08:35 | 23920 | 7910 | 4.0167 | 5784 | 7910 | 0.3848 | 3043.768 | 3.0438 | 5.3045 | 808 | 792 | 800 | 783 | 1532.567 | 1.5326 | 12.1226 | 2.0959 | 21.1265
| 2020-10-27 08:55 | 48090 | 28.86 | 19.4 | 112.92 | 2020-10-20 09:03 | 38020 | 10070 | 6.9944 | 10072 | 10070 | 0.16118 | 1623.0826 | 1.6231 | 1.6244 | 255 | 255 | 255 | 753 | 507.9681 | 0.50797 | 5.1152 | 0.50787 | 5.1193
| 2020-10-29 08:19 | 52350 | 22.4 | 31.04 | 88.07 | 2020-10-20 09:03 | 38020 | 14330 | 8.9694 | 12927 | 14330 | 0.14151 | 2027.8383 | 2.0278 | 1.5812 | 281 | 296 | 288.5 | 756 | 572.4206 | 0.57242 | 8.2028 | 0.63455 | 6.3962
| 2020-11-03 09:00 | 62970 | 55.35 | 103.15 | 209.76 | 2020-10-30 08:20 | 54490 | 8480 | 4.0278 | 5800 | 8480 | 0.36826 | 3122.8448 | 3.1228 | 5.4273 | 683 | 693 | 688 | 735 | 1404.0816 | 1.4041 | 11.9066 | 2.0529 | 20.6929
| 2020-11-10 08:50 | 76900 | 47.69 | 71.1 | 155.66 | 2020-11-06 08:28 | 69080 | 7820 | 4.0153 | 5782 | 7820 | 0.27445 | 2146.199 | 2.1462 | 3.7416 | 604 | 599 | 601.5 | 744 | 1212.7016 | 1.2127 | 9.4833 | 1.6401 | 16.5327
| 2020-11-17 08:52 | 91520 | 89.23 | 52.2 | 154.27 | 2020-11-13 08:47 | 83320 | 8200 | 4.0035 | 5765 | 8200 | 0.2957 | 2424.74 | 2.4247 | 4.2396 | 578 | 553 | 565.5 | 757 | 1120.5416 | 1.1205 | 9.1884 | 1.5938 | 16.0658
| 2020-11-24 08:47 | 106750 | 84.28 | 156.68 | 105.06 | 2020-11-20 08:58 | 97810 | 8940 | 3.9924 | 5749 | 8940 | 0.34602 | 3093.4188 | 3.0934 | 5.4238 | 744 | 767 | 755.5 | 772 | 1467.9404 | 1.4679 | 13.1234 | 2.2827 | 23.0099
| 2020-11-26 09:24 | 111200 | 42.67 | 170.26 | 131.5 | 2020-11-20 08:58 | 97810 | 13390 | 6.0181 | 8666 | 13390 | 0.34443 | 4611.9177 | 4.6119 | 5.3644 | 781 | 774 | 777.5 | 722 | 1615.3047 | 1.6153 | 21.6289 | 2.4958 | 25.158
| 2020-12-01 08:52 | 121410 | 46.99 | 121.795 | 168.18 | 2020-11-27 08:44 | 113540 | 7870 | 4.0056 | 5768 | 7870 | 0.33697 | 2651.9145 | 2.6519 | 4.6344 | 806 | 794 | 800 | 768 | 1562.5 | 1.5625 | 12.2969 | 2.1319 | 21.4897
| 2020-12-08 09:00 | 136220 | 54.589 | 206.327 | 135.1605 | 2020-12-04 08:40 | 127090 | 9130 | 4.0139 | 5780 | 9130 | 0.39608 | 3616.1784 | 3.6162 | 6.3064 | 548 | 534 | 541 | 749 | 1083.4446 | 1.0834 | 9.8918 | 1.7114 | 17.2508
| 2020-12-09 08:56 | 138160 | 54.21 | 159.01 | 147.26 | 2020-12-04 08:40 | 127090 | 11070 | 5.0111 | 7216 | 11070 | 0.36048 | 3990.5136 | 3.9905 | 5.5743 | 485 | 514 | 499.5 | 723 | 1036.3071 | 1.0363 | 11.4719 | 1.5898 | 16.0251
| 2020-12-15 08:42 | 152320 | 55.37 | 106.66 | 290.31 | 2020-12-11 08:40 | 142470 | 9850 | 4.0014 | 5762 | 9850 | 0.45234 | 4455.549 | 4.4555 | 7.7945 | 815 | 815 | 815 | 760 | 1608.5526 | 1.6086 | 15.8442 | 2.7498 | 27.7178
| 2020-12-16 08:40 | 154580 | 42.32 | 90.14 | 305.36 | 2020-12-11 08:40 | 142470 | 12110 | 5 | 7200 | 12110 | 0.43782 | 5302.0002 | 5.302 | 7.4228 | 799 | 780 | 789.5 | 756 | 1566.4683 | 1.5665 | 18.9699 | 2.6347 | 26.5579
| 2020-12-17 08:37 | 156630 | 48.04 | 83.8 | 301.4 | 2020-12-11 08:40 | 142470 | 14160 | 5.9979 | 8637 | 14160 | 0.43324 | 6134.6784 | 6.1347 | 7.1596 | 842 | 849 | 845.5 | 756 | 1677.5794 | 1.6776 | 23.7545 | 2.7503 | 27.7232
| 2020-12-22 08:44 | 167470 | 47.04 | 117.97 | 237.24 | 2020-12-18 08:49 | 158450 | 9020 | 3.9965 | 5755 | 9020 | 0.40225 | 3628.295 | 3.6283 | 6.355 | 887 | 895 | 891 | 743 | 1798.7887 | 1.7988 | 16.2251 | 2.8193 | 28.4185
| 2020-12-23 08:37 | 169800 | 42.87 | 91.77 | 256.41 | 2020-12-18 08:49 | 158450 | 11350 | 4.9917 | 7188 | 11350 | 0.39105 | 4438.4175 | 4.4384 | 6.2242 | 884 | 898 | 891 | 759 | 1760.8696 | 1.7609 | 19.9859 | 2.7804 | 28.0269
| 2020-12-29 08:38 | 184510 | 45.12 | 109.27 | 237.27 | 2020-12-24 08:30 | 172240 | 12270 | 5.0056 | 7208 | 12270 | 0.39166 | 4805.6682 | 4.8057 | 6.7205 | 802 | 842 | 822 | 744 | 1657.2581 | 1.6573 | 20.3346 | 2.8211 | 28.4368
| 2021-01-05 08:44 | 199630 | 43.14 | 154.66 | 180.13 | 2020-12-31 08:45 | 188890 | 10740 | 4.9993 | 7199 | 10740 | 0.37793 | 4058.9682 | 4.059 | 5.6833 | 738 | 754 | 746 | 758 | 1476.2533 | 1.4763 | 15.855 | 2.2024 | 22.2
| 2021-01-07 10:00 | 204130 | 43.48 | 124.23 | 204.03 | 2020-12-31 08:45 | 188890 | 15240 | 7.0521 | 10155 | 15240 | 0.37174 | 5665.3176 | 5.6653 | 5.6235 | 717 | 722 | 719.5 | 733 | 1472.3738 | 1.4724 | 22.439 | 2.2096 | 22.2733
| 2021-01-12 08:40 | 215160 | 49.31 | 85.18 | 141.39 | 2021-01-08 08:49 | 206080 | 9080 | 3.9937 | 5751 | 9080 | 0.27588 | 2504.9904 | 2.505 | 4.3906 | 683 | 707 | 695 | 759 | 1373.5178 | 1.3735 | 12.4715 | 2.1686 | 21.8594
| 2021-01-13 08:45 | 217410 | 47.09 | 80.81 | 179.18 | 2021-01-08 08:49 | 206080 | 11330 | 4.9972 | 7196 | 11330 | 0.30708 | 3479.2164 | 3.4792 | 4.8736 | 744 | 684 | 714 | 803 | 1333.7484 | 1.3337 | 15.1114 | 2.1 | 21.1677
| 2021-01-14 14:37 | 220590 | 50.76 | 60.95 | 199.41 | 2021-01-08 08:49 | 206080 | 14510 | 6.2417 | 8988 | 14510 | 0.31112 | 4514.3512 | 4.5144 | 5.0628 | 624 | 620 | 622 | 781 | 1194.6223 | 1.1946 | 17.334 | 1.9286 | 19.44
| 2021-01-19 08:45 | 231070 | 39.72 | 81.9 | 185.31 | 2021-01-15 08:30 | 222260 | 8810 | 4.0104 | 5775 | 8810 | 0.30693 | 2704.0533 | 2.7041 | 4.7198 | 629 | 674 | 651.5 | 739 | 1322.3951 | 1.3224 | 11.6503 | 2.0174 | 20.3351
| 2021-01-20 08:40 | 233310 | 82.71 | 36.01 | 208.54 | 2021-01-15 08:30 | 222260 | 11050 | 5.0069 | 7210 | 11050 | 0.32726 | 3616.223 | 3.6162 | 5.0557 | 733 | 745 | 739 | 715 | 1550.3497 | 1.5503 | 17.1314 | 2.3761 | 23.9506
| 2021-01-26 08:42 | 246650 | 124.38 | 45.48 | 152.69 | 2021-01-22 08:45 | 237700 | 8950 | 3.9979 | 5757 | 8950 | 0.32255 | 2886.8225 | 2.8868 | 5.0546 | 709 | 717 | 713 | 722 | 1481.3019 | 1.4813 | 13.2577 | 2.3029 | 23.213
| 2021-02-02 08:40 | 260970 | 87.82 | 33.26 | 179.78 | 2021-01-29 08:42 | 252490 | 8480 | 3.9986 | 5758 | 8480 | 0.30086 | 2551.2928 | 2.5513 | 4.4663 | 737 | 775 | 756 | 767 | 1478.4876 | 1.4785 | 12.5376 | 2.1774 | 21.9484
| 2021-02-09 08:40 | 277410 | 136.12 | 112.13 | 244.65 | 2021-02-05 08:57 | 267970 | 9440 | 3.9882 | 5743 | 9440 | 0.4929 | 4652.976 | 4.653 | 8.1668 | 848 | 848 | 848 | 754 | 1687.0027 | 1.687 | 15.9253 | 2.773 | 27.9518
| 2021-02-10 08:44 | 279440 | 132.05 | 52.31 | 226.52 | 2021-02-05 08:57 | 267970 | 11470 | 4.991 | 7187 | 11470 | 0.41088 | 4712.7936 | 4.7128 | 6.6098 | 813 | 809 | 811 | 745 | 1632.8859 | 1.6329 | 18.7292 | 2.606 | 26.2683
| 2021-02-16 08:50 | 293260 | 183.9 | 40.61 | 211.38 | 2021-02-12 09:03 | 283810 | 9450 | 3.991 | 5747 | 9450 | 0.43589 | 4119.1605 | 4.1192 | 7.2248 | 715 | 672 | 693.5 | 743 | 1400.0673 | 1.4001 | 13.2306 | 2.3022 | 23.206
| 2021-02-17 08:41 | 295800 | 166.75 | 41.74 | 211.38 | 2021-02-12 09:03 | 283810 | 11990 | 4.9847 | 7178 | 11990 | 0.41987 | 5034.2413 | 5.0342 | 7.0695 |  |  | 0 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| 2021-02-18 08:54 | 298470 | 139.72 | 43.3 | 225.84 | 2021-02-12 09:03 | 282810 | 15660 | 5.9938 | 8631 | 15660 | 0.40886 | 6402.7476 | 6.4027 | 7.4777 | 707 | 710 | 708.5 | 748 | 1420.7888 | 1.4208 | 22.2496 | 2.5779 | 25.9849
| 2021-02-22 20:35 | 310440 | 20.34 | 45.92 | 186.17 | 2021-02-19 08:45 | 301230 | 9210 | 3.4931 | 5030 | 9210 | 0.25243 | 2324.8803 | 2.3249 | 4.659 | 661 | 660 | 660.5 | 725 | 1366.5517 | 1.3666 | 12.5859 | 2.5022 | 25.2219
| 2021-03-02 08:41 | 325040 | 18.28 | 23.33 | 207.59 | 2021-02-26 06:00 | 317640 | 7400 | 4.1118 | 5921 | 7400 | 0.2492 | 1844.08 | 1.8441 | 3.1394 | 714 | 682 | 698 | 762 | 1374.0157 | 1.374 | 10.1677 | 1.7172 | 17.3097
| 2021-03-09 09:00 | 339240 | 14.63 | 98.04 | 195.52 | 2021-03-05 08:55 | 330050 | 9190 | 4.0035 | 5765 | 9190 | 0.30819 | 2832.2661 | 2.8323 | 4.9522 | 718 | 705 | 711.5 | 773 | 1380.6598 | 1.3807 | 12.6883 | 2.2009 | 22.1852
| 2021-03-16 10:05 | 356410 | 37.34 | 98.48 | 185.9 | 2021-03-12 08:45 | 346130 | 10280 | 4.0556 | 5840 | 10280 | 0.32172 | 3307.2816 | 3.3073 | 5.7085 | 789 | 788 | 788.5 | 748 | 1581.2166 | 1.5812 | 16.2549 | 2.7834 | 28.0564
| 2021-03-23 08:40 | 373260 | 40.64 | 192.77 | 132.39 | 2021-03-19 09:04 | 363720 | 9540 | 3.9833 | 5736 | 9540 | 0.3658 | 3489.732 | 3.4897 | 6.1326 | 890 | 897 | 893.5 | 747 | 1794.1767 | 1.7942 | 17.1164 | 2.984 | 30.0791
| 2021-03-30 08:52 | 386350 | 31.97 | 175.63 | 140.47 | 2021-03-26 08:45 | 378280 | 8070 | 4.0049 | 5767 | 8070 | 0.34807 | 2808.9249 | 2.8089 | 4.9097 | 782 | 790 | 786 | 775 | 1521.2903 | 1.5213 | 12.2768 | 2.1288 | 21.4583
| 2021-04-06 08:40 | 400660 | 21.83 | 147.94 | 110.77 | 2021-04-01 08:50 | 390200 | 10460 | 4.9931 | 7190 | 10460 | 0.28054 | 2934.4484 | 2.9344 | 4.1139 | 698 | 717 | 707.5 | 737 | 1439.9593 | 1.44 | 15.062 | 2.0949 | 21.1161
| 2021-04-13 08:40 | 414880 | 24.56 | 249.049 | 114.76 | 2021-04-09 08:40 | 407220 | 7660 | 4 | 5760 | 7660 | 0.38837 | 2974.9065 | 2.9749 | 5.2061 | 829 | 813 | 821 | 748 | 1646.3904 | 1.6464 | 12.6114 | 2.1895 | 22.0699
| 2021-04-20 08:38 | 430210 | 20.01 | 149.92 | 157.25 | 2021-04-16 08:50 | 421780 | 8430 | 3.9917 | 5748 | 8430 | 0.32718 | 2758.1274 | 2.7581 | 4.8368 | 628 | 638 | 633 | 731 | 1298.9056 | 1.2989 | 10.9498 | 1.905 | 19.2021
| 2021-04-27 08:40 | 444590 | 58.68 | 154.29 | 122.72 | 2021-04-23 08:40 | 436840 | 7750 | 4 | 5760 | 7750 | 0.33569 | 2601.5975 | 2.6016 | 4.5528 | 832 | 881 | 856.5 | 762 | 1686.0236 | 1.686 | 13.0667 | 2.2685 | 22.8667
| 2021-05-04 08:42 | 458730 | 36.5 | 293.15 | 144.63 | 2021-04-30 08:45 | 450420 | 8310 | 3.9979 | 5757 | 8310 | 0.47428 | 3941.2668 | 3.9413 | 6.9008 | 865 | 890 | 877.5 | 728 | 1808.0357 | 1.808 | 15.0248 | 2.6098 | 26.3071
| 2021-05-11 08:45 | 474530 | 79.824 | 81.44 | 175.18 | 2021-05-07 08:45 | 465590 | 8940 | 4 | 5760 | 8940 | 0.33644 | 3007.8094 | 3.0078 | 5.2637 | 694 | 721 | 707.5 | 745 | 1424.4966 | 1.4245 | 12.735 | 2.2109 | 22.2862
| 2021-05-18 08:35 | 489410 | 59.64 | 125.23 | 139.58 | 2021-05-14 09:19 | 480780 | 8630 | 3.9694 | 5716 | 8630 | 0.32445 | 2800.0035 | 2.8 | 4.9377 | 907 | 902 | 904.5 | 747 | 1816.2651 | 1.8163 | 15.6744 | 2.7422 | 27.6413
| 2021-05-25 08:40 | 3850 | 26.91 | 142.71 | 181.8 | 2021-05-21 08:40 | 496300 | 7540 | 4 | 5760 | 7540 | 0.35142 | 2649.7068 | 2.6497 | 4.637 | 849 | 833 | 841 | 752 | 1677.5266 | 1.6775 | 12.6486 | 2.1959 | 22.135
| 2021-06-01 08:45 | 17920 | 20.82 | 160.09 | 199.39 | 2021-05-28 08:50 | 10550 | 7370 | 3.9965 | 5755 | 7370 | 0.3803 | 2802.811 | 2.8028 | 4.9092 | 857 | 878 | 867.5 | 759 | 1714.4269 | 1.7144 | 12.6353 | 2.1955 | 22.131
| 2021-06-08 08:45 | 33820 | 17.25 | 107.95 | 165.67 | 2021-06-04 08:37 | 27500 | 6320 | 4.0056 | 5768 | 6320 | 0.29087 | 1838.2984 | 1.8383 | 3.2126 | 670 | 669 | 669.5 | 753 | 1333.6653 | 1.3337 | 8.4288 | 1.4613 | 14.7299
| 2021-06-15 08:45 | 46470 | 47.27 | 16.97 | 258.69 | 2021-06-11 08:38 | 39260 | 7210 | 4.0049 | 5767 | 7210 | 0.32293 | 2328.3253 | 2.3283 | 4.0696 | 651 | 644 | 647.5 | 742 | 1308.9623 | 1.309 | 9.4376 | 1.6365 | 16.4958
| 2021-06-22 08:38 | 61110 | 38.14 | 116.91 | 252.49 | 2021-06-18 08:42 | 52410 | 8700 | 3.9972 | 5756 | 8700 | 0.40754 | 3545.598 | 3.5456 | 6.2091 | 822 | 809 | 815.5 | 769 | 1590.7022 | 1.5907 | 13.8391 | 2.4043 | 24.2353
| 2021-06-23 08:54 | 63490 | 25.4241 | 94.4931 | 304.9363 | 2021-06-18 08:42 | 52410 | 11080 | 5.0083 | 7212 | 11080 | 0.42485 | 4707.3769 | 4.7074 | 6.5794 | 836 | 853 | 844.5 | 750 | 1689 | 1.689 | 18.7141 | 2.5949 | 26.1562
| 2021-06-24 | 65570 | 17.528 | 76.712 | 281.581 | 2021-06-18 08:42 | 52410 | 13160 | 5.6375 | 8118 | 13160 | 0.37582 | 4945.8044 | 4.9458 | 6.1411 | 858 | 807 | 832.5 | 729 | 1712.963 | 1.713 | 22.5426 | 2.7769 | 27.9908
| 2021-06-29 | 74230 | 58.289 | 108.98 | 235.89 | 2021-06-25 08:49 | 67320 | 6910 | 3.6326 | 5231 | 6910 | 0.40316 | 2785.8287 | 2.7858 | 5.3682 | 859 | 865 | 862 | 749 | 1726.3017 | 1.7263 | 11.9287 | 2.2804 | 22.9864
| 2021-07-06 08:45 | 87950 | 87.033 | 41.47 | 234.9308 | 2021-07-02 08:30 | 79620 | 8330 | 4.0104 | 5775 | 8330 | 0.36343 | 3027.403 | 3.0274 | 5.2842 | 689 | 665 | 677 | 745 | 1363.0872 | 1.3631 | 11.3545 | 1.9662 | 19.8188
| 2021-07-13 08:51 | 100970 | 109.5 | 36.9 | 234.8 | 2021-07-09 08:33 | 93260 | 7710 | 4.0125 | 5778 | 7710 | 0.3812 | 2939.052 | 2.9391 | 5.1273 | 704 | 724 | 714 | 765 | 1400 | 1.4 | 10.794 | 1.8681 | 18.8307
| 2021-07-19 08:45 | 111810 | 116.97 | 25.42 | 263.3 | 2021-07-16 08:46 | 106520 | 5290 | 2.9993 | 4319 | 5290 | 0.40569 | 2146.1001 | 2.1461 | 5.0087 | 677 | 720 | 698.5 | 778 | 1346.7224 | 1.3467 | 7.1242 | 1.6495 | 16.6269
| 2021-07-20 08:50 | 113870 | 121.21 | 6.56 | 312.77 | 2021-07-16 08:46 | 106520 | 7350 | 4.0028 | 5764 | 7350 | 0.44054 | 3237.969 | 3.238 | 5.6625 | 683 | 679 | 681 | 725 | 1408.9655 | 1.409 | 10.3559 | 1.7967 | 18.1102
| 2021-07-21 08:57 | 116240 | 111.65 | 14.39 | 235.3 | 2021-07-16 08:46 | 106520 | 9720 | 5.0076 | 7211 | 9720 | 0.36134 | 3512.2248 | 3.5122 | 4.9096 | 724 | 741 | 732.5 | 742 | 1480.7951 | 1.4808 | 14.3933 | 1.996 | 20.1199
| 2021-07-22 08:54 | 118470 | 117.62 | 38.02 | 234.5 | 2021-07-16 08:46 | 106520 | 11950 | 6.0056 | 8648 | 11950 | 0.39014 | 4662.173 | 4.6622 | 5.4342 | 735 | 738 | 736.5 | 747 | 1478.9157 | 1.4789 | 17.673 | 2.0436 | 20.5995
| 2021-07-26 08:45 | 127700 | 98.66 | 97.37 | 164.59 | 2021-07-23 08:45 | 120770 | 6930 | 3 | 4320 | 6930 | 0.36062 | 2499.0966 | 2.4991 | 5.8312 | 860 | 840 | 850 | 741 | 1720.6478 | 1.7206 | 11.9241 | 2.7602 | 27.8229
| 2021-07-27 08:40 | 130190 | 128.4 | 19.89 | 251.71 | 2021-07-23 08:45 | 120770 | 9420 | 3.9965 | 5755 | 9420 | 0.4 | 3768 | 3.768 | 6.5997 | 840 | 847 | 843.5 | 738 | 1714.4309 | 1.7144 | 16.1499 | 2.8062 | 28.2869
| 2021-07-28 08:24 | 131930 | 23.14 | 0 | 284.94 | 2021-07-23 08:45 | 120770 | 11160 | 4.9854 | 7179 | 11160 | 0.30808 | 3438.1728 | 3.4382 | 4.8275 | 916 | 938 | 927 | 785 | 1771.3376 | 1.7713 | 19.7681 | 2.7536 | 27.7563
| 2021-07-29 08:00 | 134280 | 26.94 | 0 | 284.94 | 2021-07-23 08:45 | 120770 | 13510 | 5.9688 | 8595 | 13510 | 0.31188 | 4213.4988 | 4.2135 | 4.9415 | 859 | 865 | 862 | 777 | 1664.0927 | 1.6641 | 22.4819 | 2.6157 | 26.3662
| 2021-08-03 08:30 | 137700 | 258.486 | 81.8517 | 81.2415 | 2021-07-30 09:05 | 136310 | 1390 | 3.9757 | 5725 | 1390 | 0.42158 | 585.9952 | 0.586 | 1.0318 | 303 | 309 | 306 | 780 | 588.4615 | 0.58846 | 0.81796 | 0.14288 | 1.4402
| 2021-08-10 | 140810 | 126.15 | 118.89 | 40.87 | 2021-08-06 08:35 | 138230 | 2580 | 3.6424 | 5245 | 2580 | 0.28591 | 737.6478 | 0.73765 | 1.4176 | 227 | 219 | 223 | 774 | 432.1705 | 0.43217 | 1.115 | 0.21258 | 2.1428
| 2021-08-17 08:44 | 154850 | 21.183 | 237.64 | 162.42 | 2021-08-13 08:41 | 146180 | 8670 | 4.0021 | 5763 | 8670 | 0.42124 | 3652.1768 | 3.6522 | 6.388 | 556 | 557 | 556.5 | 762 | 1095.4724 | 1.0955 | 9.4977 | 1.6481 | 16.6124
| 2021-08-18 08:47 | 157420 | 21.04 | 219.68 | 187.34 | 2021-08-13 08:41 | 146180 | 11240 | 5.0042 | 7206 | 11240 | 0.42806 | 4811.3944 | 4.8114 | 6.7303 | 607 | 609 | 608 | 768 | 1187.5 | 1.1875 | 13.3475 | 1.8523 | 18.6709
| 2021-08-24 08:36 | 171290 | 16.7 | 41.1 | 233.7 | 2021-08-20 08:52 | 162750 | 8540 | 3.9889 | 5744 | 8540 | 0.2915 | 2489.41 | 2.4894 | 4.3686 | 618 | 577 | 597.5 | 758 | 1182.3879 | 1.1824 | 10.0976 | 1.7579 | 17.72
| 2021-08-31 08:37 | 185570 | 22.15 | 109.39 | 235.99 | 2021-08-27 09:05 | 176750 | 8820 | 3.9806 | 5732 | 8820 | 0.36753 | 3241.6146 | 3.2416 | 5.7005 | 806 | 844 | 825 | 784 | 1578.4439 | 1.5784 | 13.9219 | 2.4288 | 24.4823
| 2021-09-07 08:53 | 199890 | 10.63 | 51.22 | 332.79 | 2021-09-03 08:48 | 192360 | 7530 | 4.0035 | 5765 | 7530 | 0.39464 | 2971.6392 | 2.9716 | 5.1959 | 847 | 844 | 845.5 | 763 | 1662.1887 | 1.6622 | 12.5163 | 2.1711 | 21.8845
| 2021-09-14 08:46 | 214580 | 20.2516 | 30.201 | 277.4977 | 2021-09-10 08:50 | 206020 | 8560 | 3.9972 | 5756 | 8560 | 0.32795 | 2807.255 | 2.8073 | 4.9161 | 630 | 631 | 630.5 | 767 | 1233.0508 | 1.2331 | 10.5549 | 1.8337 | 18.4839
| 2021-09-21 09:05 | 230010 | 9.38 | 93.89 | 212.81 | 2021-09-17 08:51 | 221430 | 8580 | 4.0097 | 5774 | 8580 | 0.31608 | 2711.9664 | 2.712 | 4.7344 | 627 | 625 | 626 | 770 | 1219.4805 | 1.2195 | 10.4631 | 1.8121 | 18.2661
| 2021-09-28 08:56 | 244140 | 24.2 | 60.57 | 296.87 | 2021-09-24 08:55 | 235380 | 8760 | 4.0007 | 5761 | 8760 | 0.38164 | 3343.1664 | 3.3432 | 5.8495 | 851 | 888 | 869.5 | 734 | 1776.9074 | 1.7769 | 15.5657 | 2.7019 | 27.2353
| 2021-09-29 08:36 | 246310 | 25.97 | 55.73 | 311.41 | 2021-09-24 08:55 | 235380 | 10930 | 4.9868 | 7181 | 10930 | 0.39311 | 4296.6923 | 4.2967 | 6.0313 | 878 | 850 | 864 | 769 | 1685.3056 | 1.6853 | 18.4204 | 2.5652 | 25.8568
| 2021-09-30 08:44 | 248570 | 26.94 | 47.54 | 317.61 | 2021-09-24 08:55 | 235380 | 13190 | 5.9924 | 8629 | 13190 | 0.39209 | 5171.6671 | 5.1717 | 6.0413 | 839 | 846 | 842.5 | 751 | 1682.7563 | 1.6828 | 22.1956 | 2.5722 | 25.9278
| 2021-10-05 08:44 | 259970 | 77.249 | 137.284 | 126.975 | 2021-10-01 08:51 | 250890 | 9080 | 3.9951 | 5753 | 9080 | 0.34151 | 3100.8926 | 3.1009 | 5.4332 | 858 | 842 | 850 | 804 | 1585.8209 | 1.5858 | 14.3993 | 2.5029 | 25.2294
| 2021-10-06 08:40 | 262180 | 16.43 | 126.91 | 181.55 | 2021-10-01 08:51 | 250890 | 11290 | 4.9924 | 7189 | 11290 | 0.32489 | 3668.0081 | 3.668 | 5.1431 | 814 | 832 | 823 | 783 | 1576.6284 | 1.5766 | 17.8001 | 2.476 | 24.9583
| 2021-10-12 08:47 | 275440 | 40.64 | 135.67 | 188.79 | 2021-10-08 08:45 | 266630 | 8810 | 4.0014 | 5762 | 8810 | 0.3651 | 3216.531 | 3.2165 | 5.627 | 748 | 765 | 756.5 | 771 | 1471.7899 | 1.4718 | 12.9665 | 2.2503 | 22.6834
| 2021-10-19 08:30 | 289600 | 36.56 | 80.9 | 171.14 | 2021-10-15 08:46 | 281890 | 7710 | 3.9889 | 5744 | 7710 | 0.2886 | 2225.106 | 2.2251 | 3.9048 | 669 | 672 | 670.5 | 749 | 1342.7904 | 1.3428 | 10.3529 | 1.8024 | 18.1681
| 2021-10-26 08:44 | 303010 | 49.8352 | 132.078 | 250.084 | 2021-10-22 08:38 | 294540 | 8470 | 4.0042 | 5766 | 8470 | 0.432 | 3659.016 | 3.659 | 6.3966 | 794 | 822 | 808 | 789 | 1536.1217 | 1.5361 | 13.011 | 2.2565 | 22.7455
| 2021-11-02 09:05 | 318250 | 21.48 | 199.74 | 126.1 | 2021-10-29 08:48 | 309340 | 8910 | 4.0118 | 5777 | 8910 | 0.34732 | 3094.6212 | 3.0946 | 5.3997 | 570 | 554 | 562 | 772 | 1091.9689 | 1.092 | 9.7294 | 1.6842 | 16.9764
| 2021-11-09 08:59 | 335940 | 17.92 | 172.81 | 161.32 | 2021-11-05 08:55 | 325090 | 10850 | 4.0028 | 5764 | 10850 | 0.35205 | 3819.7425 | 3.8197 | 6.6799 | 699 | 698 | 698.5 | 758 | 1382.2559 | 1.3823 | 14.9975 | 2.6019 | 26.2274
| 2021-11-10 08:42 | 338420 | 19.9245 | 162.2911 | 167.0605 | 2021-11-05 08:55 | 325090 | 13330 | 4.991 | 7187 | 13330 | 0.34928 | 4655.8499 | 4.6558 | 6.53 | 687 | 666 | 676.5 | 775 | 1309.3548 | 1.3094 | 17.4537 | 2.4285 | 24.4794
| 2021-11-11 08:42 | 341150 | 13.85 | 166.36 | 170.88 | 2021-11-05 08:55 | 325090 | 16060 | 5.991 | 8627 | 16060 | 0.35109 | 5638.5054 | 5.6385 | 6.5882 | 678 | 677 | 677.5 | 743 | 1367.7658 | 1.3678 | 21.9663 | 2.5462 | 25.666
| 2021-11-16 08:38 | 352540 | 44.31 | 175.37 | 286.94 | 2021-11-12 08:58 | 343660 | 8880 | 3.9861 | 5740 | 8880 | 0.50662 | 4498.7856 | 4.4988 | 7.9003 | 937 | 929 | 933 | 775 | 1805.8065 | 1.8058 | 16.0356 | 2.7937 | 28.16
| 2021-11-17 08:47 | 354690 | 57.06 | 142.91 | 259.72 | 2021-11-12 08:58 | 343660 | 11030 | 4.9924 | 7189 | 11030 | 0.45969 | 5070.3807 | 5.0704 | 7.1094 | 856 | 874 | 865 | 783 | 1657.0881 | 1.6571 | 18.2777 | 2.5425 | 25.6279
| 2021-11-18 08:45 | 356850 | 31.88 | 154.61 | 295.61 | 2021-11-12 08:58 | 343660 | 13190 | 5.991 | 8627 | 13190 | 0.4821 | 6358.899 | 6.3589 | 7.4299 | 906 | 906 | 906 | 785 | 1731.2102 | 1.7312 | 22.8347 | 2.6469 | 26.6806
| 2021-11-23 08:48 | 365360 | 24.92 | 133.64 | 157.29 | 2021-11-19 08:45 | 358630 | 6730 | 4.0021 | 5763 | 6730 | 0.31585 | 2125.6705 | 2.1257 | 3.718 | 830 | 801 | 815.5 | 763 | 1603.211 | 1.6032 | 10.7896 | 1.8722 | 18.872
| 2021-11-30 08:51 | 381830 | 27.49 | 126.34 | 120.67 | 2021-11-26 08:49 | 371740 | 10090 | 4.0014 | 5762 | 10090 | 0.2745 | 2769.705 | 2.7697 | 4.8453 | 763 | 756 | 759.5 | 748 | 1523.0615 | 1.5231 | 15.3677 | 2.6671 | 26.8841
| 2021-12-01 08:50 | 383940 | 27.28 | 139.17 | 127.2 | 2021-11-26 08:49 | 371740 | 12200 | 5.0007 | 7201 | 12200 | 0.29365 | 3582.53 | 3.5825 | 5.0148 | 797 | 798 | 797.5 | 759 | 1576.087 | 1.5761 | 19.2283 | 2.6702 | 26.9158
| 2021-12-02 09:01 | 386310 | 33.05 | 133.94 | 137.29 | 2021-11-26 08:49 | 371740 | 14570 | 6.0083 | 8652 | 14570 | 0.30428 | 4433.3596 | 4.4334 | 5.1651 | 768 | 771 | 769.5 | 791 | 1459.2288 | 1.4592 | 21.261 | 2.4573 | 24.7701
| 2021-12-07 08:54 | 397780 | 29.99 | 242.51 | 122.74 | 2021-12-03 08:58 | 388610 | 9170 | 3.9972 | 5756 | 9170 | 0.39524 | 3624.3508 | 3.6244 | 6.347 | 823 | 821 | 822 | 754 | 1635.2785 | 1.6353 | 14.9955 | 2.6052 | 26.2604
| 2021-12-08 09:06 | 399780 | 18.36 | 69.09 | 203.79 | 2021-12-03 08:58 | 388610 | 11170 | 5.0056 | 7208 | 11170 | 0.29124 | 3253.1508 | 3.2532 | 4.5494 | 722 | 714 | 718 | 784 | 1373.7245 | 1.3737 | 15.3445 | 2.1288 | 21.4585
| 2021-12-14 08:47 | 412580 | 30.15 | 134.2 | 126.88 | 2021-12-10 09:04 | 403480 | 9100 | 3.9882 | 5743 | 9100 | 0.29123 | 2650.193 | 2.6502 | 4.6516 | 732 | 755 | 743.5 | 757 | 1473.2497 | 1.4732 | 13.4066 | 2.3344 | 23.5309
| 2021-12-15 09:47 | 415060 | 33.29 | 140.23 | 133.39 | 2021-12-10 09:04 | 403480 | 11580 | 5.0299 | 7243 | 11580 | 0.30691 | 3554.0178 | 3.554 | 4.9461 | 777 | 809 | 793 | 753 | 1579.6813 | 1.5797 | 18.2927 | 2.5256 | 25.4578
| 2021-12-16 08:38 | 417330 | 29.47 | 148.31 | 161.05 | 2021-12-10 09:04 | 403480 | 13850 | 5.9819 | 8614 | 13850 | 0.33883 | 4692.7955 | 4.6928 | 5.4915 | 829 | 804 | 816.5 | 747 | 1639.5582 | 1.6396 | 22.7079 | 2.6362 | 26.5725
| 2021-12-21 09:10 | 428610 | 21.89 | 147.26 | 142.64 | 2021-12-17 08:48 | 419610 | 9000 | 4.0153 | 5782 | 9000 | 0.31179 | 2806.11 | 2.8061 | 4.892 | 761 | 761 | 761 | 742 | 1538.4097 | 1.5384 | 13.8457 | 2.3946 | 24.1378
| 2021-12-29 09:01 | 447630 | 30.61 | 219.69 | 119.11 | 2021-12-24 08:45 | 435700 | 11930 | 5.0111 | 7216 | 11930 | 0.36941 | 4407.0613 | 4.4071 | 6.1562 | 846 | 874 | 860 | 755 | 1708.6093 | 1.7086 | 20.3837 | 2.8248 | 28.4739
| 2021-12-30 09:02 | 448920 | 31.85 | 116.54 | 227.94 | 2021-12-24 08:45 | 435700 | 13220 | 6.0118 | 8657 | 13220 | 0.37633 | 4975.0826 | 4.9751 | 5.7929 | 867 | 867 | 867 | 781 | 1665.1729 | 1.6652 | 22.0136 | 2.5429 | 25.6321
| 2022-01-04 08:55 | 460140 | 30.15 | 201.24 | 163.22 | 2021-12-31 08:48 | 449860 | 10280 | 4.0049 | 5767 | 10280 | 0.39461 | 4056.5908 | 4.0566 | 7.0904 | 731 | 728 | 729.5 | 780 | 1402.8846 | 1.4029 | 14.4217 | 2.5007 | 25.2073
| 2022-01-05 08:40 | 462930 | 23.6 | 181.49 | 194.4 | 2021-12-31 08:48 | 449860 | 13070 | 4.9944 | 7192 | 13070 | 0.39949 | 5221.3343 | 5.2213 | 7.318 | 732 | 729 | 730.5 | 773 | 1417.5291 | 1.4175 | 18.5271 | 2.5761 | 25.9668
| 2022-01-06 09:10 | 465530 | 33.9 | 157.63 | 178.11 | 2021-12-31 | 449860 | 15670 | 6.3819 | 9190 | 15670 | 0.36964 | 5792.2588 | 5.7923 | 6.3532 | 710 | 712 | 711 | 780 | 1367.3077 | 1.3673 | 21.4257 | 2.3314 | 23.5007
| 2022-01-11 08:50 | 477330 | 10.27 | 86.74 | 157.96 | 2022-01-07 08:54 | 468130 | 9200 | 3.9972 | 5756 | 9200 | 0.25497 | 2345.724 | 2.3457 | 4.1079 | 696 | 704 | 700 | 783 | 1340.9962 | 1.341 | 12.3372 | 2.1434 | 21.605
| 2022-01-12 08:30 | 479450 | 12.09 | 89.76 | 168.31 | 2022-01-07 08:54 | 468130 | 11320 | 4.9833 | 7176 | 11320 | 0.27016 | 3058.2112 | 3.0582 | 4.2958 | 665 | 696 | 680.5 | 746 | 1368.2976 | 1.3683 | 15.4891 | 2.1585 | 21.7573
| 2022-01-18 08:54 | 492490 | 29.69 | 111.84 | 128.91 | 2022-01-14 08:35 | 483730 | 8760 | 4.0132 | 5779 | 8760 | 0.27044 | 2369.0544 | 2.3691 | 4.1322 | 675 | 680 | 677.5 | 758 | 1340.6992 | 1.3407 | 11.7445 | 2.0323 | 20.4853
| 2022-01-25 08:45 | 9210 | 22.6 | 94.06 | 216.47 | 2022-01-21 08:57 | 499360 | 9840 | 3.9917 | 5748 | 9870 | 0.33313 | 3287.9931 | 3.288 | 5.766 | 861 | 849 | 855 | 756 | 1696.4286 | 1.6964 | 16.6929 | 2.9041 | 29.2735
| 2022-01-26 08:50 | 11590 | 20.84 | 86.46 | 199.05 | 2022-01-21 08:57 | 2380 | 9210 | 4.9951 | 7193 | 9210 | 0.30635 | 2821.4835 | 2.8215 | 3.9539 | 804 | 830 | 817 | 763 | 1606.1599 | 1.6062 | 14.7927 | 2.0565 | 20.73
| 2022-02-01 08:40 | 22230 | 28.07 | 311.9 | 136.19 | 2022-01-28 09:00 | 15870 | 6360 | 3.9861 | 5740 | 6360 | 0.47616 | 3028.3776 | 3.0284 | 5.3181 | 788 | 786 | 787 | 760 | 1553.2895 | 1.5533 | 9.8789 | 1.7211 | 17.3483
| 2022-02-08 08:48 | 38980 | 5.54 | 140.71 | 174.76 | 2022-02-04 08:50 | 29550 | 9430 | 3.9986 | 5758 | 9430 | 0.32101 | 3027.1243 | 3.0271 | 5.2993 | 656 | 659 | 657.5 | 741 | 1330.9717 | 1.331 | 12.5511 | 2.1798 | 21.972
| 2022-02-15 08:41 | 55850 | 23.4 | 143.21 | 126.72 | 2022-02-11 08:43 | 46060 | 9790 | 3.9986 | 5758 | 9790 | 0.29333 | 2871.7007 | 2.8717 | 5.0272 | 720 | 665 | 692.5 | 774 | 1342.0543 | 1.3421 | 13.1387 | 2.2818 | 23.0007
| 2022-02-22 08:40 | 72910 | 8.43 | 140.56 | 218.22 | 2022-02-18 08:42 | 61130 | 11780 | 3.9986 | 5758 | 11780 | 0.36721 | 4325.7338 | 4.3257 | 7.5727 | 770 | 767 | 768.5 | 766 | 1504.8956 | 1.5049 | 17.7277 | 3.0788 | 31.0342
| 2022-02-23 08:50 | 74850 | 4.46 | 221.78 | 175.68 | 2022-02-18 08:42 | 61130 | 13720 | 5.0056 | 7208 | 13720 | 0.40192 | 5514.3424 | 5.5143 | 7.7115 | 737 | 735 | 736 | 744 | 1483.871 | 1.4839 | 20.3587 | 2.8245 | 28.4706
| 2022-02-24 08:41 | 76820 | 12.355 | 288.077 | 135.245 | 2022-02-18 08:42 | 61130 | 15690 | 5.9993 | 8639 | 15690 | 0.43568 | 6835.7721 | 6.8358 | 7.976 | 788 | 774 | 781 | 747 | 1568.2731 | 1.5683 | 24.6062 | 2.8483 | 28.7106
| 2022-03-01 08:52 | 87650 | 103.94 | 82.38 | 162.11 | 2022-02-25 08:48 | 78920 | 8730 | 4.0028 | 5764 | 8730 | 0.34843 | 3041.7939 | 3.0418 | 5.3194 | 649 | 642 | 645.5 | 785 | 1233.4395 | 1.2334 | 10.7679 | 1.8681 | 18.8308
| 2022-03-08 08:48 | 103530 | 32.03 | 208.99 | 117.38 | 2022-03-04 08:57 | 94570 | 8980 | 3.9937 | 5751 | 8980 | 0.3584 | 3218.432 | 3.2184 | 5.6411 | 651 | 652 | 651.5 | 744 | 1313.5081 | 1.3135 | 11.7953 | 2.051 | 20.6741
| 2022-03-15 09:01 | 119900 | 47.48 | 184.898 | 161.71 | 2022-03-11 08:48 | 110190 | 9710 | 4.009 | 5773 | 9710 | 0.39409 | 3826.5945 | 3.8266 | 6.6815 | 796 | 827 | 811.5 | 777 | 1566.6023 | 1.5666 | 15.2117 | 2.635 | 26.5605
| 2022-03-16 08:58 | 121740 | 51.09 | 229.72 | 132.89 | 2022-03-11 08:48 | 110190 | 11550 | 5.0069 | 7210 | 11550 | 0.4137 | 4778.235 | 4.7782 | 6.6803 | 766 | 756 | 761 | 775 | 1472.9032 | 1.4729 | 17.012 | 2.3595 | 23.7838
| 2022-03-22 08:56 | 133670 | 18.34 | 144.53 | 176.66 | 2022-03-18 08:54 | 125840 | 7830 | 4.0014 | 5762 | 7830 | 0.33953 | 2658.5199 | 2.6585 | 4.6508 | 646 | 643 | 644.5 | 772 | 1252.2668 | 1.2523 | 9.8052 | 1.7017 | 17.1532
| 2022-03-29 08:53 | 148150 | 54.49 | 171.63 | 115.34 | 2022-03-25 08:49 | 139480 | 8670 | 4.0028 | 5764 | 8670 | 0.34146 | 2960.4582 | 2.9605 | 5.1772 | 817 | 784 | 800.5 | 777 | 1545.3668 | 1.5454 | 13.3983 | 2.3245 | 23.4308
| 2022-04-05 08:56 | 162290 | 5.36 | 131.34 | 136.69 | 2022-04-01 08:50 | 153190 | 9100 | 4.0042 | 5766 | 9100 | 0.27339 | 2487.849 | 2.4878 | 4.3492 | 523 | 527 | 525 | 749 | 1051.4019 | 1.0514 | 9.5678 | 1.6593 | 16.7262
| 2022-04-12 08:35 | 180290 | 49.19 | 129.11 | 169.81 | 2022-04-08 08:51 | 170370 | 9920 | 3.9889 | 5744 | 9920 | 0.34811 | 3453.2512 | 3.4533 | 6.06 | 731 | 739 | 735 | 764 | 1443.0628 | 1.4431 | 14.3152 | 2.4922 | 25.1214
| 2022-04-13 08:35 | 182810 | 44.86 | 135.14 | 164.46 | 2022-04-08 08:51 | 170370 | 12440 | 4.9889 | 7148 | 12440 | 0.34446 | 4285.0824 | 4.2851 | 6.0428 | 722 | 721 | 721.5 | 772 | 1401.8782 | 1.4019 | 17.4394 | 2.4398 | 24.5927
| 2022-04-19 08:57 | 195200 | 26.11 | 85.41 | 211.93 | 2022-04-14 08:49 | 184380 | 10820 | 5.0056 | 7208 | 10820 | 0.32345 | 3499.729 | 3.4997 | 4.8942 | 614 | 635 | 624.5 | 758 | 1235.8179 | 1.2358 | 13.3716 | 1.8551 | 18.6994
| 2022-04-26 08:53 | 211440 | 34.871 | 95.0863 | 137.9365 | 2022-04-22 05:50 | 202330 | 9110 | 4.1271 | 5943 | 9110 | 0.26789 | 2440.5137 | 2.4405 | 4.1394 | 616 | 629 | 622.5 | 781 | 1195.5826 | 1.1956 | 10.8918 | 1.8327 | 18.4737
| 2022-05-03 08:48 | 225040 | 23.45 | 38.99 | 243.92 | 2022-04-29 08:53 | 217650 | 7390 | 3.9965 | 5227 | 7390 | 0.30636 | 2264.0004 | 2.264 | 4.366 | 575 | 567 | 571 | 748 | 1145.0535 | 1.1451 | 8.4619 | 1.6189 | 16.3184
| 2022-05-10 08:48 | 239470 | 31.37 | 202.55 | 112.03 | 2022-05-06 09:00 | 230810 | 8660 | 3.9917 | 5748 | 8660 | 0.34595 | 2995.927 | 2.9959 | 5.2538 | 619 | 627 | 623 | 737 | 1267.9783 | 1.268 | 10.9807 | 1.9104 | 19.2563
| 2022-05-17 08:41 | 254700 | 65.591 | 163.86 | 362.69 | 2022-05-13 08:50 | 246270 | 8430 | 3.9938 | 5751 | 8430 | 0.59214 | 4991.7486 | 4.9917 | 8.7492 | 917 | 879 | 898 | 761 | 1770.0394 | 1.77 | 14.9214 | 2.5946 | 26.1534
| 2022-05-18 08:54 | 256730 | 73.81 | 100.19 | 391.39 | 2022-05-13 08:50 | 246270 | 10460 | 5.0028 | 7204 | 10460 | 0.56539 | 5913.9794 | 5.914 | 8.275 | 880 | 894 | 887 | 752 | 1769.2819 | 1.7693 | 18.5067 | 2.5689 | 25.895
| 2022-05-19 08:48 | 259200 | 73.09 | 103.76 | 399.52 | 2022-05-13 08:50 | 246270 | 12930 | 5.9986 | 8638 | 12930 | 0.57637 | 7452.4641 | 7.4525 | 8.6966 | 892 | 866 | 879 | 775 | 1701.2903 | 1.7013 | 21.9977 | 2.5466 | 25.6699
| 2022-05-19 12:57 | 259510 | 74.78 | 59.58 | 402.41 | 2022-05-13 08:50 | 246270 | 13240 | 6.1715 | 8887 | 13240 | 0.53677 | 7106.8348 | 7.1068 | 8.0609 |  |  | 0 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| 2022-05-24 08:43 | 268610 | 53.1 | 81.36 | 237.9 | 2022-05-20 08:47 | 260850 | 7760 | 3.9972 | 5756 | 7760 | 0.37236 | 2889.5136 | 2.8895 | 5.0602 | 742 | 741 | 741.5 | 783 | 1420.4981 | 1.4205 | 11.0231 | 1.9151 | 19.3038
| 2022-05-31 08:52 | 283230 | 86.19 | 96.17 | 224.33 | 2022-05-27 08:51 | 274800 | 8430 | 4.0007 | 5761 | 8430 | 0.40669 | 3428.3967 | 3.4284 | 5.9987 | 817 | 889 | 853 | 776 | 1648.8402 | 1.6488 | 13.8997 | 2.4127 | 24.3203
| 2022-06-07 08:45 | 298510 | 37.32 | 164.12 | 130.75 | 2022-06-03 08:52 | 289400 | 9110 | 3.9951 | 5753 | 9110 | 0.33219 | 3026.2509 | 3.0263 | 5.3024 | 595 | 590 | 592.5 | 755 | 1177.1523 | 1.1772 | 10.7239 | 1.864 | 18.7896
| 2022-06-14 08:49 | 313700 | 47.96 | 39.95 | 238.79 | 2022-06-10 08:57 | 305120 | 8580 | 3.9944 | 5752 | 8580 | 0.3267 | 2803.086 | 2.8031 | 4.9122 | 674 | 674 | 674 | 753 | 1342.6295 | 1.3426 | 11.5198 | 2.0027 | 20.1876
| 2022-06-21 08:54 | 327970 | 20.3 | 90.18 | 182.95 | 2022-06-17 09:01 | 319280 | 8690 | 3.9951 | 5753 | 8690 | 0.29343 | 2549.9067 | 2.5499 | 4.4678 | 461 | 514 | 487.5 | 757 | 965.9841 | 0.96598 | 8.3944 | 1.4591 | 14.7081
| 2022-06-28 08:53 | 344740 | 38.01 | 75.58 | 258.81 | 2022-06-24 09:00 | 335140 | 9600 | 3.9951 | 5753 | 9600 | 0.3724 | 3575.04 | 3.575 | 6.2639 | 595 | 590 | 592.5 | 776 | 1145.2964 | 1.1453 | 10.9948 | 1.9111 | 19.2644
| 2022-07-05 09:01 | 360880 | 37.33 | 159.79 | 130.75 | 2022-07-01 08:55 | 351670 | 9210 | 4.0042 | 5766 | 9210 | 0.32787 | 3019.6827 | 3.0197 | 5.2789 | 564 | 636 | 600 | 772 | 1165.8031 | 1.1658 | 10.737 | 1.8621 | 18.7703
| 2022-07-12 08:55 | 376490 | 53.474 | 47.8978 | 234.1124 | 2022-07-08 08:43 | 367880 | 8610 | 4.0083 | 5772 | 8610 | 0.33548 | 2888.5194 | 2.8885 | 5.0444 | 686 | 695 | 690.5 | 776 | 1334.7294 | 1.3347 | 11.492 | 1.991 | 20.0692
| 2022-07-19 09:03 | 390670 | 25.12 | 18.75 | 253.64 | 2022-07-15 09:02 | 383210 | 7460 | 4.0007 | 5761 | 7460 | 0.29751 | 2219.4246 | 2.2194 | 3.8833 | 536 | 535 | 535.5 | 755 | 1063.9073 | 1.0639 | 7.9367 | 1.3777 | 13.8869
| 2022-07-26 09:00 | 403450 | 16.65 | 12.34 | 235.9 | 2022-07-22 08:56 | 395150 | 8300 | 4.0028 | 5764 | 8300 | 0.26489 | 2198.587 | 2.1986 | 3.8449 | 387 | 393 | 390 | 750 | 780 | 0.78 | 6.474 | 1.1232 | 11.3216
| 2022-08-02 09:03 | 418510 | 11.61 | 53.81 | 133.04 | 2022-07-29 09:05 | 408900 | 9610 | 3.9986 | 5758 | 9610 | 0.19846 | 1907.2006 | 1.9072 | 3.3388 | 361 | 389 | 375 | 746 | 754.0214 | 0.75402 | 7.2461 | 1.2584 | 12.6852
| 2022-08-09 08:55 | 435540 | 30.41 | 17.76 | 217.22 | 2022-08-05 08:54 | 425780 | 9760 | 4.0007 | 5761 | 9760 | 0.26539 | 2590.2064 | 2.5902 | 4.5321 | 476 | 469 | 472.5 | 726 | 976.2397 | 0.97624 | 9.5281 | 1.6539 | 16.6713
| 2022-08-16 08:53 | 452610 | 45.71 | 8.36 | 237.69 | 2022-08-12 09:02 | 443200 | 9410 | 3.9937 | 5751 | 9410 | 0.29176 | 2745.4616 | 2.7455 | 4.8121 | 654 | 661 | 657.5 | 764 | 1290.9031 | 1.2909 | 12.1474 | 2.1122 | 21.2912
| 2022-08-23 08:52 | 469530 | 42.1905 | 32.4228 | 457.6777 | 2022-08-19 08:57 | 459310 | 10220 | 3.9965 | 5755 | 10220 | 0.53229 | 5440.0139 | 5.44 | 9.5283 | 769 | 800 | 784.5 | 775 | 1518.3871 | 1.5184 | 15.5179 | 2.6964 | 27.1799
| 2022-08-24 10:37 | 472210 | 36.3 | 21.5 | 460.88 | 2022-08-19 08:57 | 459310 | 12900 | 5.0694 | 7300 | 12900 | 0.51868 | 6690.972 | 6.691 | 9.239 | 747 | 750 | 748.5 | 749 | 1498.9987 | 1.499 | 19.3371 | 2.6489 | 26.7011
| 2022-08-25 09:05 | 474390 | 37.5651 | 25.6851 | 403.5088 | 2022-08-19 08:57 | 459310 | 15080 | 6.0056 | 8648 | 15080 | 0.46676 | 7038.7269 | 7.0387 | 8.2043 | 695 | 695 | 695 | 787 | 1324.6506 | 1.3247 | 19.9757 | 2.3099 | 23.2835
| 2022-08-30 08:52 | 487120 | 50.06 | 66.41 | 216.76 | 2022-08-26 08:55 | 476740 | 10380 | 3.9979 | 5757 | 10380 | 0.33323 | 3458.9274 | 3.4589 | 6.0563 | 713 | 702 | 707.5 | 767 | 1383.6375 | 1.3836 | 14.3622 | 2.4947 | 25.1469
| 2022-08-31 08:52 | 489220 | 47.29 | 34.95 | 263.11 | 2022-08-26 08:55 | 476740 | 12480 | 4.9979 | 7197 | 12480 | 0.34535 | 4309.968 | 4.31 | 6.0365 | 707 | 681 | 694 | 765 | 1360.7843 | 1.3608 | 16.9826 | 2.3597 | 23.7855
| 2022-09-01 08:49 | 491130 | 47.92 | 10.48 | 284.06 | 2022-08-26 08:55 | 476740 | 14390 | 5.9958 | 8634 | 14390 | 0.34246 | 4927.9994 | 4.928 | 5.7533 | 722 | 738 | 730 | 766 | 1429.5039 | 1.4295 | 20.5706 | 2.3825 | 24.0157
| 2022-09-06 08:51 | 503500 | 58.4 | 19.47 | 388.7 | 2022-09-02 08:53 | 493280 | 10220 | 3.9986 | 5758 | 10220 | 0.46657 | 4768.3454 | 4.7683 | 8.3475 | 757 | 765 | 761 | 761 | 1500 | 1.5 | 15.33 | 2.6624 | 26.8368
| 2022-09-07 08:50 | 6480 | 52.33 | 16.35 | 344.31 | 2022-09-02 08:53 | 493280 | 13200 | 4.9979 | 7197 | 13200 | 0.41299 | 5451.468 | 5.4515 | 7.6352 | 727 | 728 | 727.5 | 771 | 1415.3696 | 1.4154 | 18.6829 | 2.5959 | 26.1669
| 2022-09-08 08:52 | 9190 | 41.63 | 12.43 | 358.68 | 2022-09-02 08:53 | 493280 | 15910 | 5.9993 | 8639 | 15910 | 0.41274 | 6566.6934 | 6.5667 | 7.662 | 736 | 748 | 742 | 777 | 1432.4324 | 1.4324 | 22.79 | 2.638 | 26.5914
| 2022-09-13 08:54 | 19540 | 31.58 | 30.66 | 297.59 | 2022-09-09 08:53 | 11490 | 8050 | 4.0007 | 5761 | 8050 | 0.35983 | 2896.6315 | 2.8966 | 5.0682 | 720 | 716 | 718 | 767 | 1404.1721 | 1.4042 | 11.3036 | 1.9621 | 19.7778
| 2022-09-20 08:54 | 35980 | 21.37 | 119.1 | 117.25 | 2022-09-16 09:01 | 26080 | 9900 | 3.9951 | 5753 | 9900 | 0.25772 | 2551.428 | 2.5514 | 4.4704 | 528 | 545 | 536.5 | 772 | 1042.4223 | 1.0424 | 10.32 | 1.7938 | 18.0819
| 2022-09-27 08:54 | 54480 | 53.43 | 86.88 | 182.65 | 2022-09-23 08:50 | 43200 | 11280 | 4.0028 | 5764 | 11280 | 0.32296 | 3642.9888 | 3.643 | 6.3708 | 643 | 652 | 647.5 | 765 | 1269.6078 | 1.2696 | 14.3212 | 2.4846 | 25.0447
| 2022-09-28 09:00 | 57200 | 56.996 | 80.4522 | 167.2459 | 2022-09-23 08:50 | 43200 | 14000 | 5.0069 | 7210 | 14000 | 0.30469 | 4265.7173 | 4.2657 | 5.9637 | 638 | 663 | 650.5 | 770 | 1267.2078 | 1.2672 | 17.7409 | 2.4606 | 24.8028
| 2022-10-04 08:55 | 71490 | 11.11 | 119.04 | 100.15 | 2022-09-30 08:55 | 61720 | 9770 | 4 | 5760 | 9770 | 0.2303 | 2250.031 | 2.25 | 3.9376 | 431 | 432 | 431.5 | 774 | 836.2403 | 0.83624 | 8.1701 | 1.4184 | 14.2976
| 2022-10-11 08:52 | 89350 | 27.06 | 142.77 | 116.75 | 2022-10-07 08:52 | 79600 | 9750 | 4 | 5760 | 9750 | 0.28658 | 2794.155 | 2.7942 | 4.8898 | 583 | 589 | 586 | 732 | 1200.8197 | 1.2008 | 11.708 | 2.0326 | 20.489
| 2022-10-18 08:44 | 104430 | 59.1524 | 248.0762 | 161.0931 | 2022-10-14 08:53 | 95370 | 9060 | 3.9937 | 5751 | 9060 | 0.46832 | 4242.9941 | 4.243 | 7.4369 | 788 | 814 | 801 | 750 | 1602 | 1.602 | 14.5141 | 2.5238 | 25.4395
| 2022-10-19 08:44 | 106810 | 53.62 | 211.12 | 175.25 | 2022-10-14 08:53 | 95370 | 11440 | 4.9938 | 7191 | 11440 | 0.43999 | 5033.4856 | 5.0335 | 7.0557 | 796 | 786 | 791 | 777 | 1527.027 | 1.527 | 17.4692 | 2.4293 | 24.4875
| 2022-10-20 08:59 | 109270 | 53.03 | 196.81 | 174.5 | 2022-10-14 08:53 | 95370 | 13900 | 6.0042 | 8646 | 13900 | 0.42434 | 5898.326 | 5.8983 | 6.8766 | 757 | 778 | 767.5 | 774 | 1487.4031 | 1.4874 | 20.6749 | 2.3913 | 24.104
| 2022-10-25 08:57 | 121610 | 60.3164 | 87.546 | 182.0289 | 2022-10-21 08:48 | 111570 | 10040 | 4.0062 | 5769 | 10040 | 0.32989 | 3312.1083 | 3.3121 | 5.7871 | 710 | 693 | 701.5 | 759 | 1386.3636 | 1.3864 | 13.9191 | 2.4127 | 24.3204
| 2022-10-26 08:48 | 123960 | 55.8213 | 71.9607 | 187.2728 | 2022-10-21 08:48 | 111570 | 12390 | 5 | 7200 | 12390 | 0.31505 | 3903.5282 | 3.9035 | 5.4649 | 748 | 740 | 744 | 777 | 1436.2934 | 1.4363 | 17.7957 | 2.4716 | 24.9139
| 2022-11-01 08:48 | 136140 | 42.7241 | 101.2785 | 202.6769 | 2022-10-28 08:42 | 128260 | 7880 | 4.0042 | 5766 | 7880 | 0.34668 | 2731.8347 | 2.7318 | 4.7757 | 675 | 675 | 675 | 724 | 1398.4807 | 1.3985 | 11.02 | 1.9112 | 19.265
| 2022-11-08 08:53 | 151730 | 37.29 | 113.39 | 121 | 2022-11-04 08:53 | 143000 | 8730 | 4 | 5760 | 8730 | 0.27168 | 2371.7664 | 2.3718 | 4.1506 | 627 | 648 | 637.5 | 768 | 1245.1172 | 1.2451 | 10.8699 | 1.8871 | 19.0223
| 2022-11-15 08:54 | 168370 | 62.89 | 150.52 | 141.96 | 2022-11-11 08:54 | 157880 | 10490 | 4 | 5760 | 10490 | 0.35537 | 3727.8313 | 3.7278 | 6.5237 | 733 | 743 | 738 | 763 | 1450.8519 | 1.4509 | 15.2194 | 2.6423 | 26.634
| 2022-11-16 08:58 | 170870 | 51.52 | 142.61 | 153.37 | 2022-11-11 08:54 | 157880 | 12990 | 5.0028 | 7204 | 12990 | 0.3475 | 4514.025 | 4.514 | 6.3161 | 689 | 707 | 698 | 750 | 1396 | 1.396 | 18.134 | 2.5172 | 25.3736
| 2022-11-17 | 173490 | 48.476 | 145.149 | 140.753 | 2022-11-11 08:54 | 157880 | 15610 | 5.6292 | 8106 | 15610 | 0.33438 | 5219.6406 | 5.2196 | 6.4907 | 660 | 693 | 676.5 | 784 | 1294.324 | 1.2943 | 20.2044 | 2.4925 | 25.1246
| 2022-11-22 08:56 | 185720 | 32.84 | 119.77 | 144.98 | 2022-11-18 08:52 | 175500 | 10220 | 4.0028 | 5764 | 10220 | 0.29759 | 3041.3698 | 3.0414 | 5.3187 | 611 | 601 | 606 | 784 | 1159.4388 | 1.1594 | 11.8495 | 2.0558 | 20.7222
| 2022-11-29 08:44 | 203890 | 19.14 | 89.35 | 141.09 | 2022-11-25 09:00 | 193370 | 10520 | 3.9889 | 5744 | 10520 | 0.24958 | 2625.5816 | 2.6256 | 4.6076 | 574 | 596 | 585 | 778 | 1127.892 | 1.1279 | 11.8654 | 2.0657 | 20.8223
| 2022-11-30 10:09 | 206430 | 16.869 | 98.138 | 164.598 | 2022-11-25 09:00 | 193370 | 13060 | 5.0479 | 7269 | 13060 | 0.2796 | 3651.6413 | 3.6516 | 5.0638 | 586 | 588 | 587 | 766 | 1149.4778 | 1.1495 | 15.0122 | 2.0652 | 20.8176
| 2022-12-06 08:53 | 221040 | 22.18 | 139.44 | 196.46 | 2022-12-02 08:54 | 211030 | 10010 | 3.9993 | 5729 | 10010 | 0.35808 | 3584.3808 | 3.5844 | 6.3066 | 659 | 663 | 661 | 755 | 1313.245 | 1.3132 | 13.1456 | 2.2946 | 23.1293
| 2022-12-07 08:56 | 223720 | 24.72 | 115.11 | 227.79 | 2022-12-02 08:54 | 211030 | 12690 | 5.0014 | 7202 | 12690 | 0.36762 | 4665.0978 | 4.6651 | 6.5293 | 683 | 670 | 676.5 | 755 | 1344.0397 | 1.344 | 17.0559 | 2.3682 | 23.8716
| 2022-12-08 08:51 | 226340 | 27.65 | 102.47 | 217.41 | 2022-12-02 08:54 | 211030 | 15310 | 5.9979 | 8637 | 15310 | 0.34753 | 5320.6843 | 5.3207 | 6.2096 | 701 | 700 | 700.5 | 776 | 1354.0593 | 1.3541 | 20.7306 | 2.4002 | 24.1942
` | 2022-12-13 08:56 | 235330 | 27.61 | 74.11 | 137.43 | 2022-12-09 08:49 | 228720 | 6610 | 4.0049 | 5767 | 6610 | 0.23915 | 1580.7815 | 1.5808 | 2.763 | 468 | 464 | 466 | 748 | 934.492 | 0.93449 | 6.177 | 1.0711 | 10.7966
| 2022-12-20 09:10 | 252950 | 14.99 | 113.82 | 144.2 | 2022-12-16 08:49 | 241910 | 11040 | 4.0146 | 5781 | 11040 | 0.27301 | 3014.0304 | 3.014 | 5.2554 | 639 | 608 | 623.5 | 778 | 1202.1208 | 1.2021 | 13.2714 | 2.2957 | 23.1406
| 2022-12-28 08:52 | 272660 | 28.2666 | 78.9343 | 248.5732 | 2022-12-23 08:56 | 260720 | 11940 | 4.9972 | 7196 | 11940 | 0.35577 | 4247.9432 | 4.2479 | 5.9504 | 807 | 819 | 813 | 780 | 1563.4615 | 1.5635 | 18.6677 | 2.5942 | 26.1494
| 2022-12-29 08:49 | 274590 | 28.15 | 79.35 | 261.47 | 2022-12-23 08:56 | 260720 | 13870 | 5.9951 | 8633 | 13870 | 0.36897 | 5117.6139 | 5.1176 | 5.9754 | 758 | 757 | 757.5 | 773 | 1469.9224 | 1.4699 | 20.3878 | 2.3616 | 23.8051
| 2023-01-03 08:45 | 284940 | 28.18 | 117.55 | 203.94 | 2022-12-30 08:49 | 276210 | 8730 | 3.9972 | 5756 | 8730 | 0.34967 | 3052.6191 | 3.0526 | 5.3458 | 774 | 790 | 782 | 765 | 1533.3333 | 1.5333 | 13.386 | 2.3256 | 23.4418
| 2023-01-10 08:53 | 300750 | 15.01 | 88.36 | 182.87 | 2023-01-06 08:48 | 291940 | 8810 | 4.0035 | 5765 | 8810 | 0.28624 | 2521.7744 | 2.5218 | 4.4093 | 636 | 630 | 633 | 754 | 1259.2838 | 1.2593 | 11.0943 | 1.9244 | 19.3982
| 2023-01-17 08:43 | 314680 | 41.15 | 58.27 | 164 | 2023-01-13 09:04 | 306440 | 8240 | 3.9854 | 5739 | 8240 | 0.26342 | 2170.5808 | 2.1706 | 3.8124 | 697 | 651 | 674 | 768 | 1316.4062 | 1.3164 | 10.8472 | 1.8901 | 19.052
| 2023-01-24 08:55 | 329200 | 39.8 | 50.91 | 197.23 | 2023-01-20 08:50 | 320770 | 8430 | 4.0035 | 5765 | 8430 | 0.28794 | 2427.3342 | 2.4273 | 4.2442 | 606 | 613 | 609.5 | 744 | 1228.8306 | 1.2288 | 10.359 | 1.7969 | 18.1126
| 2023-01-31 08:57 | 341280 | 26.39 | 122.03 | 165.53 | 2023-01-27 08:53 | 334880 | 6400 | 4.0028 | 5764 | 6400 | 0.31395 | 2009.28 | 2.0093 | 3.5138 | 641 | 668 | 654.5 | 767 | 1279.987 | 1.28 | 8.1919 | 1.4212 | 14.3259
| 2023-02-07 09:05 | 356580 | 31.24 | 69.48 | 194.3 | 2023-02-03 09:00 | 346091 | 10489 | 4.0035 | 5765 | 10489 | 0.29502 | 3094.4648 | 3.0945 | 5.4106 | 570 | 577 | 573.5 | 771 | 1115.7588 | 1.1158 | 11.7032 | 2.03 | 20.4628
| 2023-02-14 09:10 | 370662 | 29.03 | 61.82 | 174.24 | 2023-02-10 08:54 | 363240 | 7422 | 4.0111 | 5776 | 7422 | 0.26509 | 1967.498 | 1.9675 | 3.4336 | 674 | 664 | 669 | 753 | 1332.6693 | 1.3327 | 9.8911 | 1.7124 | 17.2614
| 2023-02-21 08:52 | 384970 | 30.12 | 64.05 | 213.9 | 2023-02-17 08:52 | 377010 | 7960 | 4 | 5760 | 7960 | 0.30807 | 2452.2372 | 2.4522 | 4.2914 | 779 | 679 | 729 | 736 | 1485.7337 | 1.4857 | 11.8264 | 2.0532 | 20.6963
| 2023-02-28 08:51 | 399920 | 89.64 | 144.38 | 168.91 | 2023-02-24 09:02 | 391050 | 8870 | 3.9924 | 5749 | 8870 | 0.40293 | 3573.9891 | 3.574 | 6.2664 | 875 | 866 | 870.5 | 741 | 1762.1457 | 1.7621 | 15.6302 | 2.7188 | 27.4052
| 2023-03-01 08:53 | 402150 | 88.29 | 126.08 | 188.19 | 2023-02-24 09:02 | 391050 | 11100 | 4.9938 | 7191 | 11100 | 0.40256 | 4468.416 | 4.4684 | 6.2636 | 849 | 870 | 859.5 | 736 | 1751.6984 | 1.7517 | 19.4439 | 2.7039 | 27.2555
| 2023-03-02 08:45 | 404240 | 82.99 | 121.46 | 201.67 | 2023-02-24 09:02 | 391050 | 13190 | 5.9882 | 8623 | 13190 | 0.40612 | 5356.7228 | 5.3567 | 6.2618 | 896 | 863 | 879.5 | 765 | 1724.5098 | 1.7245 | 22.7463 | 2.6379 | 26.5896
| 2023-03-07 08:48 | 414950 | 40.05 | 100 | 171.4 | 2023-03-03 09:00 | 406170 | 8780 | 3.9917 | 5748 | 8780 | 0.31145 | 2734.531 | 2.7345 | 4.7954 | 727 | 735 | 731 | 769 | 1425.8778 | 1.4259 | 12.5192 | 2.178 | 21.9544
| 2023-03-14 09:00 | 431060 | 59.25 | 113.05 | 198.55 | 2023-03-10 08:55 | 422080 | 8980 | 4.0035 | 5765 | 8980 | 0.37085 | 3330.233 | 3.3302 | 5.8229 | 705 | 724 | 714.5 | 778 | 1377.5707 | 1.3776 | 12.3706 | 2.1458 | 21.6297
| 2023-03-21 08:55 | 445750 | 71.3 | 108.55 | 243.47 | 2023-03-17 08:53 | 436680 | 9070 | 4.0014 | 5762 | 9070 | 0.42332 | 3839.5124 | 3.8395 | 6.7168 | 736 | 749 | 742.5 | 751 | 1483.0226 | 1.483 | 13.451 | 2.3344 | 23.5311
| 2023-03-22 08:47 | 448350 | 78.67 | 110.6 | 265.22 | 2023-03-17 08:53 | 436680 | 11670 | 4.9958 | 7194 | 11670 | 0.45449 | 5303.8983 | 5.3039 | 7.4317 | 794 | 795 | 794.5 | 783 | 1522.0307 | 1.522 | 17.7621 | 2.469 | 24.8877
| 2023-03-23 08:44 | 450290 | 70.39 | 92.28 | 265.85 | 2023-03-17 08:53 | 436680 | 13610 | 5.9938 | 8631 | 13610 | 0.42852 | 5832.1572 | 5.8322 | 6.8113 | 728 | 734 | 731 | 724 | 1514.5028 | 1.5145 | 20.6124 | 2.3882 | 24.0729
| 2023-03-28 09:09 | 458860 | 24.33 | 69.197 | 184.68 | 2023-03-24 08:46 | 451910 | 6950 | 4.016 | 5783 | 6950 | 0.27821 | 1933.5386 | 1.9335 | 3.3702 | 502 | 508 | 505 | 761 | 995.4008 | 0.9954 | 6.918 | 1.1963 | 12.0584
| 2023-04-04 08:44 | 472370 | 33.06 | 72.48 | 231.28 | 2023-03-31 08:50 | 463030 | 9340 | 3.9958 | 5754 | 9340 | 0.33682 | 3145.8988 | 3.1459 | 5.5111 | 637 | 678 | 657.5 | 782 | 1261.1893 | 1.2612 | 11.7795 | 2.0472 | 20.6356
| 2023-04-11 08:44 | 488140 | 49.76 | 94.49 | 235.72 | 2023-04-06 08:49 | 476940 | 11200 | 4.9965 | 7195 | 11200 | 0.37997 | 4255.664 | 4.2557 | 5.9621 | 631 | 646 | 638.5 | 752 | 1273.6037 | 1.2736 | 14.2644 | 1.9825 | 19.984
| 2023-04-18 08:15 | 4200 | 57.0967 | 158.5123 | 236.5966 | 2023-04-14 08:54 | 495280 | 8920 | 3.9729 | 5721 | 8920 | 0.45221 | 4033.6735 | 4.0337 | 7.107 | 746 | 740 | 743 | 786 | 1417.9389 | 1.4179 | 12.648 | 2.2108 | 22.2849
| 2023-04-19 08:14 | 6640 | 58.05 | 154.1 | 242.4 | 2023-04-14 08:54 | 495280 | 11360 | 4.9722 | 7160 | 11360 | 0.45455 | 5163.688 | 5.1637 | 7.2695 | 783 | 781 | 782 | 770 | 1523.3766 | 1.5234 | 17.3056 | 2.417 | 24.3631
| 2023-04-20 08:33 | 8840 | 37.68 | 166.1 | 236.06 | 2023-04-14 08:54 | 495280 | 13560 | 5.9854 | 8619 | 13560 | 0.43984 | 5964.2304 | 5.9642 | 6.9752 | 770 | 767 | 768.5 | 751 | 1534.9534 | 1.535 | 20.814 | 2.4149 | 24.3421
| 2023-04-25 08:53 | 20640 | 32.12 | 362.32 | 141.43 | 2023-04-21 08:40 | 9989 | 10651 | 4.009 | 5773 | 10651 | 0.53587 | 5707.5514 | 5.7076 | 9.9657 | 702 | 750 | 726 | 771 | 1412.4514 | 1.4125 | 15.044 | 2.6059 | 26.2677
| 2023-04-26 08:52 | 22880 | 29.36 | 307.66 | 136.09 | 2023-04-21 08:40 | 9989 | 12891 | 5.0083 | 7212 | 12891 | 0.47311 | 6098.861 | 6.0989 | 8.5242 | 644 | 649 | 646.5 | 786 | 1233.7786 | 1.2338 | 15.9046 | 2.2053 | 22.2294
| 2023-04-27 08:46 | 24470 | 23.32 | 280.66 | 136.74 | 2023-04-21 08:40 | 9989 | 14481 | 6.0042 | 8646 | 14481 | 0.44072 | 6382.0663 | 6.3821 | 7.4406 | 687 | 656 | 671.5 | 758 | 1328.8259 | 1.3288 | 19.2427 | 2.2256 | 22.4343
| 2023-05-02 08:46 | 35690 | 19 | 77.4 | 186.9 | 2023-04-28 08:42 | 26620 | 9070 | 4.0028 | 5764 | 9070 | 0.2833 | 2569.531 | 2.5695 | 4.4936 | 617 | 623 | 620 | 763 | 1218.8729 | 1.2189 | 11.0552 | 1.918 | 19.3331
| 2023-05-09 09:00 | 51440 | 46.04 | 117.89 | 182.08 | 2023-05-05 08:49 | 42070 | 9370 | 4.0076 | 5771 | 9370 | 0.34601 | 3242.1137 | 3.2421 | 5.6629 | 604 | 602 | 603 | 739 | 1223.9513 | 1.224 | 11.4684 | 1.9873 | 20.0315
| 2023-05-16 08:49 | 67500 | 20.48 | 62.15 | 230.12 | 2023-05-12 08:48 | 58230 | 9270 | 4.0007 | 5761 | 9270 | 0.31275 | 2899.1925 | 2.8992 | 5.0727 | 654 | 664 | 659 | 732 | 1350.4098 | 1.3504 | 12.5183 | 2.1729 | 21.9032
| 2023-05-23 09:05 | 83160 | 99.74 | 138.799 | 154.48 | 2023-05-19 08:53 | 74390 | 8770 | 4.0083 | 5772 | 8770 | 0.39302 | 3446.7766 | 3.4468 | 6.0193 | 875 | 856 | 865.5 | 784 | 1655.9311 | 1.6559 | 14.5225 | 2.516 | 25.3616
| 2023-05-24 09:09 | 85350 | 118.197 | 162.18 | 128.69 | 2023-05-19 08:53 | 74390 | 10960 | 5.0111 | 7216 | 10960 | 0.40907 | 4483.3743 | 4.4834 | 6.2628 | 863 | 869 | 866 | 765 | 1698.0392 | 1.698 | 18.6105 | 2.5791 | 25.9969
| 2023-05-25 09:12 | 86240 | 111.4 | 105.39 | 193.86 | 2023-05-19 08:53 | 74390 | 11850 | 6.0132 | 8659 | 11850 | 0.41065 | 4866.2025 | 4.8662 | 5.6648 | 842 | 808 | 825 | 762 | 1624.0157 | 1.624 | 19.2446 | 2.2225 | 22.4028
| 2023-05-30 08:46 | 94580 | 4.81 | 114.87 | 262.54 | 2023-05-26 09:10 | 87500 | 7080 | 3.9833 | 5736 | 7080 | 0.38222 | 2706.1176 | 2.7061 | 4.7555 | 839 | 869 | 854 | 766 | 1672.3238 | 1.6723 | 11.8401 | 2.0642 | 20.8068
| 2023-06-06 09:10 | 108840 | 5.48 | 170.05 | 134.17 | 2023-06-02 08:56 | 99980 | 8860 | 4.0097 | 5774 | 8860 | 0.3097 | 2743.942 | 2.7439 | 4.7903 | 863 | 899 | 881 | 764 | 1729.712 | 1.7297 | 15.3252 | 2.6542 | 26.7542
| 2023-06-07 09:09 | 111410 | 7.18 | 152.39 | 139.97 | 2023-06-02 08:56 | 99980 | 11430 | 5.009 | 7213 | 11430 | 0.29954 | 3423.7422 | 3.4237 | 4.7846 | 851 | 870 | 860.5 | 772 | 1671.956 | 1.672 | 19.1105 | 2.6494 | 26.7064
| 2023-06-08 09:15 | 114090 | 4.44 | 139.59 | 163.17 | 2023-06-02 08:56 | 99980 | 14110 | 6.0132 | 8659 | 14110 | 0.3072 | 4334.592 | 4.3346 | 5.0459 | 870 | 856 | 863 | 760 | 1703.2895 | 1.7033 | 24.0334 | 2.7755 | 27.9775
| 2023-06-13 08:56 | 121330 | 4.32 | 13.68 | 166.61 | 2023-06-09 09:07 | 116430 | 4900 | 3.9924 | 5749 | 4900 | 0.18461 | 904.589 | 0.90459 | 1.5861 | 404 | 401 | 402.5 | 754 | 800.7294 | 0.80073 | 3.9236 | 0.68248 | 6.8794
| 2023-06-20 09:11 | 132990 | 5.56 | 165.47 | 191.68 | 2023-06-16 09:10 | 125870 | 7120 | 4.0007 | 5761 | 7120 | 0.36271 | 2582.4952 | 2.5825 | 4.5186 | 734 | 710 | 722 | 740 | 1463.5135 | 1.4635 | 10.4202 | 1.8088 | 18.2322
| 2023-06-27 08:44 | 144700 | 5.0663 | 18.1987 | 155.3125 | 2023-06-23 09:15 | 138170 | 6530 | 3.9785 | 5729 | 6530 | 0.17858 | 1166.1114 | 1.1661 | 2.0517 | 484 | 493 | 488.5 | 786 | 932.2519 | 0.93225 | 6.0876 | 1.0626 | 10.711
| 2023-07-04 09:03 | 156170 | 14.62 | 75.95 | 100.39 | 2023-06-30 09:06 | 149760 | 6410 | 3.9979 | 5757 | 6410 | 0.19096 | 1224.0536 | 1.2241 | 2.1432 | 522 | 514 | 518 | 748 | 1038.7701 | 1.0388 | 6.6585 | 1.1566 | 11.6585
| 2023-07-11 08:56 | 174380 | 5.37 | 29.63 | 70.89 | 2023-07-07 08:46 | 164000 | 10380 | 4.0069 | 5770 | 10380 | 0.10589 | 1099.1382 | 1.0991 | 1.9202 | 383 | 366 | 374.5 | 758 | 741.095 | 0.74109 | 7.6926 | 1.3332 | 13.4387
| 2023-07-13 08:55 | 179350 | 8.22 | 11.58 | 124.19 | 2023-07-07 08:46 | 164000 | 15350 | 6.0063 | 8649 | 15350 | 0.14399 | 2210.2465 | 2.2102 | 2.5759 | 414 | 400 | 407 | 753 | 810.757 | 0.81076 | 12.4451 | 1.4389 | 14.5042
| 2023-07-17 17:00 | 190370 | 7.24 | 8.67 | 112.74 | 2023-07-14 08:57 | 182050 | 8320 | 3.3354 | 4803 | 8320 | 0.12865 | 1070.368 | 1.0704 | 2.2464 | 543 | 552 | 547.5 | 776 | 1058.3119 | 1.0583 | 8.8052 | 1.8333 | 18.4793
| 2023-07-25 09:24 | 210110 | 8.8597 | 86.4786 | 88.5287 | 2023-07-21 08:55 | 199120 | 10990 | 4.0201 | 5789 | 10990 | 0.18387 | 2020.6988 | 2.0207 | 3.5185 | 580 | 575 | 577.5 | 777 | 1114.8649 | 1.1149 | 12.2524 | 2.1165 | 21.3342
| 2023-08-01 08:55 | 227380 | 11.099 | 133.146 | 71.419 | 2023-07-28 09:01 | 218150 | 9230 | 3.9958 | 5754 | 9230 | 0.21566 | 1990.5787 | 1.9906 | 3.4871 | 585 | 595 | 590 | 784 | 1128.8265 | 1.1288 | 10.4191 | 1.8108 | 18.2524
| 2023-08-08 08:49 | 243080 | 14.91 | 59.71 | 107.89 | 2023-08-04 08:44 | 233640 | 9440 | 4.0035 | 5765 | 9440 | 0.18251 | 1722.8944 | 1.7229 | 3.0125 | 492 | 490 | 491 | 745 | 988.5906 | 0.98859 | 9.3323 | 1.6188 | 16.3174
| 2023-08-15 09:00 | 260350 | 20.28 | 63.1 | 98.93 | 2023-08-11 08:43 | 250990 | 9360 | 4.0118 | 5777 | 9360 | 0.18231 | 1706.4216 | 1.7064 | 2.9775 | 466 | 502 | 484 | 785 | 924.8408 | 0.92484 | 8.6565 | 1.4984 | 15.1043
| 2023-08-22 08:57 | 275980 | 11.53 | 122.65 | 157.85 | 2023-08-18 08:52 | 266100 | 9880 | 4.0035 | 5765 | 9880 | 0.29203 | 2885.2564 | 2.8853 | 5.0448 | 723 | 744 | 733.5 | 783 | 1405.1724 | 1.4052 | 13.8831 | 2.4082 | 24.2744
| 2023-08-29 08:57 | 294050 | 13.01 | 69.056 | 220.197 | 2023-08-25 09:01 | 284060 | 9990 | 3.9972 | 5756 | 9990 | 0.30226 | 3019.6074 | 3.0196 | 5.288 | 703 | 684 | 693.5 | 745 | 1396.3087 | 1.3963 | 13.9491 | 2.4234 | 24.4279
| 2023-09-05 08:56 | 311090 | 13.78 | 6.73 | 152.08 | 2023-09-01 09:00 | 301000 | 10090 | 3.9972 | 5756 | 10090 | 0.17259 | 1741.4331 | 1.7414 | 3.0496 | 564 | 592 | 578 | 779 | 1112.9653 | 1.113 | 11.2298 | 1.951 | 19.6658
| 2023-09-12 08:58 | 326610 | 14.165 | 11.57 | 151.41 | 2023-09-08 08:57 | 318250 | 8360 | 4.0007 | 5761 | 8360 | 0.17714 | 1480.9322 | 1.4809 | 2.5912 | 518 | 554 | 536 | 742 | 1083.558 | 1.0836 | 9.0585 | 1.5724 | 15.8497
| 2023-09-19 08:52 | 344720 | 41.8794 | 36.8664 | 165.6953 | 2023-09-15 09:01 | 334100 | 10620 | 3.9937 | 5751 | 10620 | 0.24444 | 2595.9638 | 2.596 | 4.55 | 673 | 663 | 668 | 775 | 1292.9032 | 1.2929 | 13.7306 | 2.3875 | 24.0662
| 2023-09-26 09:00 | 358880 | 46.7579 | 144.5 | 130.95 | 2023-09-22 08:55 | 350900 | 7980 | 4.0035 | 5765 | 7980 | 0.32221 | 2571.219 | 2.5712 | 4.4957 | 864 | 843 | 853.5 | 751 | 1704.727 | 1.7047 | 13.6037 | 2.3597 | 23.7859
| 2023-10-03 08:51 | 374060 | 60.9496 | 29.7543 | 210.1697 | 2023-09-29 09:11 | 365650 | 8410 | 3.9861 | 5740 | 8410 | 0.30087 | 2530.347 | 2.5303 | 4.4435 | 859 | 857 | 858 | 777 | 1656.3707 | 1.6564 | 13.9301 | 2.4268 | 24.4626
| 2023-10-10 08:57 | 388750 | 29.96 | 44.78 | 188.9 | 2023-10-06 08:54 | 379800 | 8950 | 4.0021 | 5763 | 8950 | 0.26364 | 2359.578 | 2.3596 | 4.1271 | 676 | 699 | 687.5 | 785 | 1313.6943 | 1.3137 | 11.7576 | 2.0402 | 20.565
| 2023-10-17 08:57 | 404390 | 36.7623 | 102.2611 | 121.127 | 2023-10-13 08:55 | 395630 | 8760 | 4.0014 | 5762 | 8760 | 0.26015 | 2278.9177 | 2.2789 | 3.9867 | 688 | 715 | 701.5 | 779 | 1350.7702 | 1.3508 | 11.8327 | 2.0536 | 20.7001
| 2023-10-24 08:59 | 418490 | 35.01 | 107.67 | 92.92 | 2023-10-20 09:01 | 408690 | 9800 | 3.9986 | 5758 | 9800 | 0.2356 | 2308.88 | 2.3089 | 4.0419 | 718 | 700 | 709 | 773 | 1375.8085 | 1.3758 | 13.4829 | 2.3416 | 23.6033
| 2023-10-31 08:56 | 430220 | 16.26 | 67.34 | 92.78 | 2023-10-27 08:55 | 423310 | 6910 | 4.0007 | 5761 | 6910 | 0.17638 | 1218.7858 | 1.2188 | 2.1325 | 342 | 358 | 350 | 746 | 703.7534 | 0.70375 | 4.8629 | 0.84411 | 8.5087
| 2023-11-07 08:55 | 446130 | 58.89 | 169.748 | 154.499 | 2023-11-03 09:01 | 437450 | 8680 | 3.9958 | 5754 | 8680 | 0.38314 | 3325.6292 | 3.3256 | 5.8259 | 755 | 743 | 749 | 776 | 1447.8093 | 1.4478 | 12.567 | 2.184 | 22.0152
| 2023-11-14 08:58 | 461380 | 54.3454 | 106.8317 | 152.3949 | 2023-11-10 08:55 | 452930 | 8450 | 4.0021 | 5763 | 8450 | 0.31357 | 2649.6831 | 2.6497 | 4.6345 | 704 | 702 | 703 | 782 | 1348.4655 | 1.3485 | 11.3945 | 1.9772 | 19.9301
| 2023-11-21 08:59 | 475990 | 41.54 | 101.7 | 171.06 | 2023-11-17 09:00 | 467940 | 8050 | 3.9993 | 5759 | 8050 | 0.3143 | 2530.115 | 2.5301 | 4.4285 | 674 | 691 | 682.5 | 760 | 1347.0395 | 1.347 | 10.8437 | 1.8829 | 18.9797
| 2023-11-27 09:29 | 488200 | 79.77 | 172.907 | 157.087 | 2023-11-24 08:50 | 481380 | 6820 | 3.0271 | 4359 | 6820 | 0.40976 | 2794.5905 | 2.7946 | 6.4624 | 911 | 889 | 900 | 773 | 1746.4424 | 1.7464 | 11.9107 | 2.7324 | 27.5431
| 2023-11-28 08:55 | 490510 | 71.04 | 186.04 | 212.52 | 2023-11-24 08:50 | 481380 | 9130 | 4.0035 | 5765 | 9130 | 0.4696 | 4287.448 | 4.2874 | 7.4965 | 899 | 917 | 908 | 780 | 1746.1538 | 1.7462 | 15.9424 | 2.7654 | 27.875
| 2023-11-29 09:01 | 492550 | 79.39 | 168.05 | 195.25 | 2023-11-24 08:50 | 481380 | 11170 | 5.0076 | 7211 | 11170 | 0.44269 | 4944.8473 | 4.9448 | 6.9122 | 835 | 835 | 835 | 737 | 1699.4573 | 1.6995 | 18.9829 | 2.6325 | 26.5356
| 2023-11-30 08:57 | 494728 | 58.1325 | 169.835 | 216.008 | 2023-11-24 08:50 | 481380 | 13348 | 6.0049 | 8647 | 13348 | 0.44398 | 5926.1852 | 5.9262 | 6.9083 | 898 | 865 | 881.5 | 770 | 1717.2078 | 1.7172 | 22.9213 | 2.6508 | 26.7199
| 2023-12-05 08:52 | 1420 | 50.6122 | 273.1464 | 135.1679 | 2023-12-01 08:55 | 496890 | 4529 | 3.9979 | 5757 | 4529 | 0.45893 | 2078.4782 | 2.0785 | 3.6392 | 668 | 704 | 686 | 780 | 1319.2308 | 1.3192 | 5.9748 | 1.0378 | 10.4613
| 2023-12-06 10:45 | 2260 | 37.23 | 379.43 | 135.88 | 2023-12-01 08:55 | 496890 | 5369 | 5.0764 | 7310 | 5369 | 0.55254 | 2966.5873 | 2.9666 | 4.0907 | 697 | 709 | 703 | 757 | 1392.9987 | 1.393 | 7.479 | 1.0231 | 10.3131
| 2023-12-07 09:14 | 3260 | 31.91 | 412.42 | 134.81 | 2023-12-01 08:55 | 496890 | 6369 | 6.0132 | 8659 | 6369 | 0.57914 | 3688.5427 | 3.6885 | 4.2939 | 707 | 647 | 677 | 768 | 1322.2656 | 1.3223 | 8.4215 | 0.97257 | 9.8035
| 2023-12-12 08:55 | 9430 | 22.91 | 36.45 | 214.67 | 2023-12-08 08:58 | 4520 | 4910 | 3.9979 | 5757 | 4910 | 0.27403 | 1345.4873 | 1.3455 | 2.3558 | 474 | 475 | 474.5 | 760 | 936.5132 | 0.93651 | 4.5983 | 0.79873 | 8.0512
| 2023-12-19 09:01 | 18620 | 19.1041 | 69.1069 | 153.462 | 2023-12-15 09:00 | 13810 | 4810 | 4.0007 | 5761 | 4810 | 0.24167 | 1162.4471 | 1.1624 | 2.0339 | 547 | 549 | 548 | 769 | 1068.9207 | 1.0689 | 5.1415 | 0.89247 | 8.9961
| 2023-12-27 09:00 | 35370 | 21.5492 | 105.4182 | 148.6936 | 2023-12-22 09:00 | 24310 | 11060 | 5 | 7200 | 11060 | 0.27566 | 3048.8114 | 3.0488 | 4.2683 | 869 | 854 | 861.5 | 770 | 1678.2468 | 1.6782 | 18.5614 | 2.578 | 25.986
| 2023-12-28 08:47 | 37600 | 19.6292 | 93.8424 | 141.1367 | 2023-12-22 09:00 | 24310 | 13290 | 5.991 | 8627 | 13290 | 0.25461 | 3383.7442 | 3.3837 | 3.9537 | 810 | 845 | 827.5 | 769 | 1614.1092 | 1.6141 | 21.4515 | 2.4866 | 25.0645
| 2024-01-02 08:51 | 49520 | 45.18 | 69.51 | 147.86 | 2023-12-29 08:57 | 40040 | 9480 | 3.9958 | 5754 | 9480 | 0.26255 | 2488.974 | 2.489 | 4.3602 | 807 | 825 | 816 | 739 | 1656.2923 | 1.6563 | 15.7017 | 2.7288 | 27.5065
| 2024-01-03 09:01 | 51920 | 67.47 | 73.399 | 215.71 | 2023-12-29 08:57 | 40040 | 11880 | 5.0028 | 7204 | 11880 | 0.35658 | 4236.1585 | 4.2362 | 5.9273 | 712 | 755 | 733.5 | 759 | 1449.6047 | 1.4496 | 17.2213 | 2.3905 | 24.0964
| 2024-01-04 09:05 | 54230 | 53.0825 | 76.0195 | 220.4517 | 2023-12-29 08:57 | 40040 | 14190 | 6.0056 | 8648 | 14190 | 0.34955 | 4960.1674 | 4.9602 | 5.7815 | 719 | 769 | 744 | 764 | 1460.733 | 1.4607 | 20.7278 | 2.3968 | 24.1601
| 2024-01-09 08:54 | 64990 | 54.96 | 78.75 | 195.72 | 2024-01-05 09:00 | 56360 | 8630 | 3.9958 | 5754 | 8630 | 0.32943 | 2842.9809 | 2.843 | 4.9804 | 723 | 737 | 730 | 769 | 1423.9272 | 1.4239 | 12.2885 | 2.1356 | 21.5273
| 2024-01-16 08:57 | 78800 | 76.8479 | 72.0113 | 275.3166 | 2024-01-12 08:58 | 70340 | 8460 | 3.9993 | 5759 | 8460 | 0.42418 | 3588.5273 | 3.5885 | 6.281 | 839 | 834 | 836.5 | 776 | 1616.9459 | 1.6169 | 13.6794 | 2.3753 | 23.943
| 2024-01-17 08:58 | 81270 | 83.9758 | 49.9546 | 238.7805 | 2024-01-12 08:58 | 70340 | 10930 | 5 | 7200 | 10930 | 0.37271 | 4073.7299 | 4.0737 | 5.7032 | 817 | 819 | 818 | 761 | 1612.3522 | 1.6124 | 17.623 | 2.4476 | 24.6722
| 2024-01-23 08:55 | 94320 | 68.965 | 49.088 | 203.019 | 2024-01-19 08:59 | 85520 | 8800 | 3.9972 | 5756 | 8800 | 0.32107 | 2825.4336 | 2.8254 | 4.9479 | 660 | 686 | 673 | 776 | 1300.9021 | 1.3009 | 11.4479 | 1.9889 | 20.0478
| 2024-01-30 08:55 | 107940 | 71.751 | 53.0168 | 267.774 | 2024-01-26 09:07 | 100040 | 7900 | 3.9917 | 5748 | 7900 | 0.39254 | 3101.0802 | 3.1011 | 5.4382 | 779 | 821 | 800 | 764 | 1570.6806 | 1.5707 | 12.4084 | 2.1587 | 21.76
| 2024-02-06 08:55 | 120930 | 5.874 | 87.759 | 119.785 | 2024-02-02 08:55 | 112240 | 8690 | 4 | 5760 | 8690 | 0.21342 | 1854.6024 | 1.8546 | 3.2456 | 560 | 566 | 563 | 749 | 1127.5033 | 1.1275 | 9.798 | 1.701 | 17.1465
| 2024-02-13 08:55 | 137620 | 6.676 | 51.1121 | 133.9145 | 2024-02-09 08:54 | 128670 | 8950 | 4.0007 | 5761 | 8950 | 0.1917 | 1715.7389 | 1.7157 | 3.002 | 726 | 710 | 718 | 732 | 1471.3115 | 1.4713 | 13.1682 | 2.2858 | 23.0404
| 2024-02-20 09:03 | 151170 | 6.9715 | 58.8355 | 201.8914 | 2024-02-16 09:10 | 143560 | 7610 | 3.9951 | 5753 | 7610 | 0.2677 | 2037.1847 | 2.0372 | 3.5694 | 825 | 824 | 824.5 | 768 | 1610.3516 | 1.6104 | 12.2548 | 2.1302 | 21.472
| 2024-02-27 08:51 | 165230 | 15.8919 | 86.1611 | 218.012 | 2024-02-23 08:51 | 157120 | 8110 | 4 | 5760 | 8110 | 0.32006 | 2595.7269 | 2.5957 | 4.5425 | 838 | 832 | 835 | 770 | 1626.6234 | 1.6266 | 13.1919 | 2.2903 | 23.0859
| 2024-03-05 08:56 | 178270 | 13.3598 | 45.4674 | 164.7501 | 2024-03-01 09:01 | 171310 | 6960 | 3.9965 | 5755 | 6960 | 0.22358 | 1556.0981 | 1.5561 | 2.7255 | 661 | 662 | 661.5 | 753 | 1317.7291 | 1.3177 | 9.1714 | 1.5936 | 16.0639
| 2024-03-12 08:52 | 191510 | 15.5066 | 30.6337 | 220.486 | 2024-03-08 09:02 | 183660 | 7850 | 3.9931 | 5750 | 7850 | 0.26663 | 2093.0168 | 2.093 | 3.6691 | 711 | 703 | 707 | 739 | 1435.0474 | 1.435 | 11.2651 | 1.9592 | 19.7482
| 2024-03-19 08:50 | 205280 | 10.352 | 57.12 | 286.211 | 2024-03-15 09:04 | 197260 | 8020 | 3.9903 | 5746 | 8020 | 0.35368 | 2836.5377 | 2.8365 | 4.976 | 739 | 751 | 745 | 763 | 1464.6134 | 1.4646 | 11.7462 | 2.0442 | 20.6059
| 2024-03-26 08:43 | 220410 | 43.5572 | 41.5374 | 263.7764 | 2024-03-22 08:58 | 211450 | 8960 | 3.9896 | 5745 | 8960 | 0.34887 | 3125.8844 | 3.1259 | 5.4846 | 813 | 779 | 796 | 736 | 1622.2826 | 1.6223 | 14.5357 | 2.5301 | 25.5038
| 2024-03-27 08:55 | 222610 | 46.269 | 30.92 | 248.69 | 2024-03-22 08:58 | 211450 | 11160 | 4.9979 | 7197 | 11160 | 0.32588 | 3636.8096 | 3.6368 | 5.0937 | 768 | 784 | 776 | 761 | 1529.5664 | 1.5296 | 17.07 | 2.3718 | 23.9079
| 2024-04-02 08:59 | 236490 | 48.34 | 35.526 | 219.86 | 2024-03-28 09:00 | 225060 | 11430 | 4.9993 | 7199 | 11430 | 0.30373 | 3471.5882 | 3.4716 | 4.8609 | 762 | 772 | 767 | 759 | 1515.8103 | 1.5158 | 17.3257 | 2.4067 | 24.2594
| 2024-04-09 08:58 | 250560 | 28.604 | 16.227 | 216.16 | 2024-04-05 08:52 | 242230 | 8330 | 4.0042 | 5766 | 8330 | 0.26099 | 2174.055 | 2.1741 | 3.8006 | 685 | 677 | 681 | 746 | 1369.3029 | 1.3693 | 11.4063 | 1.9782 | 19.9402
| 2024-04-16 08:58 | 265330 | 44.263 | 38.219 | 183.401 | 2024-04-12 08:53 | 256480 | 8850 | 4.0035 | 5765 | 8850 | 0.26588 | 2353.0646 | 2.3531 | 4.1143 | 825 | 827 | 826 | 736 | 1683.4239 | 1.6834 | 14.8983 | 2.5843 | 26.0494
| 2024-04-17 08:59 | 267460 | 40.075 | 19.292 | 201.86 | 2024-04-12 08:53 | 256480 | 10980 | 5.0042 | 7206 | 10980 | 0.26123 | 2868.2725 | 2.8683 | 4.0122 | 783 | 809 | 796 | 758 | 1575.1979 | 1.5752 | 17.2957 | 2.4002 | 24.1938
| 2024-04-23 08:53 | 280150 | 70.818 | 126.214 | 210.841 | 2024-04-19 08:55 | 271590 | 8560 | 3.9986 | 5758 | 8560 | 0.40787 | 3491.3929 | 3.4914 | 6.1121 | 910 | 844 | 877 | 769 | 1710.6632 | 1.7107 | 14.6433 | 2.5431 | 25.6346
| 2024-04-30 09:01 | 293060 | 21.23 | 65.179 | 166.08 | 2024-04-26 08:58 | 284870 | 8190 | 4.0021 | 5763 | 8190 | 0.25249 | 2067.8849 | 2.0679 | 3.6169 | 727 | 726 | 726.5 | 760 | 1433.8816 | 1.4339 | 11.7435 | 2.0377 | 20.5404
| 2024-05-07 09:03 | 307750 | 18.31 | 79.964 | 129.174 | 2024-05-03 08:58 | 299440 | 8310 | 4.0035 | 5765 | 8310 | 0.22745 | 1890.0929 | 1.8901 | 3.3048 | 701 | 711 | 706 | 779 | 1359.4352 | 1.3594 | 11.2969 | 1.9596 | 19.7524
| 2024-05-14 09:01 | 322850 | 54.087 | 37.347 | 249.45 | 2024-05-10 09:00 | 314190 | 8660 | 4.0007 | 5761 | 8660 | 0.34088 | 2952.0554 | 2.9521 | 5.1652 | 909 | 904 | 906.5 | 759 | 1791.502 | 1.7915 | 15.5144 | 2.693 | 27.1455
| 2024-05-15 09:00 | 325210 | 59.804 | 13.157 | 241.89 | 2024-05-10 09:00 | 314190 | 11020 | 5 | 7200 | 11020 | 0.31485 | 3469.658 | 3.4697 | 4.8575 | 912 | 897 | 904.5 | 764 | 1775.8508 | 1.7759 | 19.5699 | 2.718 | 27.3978
| 2024-05-16 08:59 | 327410 | 37.47 | 11.022 | 213.39 | 2024-05-10 09:00 | 314190 | 13220 | 5.9993 | 8639 | 13220 | 0.26188 | 3462.08 | 3.4621 | 4.0396 | 851 | 866 | 858.5 | 754 | 1707.8912 | 1.7079 | 22.5783 | 2.6135 | 26.3444
| 2024-05-21 08:55 | 337550 | 22.441 | 86.088 | 197.484 | 2024-05-17 08:58 | 329130 | 8420 | 3.9979 | 5757 | 8420 | 0.30601 | 2576.6295 | 2.5766 | 4.5115 | 656 | 686 | 671 | 741 | 1358.2996 | 1.3583 | 11.4369 | 1.9866 | 20.025
| 2024-05-28 08:48 | 352190 | 29.6835 | 84.9403 | 235.2358 | 2024-05-24 09:00 | 344210 | 7980 | 3.9917 | 5748 | 7980 | 0.34986 | 2791.8794 | 2.7919 | 4.896 | 930 | 960 | 945 | 772 | 1836.1399 | 1.8361 | 14.6524 | 2.5491 | 25.6952
| 2024-05-29 08:58 | 353820 | 28.6838 | 38.1878 | 262.8967 | 2024-05-24 09:00 | 344210 | 9610 | 4.9986 | 7198 | 9610 | 0.32977 | 3169.0738 | 3.1691 | 4.4379 | 854 | 892 | 873 | 770 | 1700.6494 | 1.7006 | 16.3432 | 2.2705 | 22.8869
| 2024-06-04 08:52 | 363990 | 14.331 | 97.53 | 158.561 | 2024-05-31 08:56 | 356440 | 7550 | 3.9972 | 5756 | 7550 | 0.27042 | 2041.6861 | 2.0417 | 3.5754 | 709 | 713 | 711 | 750 | 1422 | 1.422 | 10.7361 | 1.8652 | 18.8012
| 2024-06-11 08:51 | 378770 | 11.9185 | 106.8581 | 127.0169 | 2024-06-07 09:01 | 370330 | 8440 | 3.9931 | 5750 | 8440 | 0.24579 | 2074.4978 | 2.0745 | 3.6367 | 746 | 743 | 744.5 | 771 | 1448.4436 | 1.4484 | 12.2249 | 2.1261 | 21.4307
| 2024-06-18 09:00 | 391150 | 30.2254 | 164.0964 | 148.2131 | 2024-06-14 08:57 | 382990 | 8160 | 4.0021 | 5763 | 8160 | 0.34253 | 2795.0845 | 2.7951 | 4.8889 | 1030 | 1031 | 1030.5 | 772 | 2002.2668 | 2.0023 | 16.3385 | 2.8351 | 28.5775
| 2024-06-19 08:57 | 393150 | 30.56 | 156.43 | 155.698 | 2024-06-14 08:57 | 382990 | 10160 | 5 | 7200 | 10160 | 0.34269 | 3481.7101 | 3.4817 | 4.8744 | 954 | 931 | 942.5 | 766 | 1845.6266 | 1.8456 | 18.7516 | 2.6044 | 26.2522
| 2024-06-20 09:05 | 394970 | 29.67 | 134.56 | 172.65 | 2024-06-14 08:57 | 382990 | 11980 | 6.0056 | 8648 | 11980 | 0.33688 | 4035.8224 | 4.0358 | 4.7041 | 973 | 940 | 956.5 | 766 | 1873.0418 | 1.873 | 22.439 | 2.5947 | 26.1547
| 2024-06-25 08:58 | 405290 | 21.693 | 90.456 | 175.56 | 2024-06-21 09:00 | 397040 | 8250 | 3.9986 | 8648 | 8250 | 0.28771 | 2373.5993 | 2.3736 | 2.7666 | 903 | 927 | 915 | 731 | 1877.565 | 1.8776 | 15.4899 | 1.7912 | 18.0548
| 2024-07-02 08:59 | 417820 | 19.486 | 42.3656 | 206.8743 | 2024-06-28 09:00 | 410250 | 7570 | 3.9993 | 5759 | 7570 | 0.26873 | 2034.2551 | 2.0343 | 3.5606 | 863 | 853 | 858 | 749 | 1718.2911 | 1.7183 | 13.0075 | 2.2586 | 22.767
| 2024-07-09 09:00 | 432610 | 9.949 | 51.1186 | 117.323 | 2024-07-05 08:58 | 423840 | 8770 | 4.0014 | 5762 | 8770 | 0.17839 | 1564.4849 | 1.5645 | 2.7369 | 716 | 685 | 700.5 | 756 | 1389.881 | 1.3899 | 12.1893 | 2.1155 | 21.3238
| 2024-07-16 09:00 | 447680 | 16.5285 | 8.2438 | 235.3271 | 2024-07-12 08:56 | 439350 | 8330 | 4.0028 | 5764 | 8330 | 0.2601 | 2166.6278 | 2.1666 | 3.789 | 693 | 670 | 681.5 | 745 | 1372.1477 | 1.3721 | 11.43 | 1.983 | 19.9886
| 2024-07-23 08:55 | 462290 | 10.2731 | 6.2725 | 171.3575 | 2024-07-19 08:57 | 453990 | 8300 | 3.9986 | 5758 | 8300 | 0.1879 | 1559.5964 | 1.5596 | 2.7302 | 554 | 565 | 559.5 | 774 | 1084.3023 | 1.0843 | 8.9997 | 1.563 | 15.755
| 2024-07-30 08:59 | 468940 | 11.511 | 24.0139 | 76.107 | 2024-07-26 09:03 | 466400 | 2540 | 3.9972 | 5756 | 2540 | 0.11163 | 283.5449 | 0.28354 | 0.49655 | 227 | 251 | 239 | 785 | 456.6879 | 0.45669 | 1.16 | 0.20153 | 2.0314
| 2024-08-06 09:01 | 478910 | 20.741 | 0 | 249.74 | 2024-08-02 08:58 | 472990 | 5920 | 4.0021 | 5763 | 5920 | 0.27048 | 1601.2475 | 1.6012 | 2.8007 | 766 | 773 | 769.5 | 754 | 1530.8355 | 1.5308 | 9.0625 | 1.5725 | 15.8512
| 2024-08-13 08:58 | 487540 | 27.701 | 4.15 | 513.934 | 2024-08-09 09:06 | 482780 | 4760 | 3.9944 | 5752 | 4760 | 0.54578 | 2597.9366 | 2.5979 | 4.5527 | 978 | 1013 | 995.5 | 760 | 1964.8026 | 1.9648 | 9.3525 | 1.6259 | 16.3896
| 2024-08-20 08:55 | 501530 | 4.6343 | 13.8855 | 244.0861 | 2024-08-16 09:01 | 493350 | 8180 | 3.9958 | 5754 | 8180 | 0.26261 | 2148.1163 | 2.1481 | 3.7631 | 651 | 673 | 662 | 788 | 1260.1523 | 1.2602 | 10.308 | 1.7915 | 18.0579
| 2024-08-27 09:02 | 15780 | 10.2845 | 101.8912 | 144.6876 | 2024-08-23 08:55 | 7320 | 8460 | 4.0049 | 5767 | 8460 | 0.25686 | 2173.0637 | 2.1731 | 3.7982 | 756 | 776 | 766 | 764 | 1503.9267 | 1.5039 | 12.7232 | 2.2062 | 22.2386
| 2024-09-03 08:54 | 30300 | 4.292 | 14.765 | 261.906 | 2024-08-30 09:02 | 22250 | 8050 | 3.9944 | 5752 | 8050 | 0.28096 | 2261.7521 | 2.2618 | 3.9636 | 859 | 833 | 846 | 757 | 1676.354 | 1.6764 | 13.4946 | 2.3461 | 23.6485
| 2024-09-05 09:05 | 34450 | 22.1616 | 5.1601 | 283.886 | 2024-08-30 09:02 | 22250 | 12200 | 6.0021 | 8643 | 12200 | 0.31121 | 3796.7333 | 3.7967 | 4.428 | 850 | 869 | 859.5 | 756 | 1705.3571 | 1.7054 | 20.8054 | 2.4072 | 24.2645
| 2024-09-10 09:01 | 44940 | 7.9 | 15.957 | 233.767 | 2024-09-06 09:11 | 36460 | 8480 | 3.9931 | 5750 | 8480 | 0.25762 | 2184.6515 | 2.1847 | 3.8298 | 734 | 746 | 740 | 725 | 1531.0345 | 1.531 | 12.9832 | 2.2579 | 22.7601
| 2024-09-17 09:02 | 56270 | 4.7165 | 132.2701 | 84.5064 | 2024-09-13 09:00 | 50950 | 5320 | 4.0014 | 5762 | 5320 | 0.22149 | 1178.3433 | 1.1783 | 2.0614 | 697 | 695 | 696 | 751 | 1390.1465 | 1.3901 | 7.3956 | 1.2835 | 12.9378
| 2024-09-24 09:05 | 62730 | 7.966 | 161.9 | 194.21 | 2024-09-20 09:05 | 57830 | 4900 | 4 | 5760 | 4900 | 0.36408 | 1783.9724 | 1.784 | 3.122 | 833 | 810 | 821.5 | 780 | 1579.8077 | 1.5798 | 7.7411 | 1.3439 | 13.5469
[7 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | #DIV/0! |  |  | 0 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[7 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | #DIV/0! |  |  | 0 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[7 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | #DIV/0! |  |  | 0 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Add new rows above this line
[7 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | #DIV/0! |  |  | 0 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
A
Note on B213: Lab Sl3 - LGL: Sample date corresponds to when the SIRCO sampler was believed to have gone offline.
Note on B273: Lab Sl3 - LGL: sample contaminated with bleach from cleaning sampler.
Note on B519: Lab Sl3 - LGL: new sensor fitted
Note on B530: lfllab: following sensor change
Note on C286: Lab Sl3 - LGL: counter reset at 49990
Note on C330: Lab Sl3 - LGL: counter resets to 3500
Note on C423: Lab Sl3 - LGL: counter reset at 500K
Note on C473: Lab Sl3 - LGL: Reset at 500,000
Note on I226: Lab Sl3 - LGL: counterr reset at 499,990. 499900-496300=3690 3690+ 3850= 7540
Note on L226: Lab Sl3 - LGL: counterr reset at 499,990. 499900-496300=3690 3690+ 3850= 7540
Note on P212: Lab Sl3 - LGL: Changing to a new column for tomorrow's Friday effluent.

## SL3 Effluent results
LIMITS UPDATED 06/01/04 DUE TO IPC VARIATION
LIMITS UPDATED 23/11/06 DUE TO CHANGE TO PPC PERMIT
ENVIRONMENTAL TESTING OF LYOCELL EFFLUENT - SL3 | [20 empty] | Max | 27122.7575 | 24868.8125 | 80045.25 | 213595.1559
[21 empty] | Min | 9988.6875 | 12200.4037 | 11508.97 | 61574.2497
[21 empty] | Average | 18795.7285 | 18794.23 | 44911.0172 | 134773.0912
SAMPLE DATE | Sampled Time | NUMBER OF SAMPLES | TOTAL FLOW (m3) | WEEKLY FLOW (m3) | pH | TOTAL SUSPENDED SOLIDS (mg/l) | PeCOD COD (mg/l) | COD (mg/l) | COD (Kg/ week) | FREE CHLORINE | Phosphates as P (mg/l) | NMMO (mg/l) | NMM (mg/l) | M (mg/l) | TOTAL AMINES (mg/l) | TOTAL AMINES (Kg / week) | VISIBLE OIL IN SAMPLE (Y / N) | NITROGEN (Kg/week) | RO UNIT PERMEATE TOTAL AMINES (mg/L) | [6 empty] | TOTAL AMINES (Kg / week) LIMIT | COD (Kg/ week) | TOTAL SUSPENDED SOLIDS (mg/l) | pH (LCL) | pH (UCL) | WEEKLY FLOW (m3)
IPC limits |  |  |  | Limit 42,000 m3/wk | Limit 5 -10 | Limit 50 mg/l |  |  | Limit 45,500 Kg/week | Limit 50 mg/l | [5 empty] | Limit 10,500 Kg/week | Limit - N |  |  |  |  | 120000 | 360000
EPR / PPC limits |  |  |  | Limit 35,000 m3/wk | Limit 6 -10 | Limit 100 mg/l |  |  | Limit 30,000 Kg/week |  | No limit |  |  |  |  | Limit 8,000 Kg/week | Limit - N |  |  |  |  | 1 month ave COD | 3 month ave COD | 1 mth total COD remain | 3 mth total COD remain
2003-01-03 |  | 305 | 58663 | 16822 | 7.4 | 31.2 |  | 715 | 12027.73 | 0.2 |  | 132 | 71 | 68 | 271 | 4558.762 | N | 615.3317 | [7 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-01-10 |  | 316 | 76456 | 17793 | 7.21 | 21.6 |  | 671 | 11939.103 | 0.2 |  | 83 | 79 | 0 | 162 | 2882.466 | N | 371.5555 | [7 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-01-17 |  | 338 | 95555 | 19099 | 8.04 | 28 |  | 770 | 14706.23 | 0.2 |  | 108 | 61 | 52 | 221 | 4220.879 | N | 568.1253 | [7 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-01-24 |  | 366 | 116118 | 20563 | 7.92 | 44.4 |  | 732 | 15052.116 | 0.4 |  | 84 | 56 | 48 | 188 | 3865.844 | N | 525.1337 | [7 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-01-31 |  | 345 | 135684 | 19566 | 7.2 | 42 |  | 702 | 13735.332 | 0.3 |  | 100 | 84 | 53 | 237 | 4637.142 | N | 628.8143 |  |  |  | 13858.1953 |  | 64567.219 |  | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-02-07 |  | 356 | 156262 | 20578 | 7.93 | 46.4 |  | 1001 | 20598.578 | 0.3 |  | 175 | 62 | 18 | 255 | 5247.39 | N | 667.3606 |  |  |  | 16023.064 |  | 55907.744 |  | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-02-14 |  | 310 | 173586 | 17324 | 7.64 | 42.4 |  | 782 | 13547.368 | 0 |  | 100 | 74 | 44 | 218 | 3776.632 | N | 507.6573 |  |  |  | 15733.3485 |  | 57066.606 |  | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-02-21 |  | 342 | 193278 | 19692 | 7.8 | 38.4 |  | 844 | 16620.048 | 0.4 |  | 72 | 51 | 44 | 167 | 3288.564 | N | 448.2914 |  |  |  | 16125.3315 |  | 55498.674 |  | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-02-28 |  | 379 | 214766 | 21488 | 7.69 | 34.4 |  | 837 | 17985.456 | 0.3 |  | 95 | 63 | 48 | 206 | 4426.528 | N | 597.8893 |  |  |  | 17187.8625 |  | 51248.55 |  | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-03-07 |  | 293 | 230901 | 16135 | 7.09 | 33.6 |  | 776 | 12520.76 | 2.6 |  | 72 | 94 | 81 | 247 | 3985.345 | N | 559.5549 |  |  |  | 15168.408 |  | 59326.368 |  | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-03-14 |  | 292 | 247678 | 16777 | 7.7 | 55.6 |  | 709 | 11894.893 | 0.4 |  | 11 | 113 | 54 | 178 | 2986.306 | N | 430.6532 |  |  |  | 14755.2892 |  | 60978.843 |  | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-03-21 |  | 334 | 267252 | 19574 | 7.51 | 39.6 |  | 917 | 17949.358 | 0 |  | 120 | 86 | 2 | 208 | 4071.392 | N | 520.6998 |  |  |  | 15087.6167 |  | 59649.533 |  | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-03-28 |  | 362 | 290194 | 22942 | 6.69 | 40 |  | 735 | 16862.37 | 0.1 |  | 53 | 61 | 14 | 128 | 2936.576 | N | 391.1657 |  |  |  | 14806.8453 | 15284.301 | 60772.619 | 176588.388 | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-04-04 |  | 367 | 313329 | 23135 | 8.03 | 31.2 |  | 800 | 18508 | 0.7 |  | 74 | 55 | 6 | 135 | 3123.225 | N | 403.5665 |  |  |  | 16303.6552 | 15831.7091 | 54785.379 | 170019.491 | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-04-11 |  | 264 | 329065 | 15736 | 7.51 | 37.2 |  | 713 | 11219.768 | 0 |  | 85 | 49 | 6 | 140 | 2203.04 | N | 282.1235 |  |  |  | 16134.874 | 15541.1706 | 55460.504 | 173505.953 | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-04-18 |  | 310 | 345260 | 16195 | 7.62 | 56.4 |  | 864 | 13992.48 | 0 |  | 134 | 66 | 12 | 212 | 3433.34 | N | 439.107 |  |  |  | 15145.6545 | 15452.8676 | 59417.382 | 174565.589 | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-04-25 |  | 315 | 363183 | 17923 | 7.43 | 36.8 |  | 684 | 12259.332 | 0.2 |  | 39 | 91 | 8 | 138 | 2473.374 | N | 332.7922 |  |  |  | 13994.895 | 15329.8676 | 64020.42 | 176041.589 | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-05-02 |  | 371 | 384742 | 21559 | 7.59 | 38.8 |  | 774 | 16686.666 | 0.4 |  | 79 | 71 | 0 | 150 | 3233.85 | N | 415.9718 |  |  |  | 13539.5615 | 15003.8749 | 65841.754 | 179953.501 | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-05-09 |  | 371 | 406714 | 21972 | 7.62 | 63.2 |  | 852 | 18720.144 | 0.2 |  | 86 | 82 | 0 | 168 | 3691.296 | N | 475.8462 |  |  |  | 15414.6555 | 15434.9396 | 58341.378 | 174780.725 | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-05-16 |  | 349 | 427843 | 21129 | 7.67 | 60 |  | 774 | 16353.846 | 0.1 |  | 41 | 82 | 4 | 127 | 2683.383 | N | 357.4181 |  |  |  | 16004.997 | 15412.7561 | 55980.012 | 175046.927 | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-05-23 |  | 721 | 450207 | 22364 | 6.99 | 48 |  | 811 | 18137.204 | 0.5 |  | 45 | 75 | 0 | 120 | 2683.68 | N | 352.9186 |  |  |  | 17474.465 | 15425.4018 | 50102.14 | 174895.179 | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-05-30 |  | 421 | 474913 | 24706 | 7.23 | 40 |  | 694 | 17145.964 | 0.2 |  | 51 | 89 | 4 | 144 | 3557.664 | N | 471.4615 |  |  |  | 17589.2895 | 15810.8354 | 49642.842 | 170269.975 | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-06-06 |  | 361 | 495730 | 20817 | 7.47 | 62.8 |  | 810 | 16861.77 | 0.2 |  | 83 | 95 | 4 | 182 | 3788.694 | N | 494.2709 |  |  |  | 17124.696 | 16224.7418 | 51501.216 | 165303.098 | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-06-13 |  | 331 | 13724 | 17992 | 7.55 | 57 |  | 1101 | 19809.192 | 0.4 |  | 41 | 124 | 5 | 170 | 3058.64 | N | 411.9934 |  |  |  | 17988.5325 | 16379.728 | 48045.87 | 163443.264 | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-06-20 |  | 380 | 34360 | 20636 | 7.76 | 63.2 |  | 806 | 16632.616 | 0.6 |  | 6 | 80 | 0 | 86 | 1774.696 | N | 243.6504 |  |  |  | 17612.3855 | 16360.5818 | 49550.458 | 163673.018 | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-06-27 |  | 399 | 56030 | 21670 | 7.65 | 59.2 |  | 737 | 15970.79 | 0 |  | 12 | 93 | 2 | 107 | 2318.69 | n | 317.4401 |  |  |  | 17318.592 | 16149.1477 | 50725.632 | 166210.228 | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-07-04 |  | 423 | 79319 | 23289 | 7.57 | 57.6 |  | 677 | 15766.653 | 0.4 |  | 39 | 33 | 1 | 73 | 1700.097 | n | 218.9595 |  |  |  | 17044.8128 | 16528.0547 | 51820.749 | 161663.343 | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-07-11 |  | 410 | 101698 | 22379 | 7.55 | 69.6 |  | 770 | 17231.83 | 0.1 |  | 22 | 28 | 0 | 50 | 1118.95 | n | 145.7693 |  |  |  | 16400.4722 | 16798.0006 | 54398.111 | 158423.993 | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-07-18 |  | 390 | 123051 | 21353 | 7.65 | 44.8 |  | 719 | 15352.807 | 0.5 |  | 62 | 68 | 0 | 130 | 2775.89 | n | 359.6816 |  |  |  | 16080.52 | 17055.7902 | 55677.92 | 155330.518 | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-07-25 |  | 390 | 145074 | 22023 | 7.73 | 62 |  | 668 | 14711.364 | 0.3 |  | 25 | 81 | 0 | 106 | 2334.438 | N | 313.1489 |  |  |  | 15765.6635 | 16891.1817 | 56937.346 | 157305.82 | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-08-01 |  | 435 | 170565 | 25491 | 7.41 | 66.4 |  | 718 | 18302.538 | 0.2 |  | 32 | 134 | 0 | 166 | 4231.506 | N | 571.083 |  |  |  | 16399.6348 | 16856.3812 | 54401.461 | 157723.426 | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-08-08 |  | 406 | 193402 | 22837 | 7.66 | 68 |  | 808 | 18452.296 | 0.8 |  | 116 | 0 | 0 | 116 | 2649.092 | N | 316.9854 |  |  |  | 16704.7513 | 17031.252 | 53180.995 | 155624.976 | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-08-15 |  | 388 | 214616 | 21214 | 7.58 | 71.6 |  | 831 | 17628.834 | 0 |  | 0 | 138 | 0 | 138 | 2927.532 | n | 405.7965 |  |  |  | 17273.758 | 16988.8878 | 50904.968 | 156133.346 | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-08-22 |  | 387 | 236503 | 21887 | 7.77 | 64.8 |  | 910 | 19917.17 | 0.4 |  | 166 | 0 | 0 | 166 | 3633.242 | n | 434.7469 |  |  |  | 18575.2095 | 17219.8217 | 45699.162 | 153362.14 | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-08-29 |  | 378 | 259335 | 22832 | 7.85 | 64 |  | 829 | 18927.728 | 0.1 |  | 116 | 0 | 0 | 116 | 2648.512 | n | 316.916 |  |  |  | 18731.507 | 17391.9848 | 45073.972 | 151296.182 | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-09-05 |  | 361 | 282879 | 23544 | 7.85 | 38 |  | 856 | 20153.664 | 0.9 |  | 96 | 72 | 64 | 232 | 5462.208 | n | 747.9041 |  |  |  | 19156.849 | 17420.6908 | 43372.604 | 150951.71 | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-09-12 |  | 357 | 305302 | 22423 | 7.39 | 38.8 |  | 657 | 14731.911 | 0.9 |  | 59 | 82 | 74 | 215 | 4820.945 | N | 680.184 |  |  |  | 18432.6182 | 17262.2988 | 46269.527 | 152852.415 | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-09-19 |  | 335 | 325896 | 20594 | 7.63 | 73.6 |  | 901 | 18555.194 | 0 |  | 72 | 131 | 61 | 264 | 5436.816 | N | 753.5322 |  |  |  | 18092.1243 | 17477.6658 | 47631.503 | 150268.011 | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-09-26 |  | 367 | 347547 | 21651 | 7.42 | 46.4 |  | 834 | 18056.934 | 0.1 |  | 79 | 109 | 77 | 265 | 5737.515 | N | 800.0631 |  |  |  | 17874.4257 | 17668.5225 | 48502.297 | 147977.73 | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-10-03 |  | 87 | 370722 | 23175 | 7.52 | 52.8 |  | 857 | 19860.975 | 0.1 |  | 108 | 84 | 73 | 265 | 6141.375 | N | 841.5716 |  |  |  | 17801.2535 | 17887.6179 | 48794.986 | 145348.585 | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-10-10 |  | 398 | 391695 | 20973 | 7.4 | 34.8 |  | 807 | 16925.211 | 0.4 |  | 80 | 0 | 0 | 80 | 1677.84 | N | 200.7672 |  |  |  | 18349.5785 | 18018.6516 | 46601.686 | 143776.181 | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-10-17 |  | 201 | 414409 | 22714 | 7.42 | 49.6 |  | 832 | 18898.048 | 0.4 |  | 126 | 69 | 0 | 195 | 4429.23 | N | 559.702 |  |  |  | 18435.292 | 18367.5419 | 46258.832 | 139589.497 | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-10-24 |  | 407 | 435866 | 21457 | 6.89 | 17.2 |  | 669 | 14354.733 | 0 |  | 77 | 40 | 0 | 117 | 2510.469 | N | 316.6673 |  |  |  | 17509.7418 | 18038.5582 | 49961.033 | 143537.302 | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-10-31 |  | 482 | 455722 | 19856 | 7.49 | 22.4 |  | 522 | 10364.832 | 0.2 |  | 68 | 22 | 0 | 90 | 1787.04 | N | 222.1143 |  |  |  | 15135.706 | 17364.6028 | 59457.176 | 151624.766 | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-11-07 |  | 440 | 472816 | 17094 | 7.2 | 32.4 |  | 832 | 14222.208 | 0.2 |  | 66 | 44 | 0 | 110 | 1880.34 | N | 239.2552 |  |  |  | 14459.9553 | 17080.7173 | 62160.179 | 155031.392 | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-11-14 |  | 401 | 492649 | 19833 | 7.29 | 35.6 |  | 838 | 16620.054 | 0.1 |  | 113 | 57 | 0 | 170 | 3371.61 | N | 424.8696 |  |  |  | 13890.4567 | 16805.9577 | 64438.173 | 158328.508 | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-11-21 |  | 411 | 11151 | 18499 | 7.38 | 43.2 |  | 991 | 18332.509 | 0.2 |  | 91.6 | 61.1 | 0 | 152.7 | 2824.7973 | N | 359.4354 |  |  |  | 14884.9008 | 16756.3561 | 60460.397 | 158923.727 | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-11-28 |  | 403 | 31071 | 19920 | 7.22 | 22.8 |  | 795 | 15836.4 | 0.2 |  | 109 | 52 | 0 | 161 | 3207.12 | N | 403.3931 |  |  |  | 16252.7928 | 16396.5841 | 54988.829 | 163240.991 | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-12-05 |  | 216 | 52111 | 21040 | 7 | 22.8 |  | 886 | 18641.44 | 0.2 |  | 132 | 74 | 0 | 206 | 4334.24 | N | 548.1403 |  |  |  | 17357.6008 | 16722.3782 | 50569.597 | 159331.462 | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-12-12 |  | 209 | 72904 | 20793 | 7.07 | 32.8 |  | 953 | 19815.729 | 0.5 |  | 126 | 72 | 0 | 198 | 4117.014 | N | 521.0127 |  |  |  | 18156.5195 | 16827.4228 | 47373.922 | 158070.927 | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-12-19 |  | 415 | 93320 | 20416 | 7.21 | 33.2 |  | 872 | 17802.752 | 0 |  | 107 | 66 | 25 | 198 | 4042.368 | N | 530.304 |  |  |  | 18024.0802 | 16806.2409 | 47903.679 | 158325.109 | 8000 | 30000 | 100 | 6 | 10 | 35000
2003-12-26 |  | 179 | 110562 | 17242 | 7.43 | 34.4 |  | 923 | 15914.366 | 0 |  | 52 | 64 | 29 | 145 | 2500.09 | N | 340.705 |  |  |  | 18043.5717 | 16477.3568 | 47825.713 | 162271.718 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-01-02 |  | 168 | 126595 | 16033 | 7.36 | 30.4 |  | 860 | 13788.38 | 0 |  | 56.488 | 61.0613 | 31.727 | 149.2763 | 2393.3469 | N | 325.9298 |  |  |  | 16830.3067 | 16215.9543 | 52678.773 | 165408.549 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-01-09 |  | 169 | 143960 | 17365 | 7.08 | 24.4 |  | 895 | 15541.675 | 1 |  | 114 | 53 | 55 | 222 | 3855.03 | N | 518.1392 |  |  |  | 15761.7933 | 15936.2565 | 56952.827 | 168764.922 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-01-16 |  | 209 | 165966 | 22006 | 7.3 | 24.8 |  | 665 | 14633.99 | 0 |  | 125 | 48 | 0 | 173 | 3807.038 | N | 475.5657 |  |  |  | 14969.6028 | 15959.5279 | 60121.589 | 168485.665 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-01-23 |  | 187 | 185415 | 19449 | 7.34 | 8.4 |  | 963 | 18729.387 | 0 |  | 139 | 53 | 108 | 300 | 5834.7 | N | 804.378 |  |  |  | 15673.358 | 16656.5742 | 57306.568 | 160121.11 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-01-30 |  | 156 | 201800 | 16385 | 7.23 | 18.8 |  | 1113 | 18236.505 | 0.5 |  | 141 | 56 | 83 | 280 | 4587.8 | N | 622.4742 |  |  |  | 16785.3893 | 16991.0989 | 52858.443 | 156106.813 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-02-06 |  | 197 | 222522 | 20722 | 7.21 | 34 |  | 905 | 18753.41 | 0 |  | 135 | 53 | 78 | 266 | 5512.052 | N | 747.0717 |  |  |  | 17588.323 | 17168.8786 | 49646.708 | 153973.457 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-02-13 |  | 179 | 241051 | 18529 | 7.3 | 24.4 |  | 1082 | 20048.378 | 0 |  | 196 | 56 | 21 | 273 | 5058.417 | n | 641.0048 |  |  |  | 18941.92 | 17311.8677 | 44232.32 | 152257.588 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-02-20 |  | 155 | 257169 | 16118 | 7.23 | 26 |  | 1028 | 16569.304 | 0 |  | 120 | 55 | 80 | 255 | 4110.09 | n | 561.8138 |  |  |  | 18401.8992 | 17372.943 | 46392.403 | 151524.684 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-02-27 |  | 199 | 278597 | 21428 | 7.3 | 30 |  | 954 | 20442.312 | 1 |  | 119.7 | 18.5 | 63.8 | 202 | 4328.456 | N | 581.8581 |  |  |  | 18953.351 | 17523.0157 | 44186.596 | 149723.812 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-03-05 |  | 210 | 300816 | 22219 | 7.27 | 13.6 |  | 945 | 20996.955 | 0 |  | 116.57 | 18.467 | 0 | 135.037 | 3000.3871 | N | 366.7986 |  |  |  | 19514.2372 | 17621.4512 | 41943.051 | 148542.586 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-03-12 |  | 193 | 321078 | 20262 | 7.28 | 27.6 |  | 951 | 19269.162 | 0.5 |  | 159 | 51 | 96 | 306 | 6200.172 | N | 841.7488 |  |  |  | 19319.4332 | 17743.652 | 42722.267 | 147076.176 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-03-19 |  | 205 | 342509 | 21431 | 7.21 | 31.2 |  | 1049 | 22481.119 | 0.5 |  | 146.8465 | 47.5697 | 71 | 265.4162 | 5688.1346 | N | 762.7396 |  |  |  | 20797.387 | 18290.8814 | 36810.452 | 140509.423 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-03-26 |  | 168 | 359905 | 17396 | 7.36 | 34.8 |  | 932 | 16213.072 | 0.5 |  | 212 | 70 | 83 | 365 | 6349.54 | N | 842.4328 |  |  |  | 19740.077 | 18492.9391 | 41039.692 | 138084.731 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-04-02 |  | 161 | 376880 | 16975 | 7.23 | 68 |  | 1008 | 17110.8 | 0 |  | 176 | 97 | 84 | 357 | 6060.075 | N | 815.1839 |  |  |  | 18768.5383 | 18623.6995 | 44925.847 | 136515.606 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-04-09 |  | 167 | 394841 | 17961 | 7.33 | 40 |  | 1078 | 19361.958 | 0.5 |  | 93 | 131 | 56 | 280 | 5029.08 | N | 687.8724 |  |  |  | 18791.7372 | 19017.6968 | 44833.051 | 131787.638 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-04-16 |  | 190 | 415124 | 20283 | 7.54 | 33.6 |  | 1003 | 20343.849 | 1.5 |  | 93 | 114 | 47 | 254 | 5151.882 | N | 699.6297 |  |  |  | 18257.4198 | 19152.2353 | 46970.321 | 130173.176 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-04-23 |  | 171 | 433279 | 18155 | 7.13 | 30.8 |  | 970 | 17610.35 | 0.5 |  | 99 | 64 | 71 | 234 | 4248.27 | N | 583.5512 |  |  |  | 18606.7392 | 19100.0557 | 45573.043 | 130799.331 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-04-30 |  | 179 | 452429 | 19150 | 7.17 | 42.8 |  | 980 | 18767 | 1 |  | 124 | 57 | 60 | 241 | 4615.15 | N | 620.3407 |  |  |  | 19020.7893 | 19101.1882 | 43916.843 | 130785.741 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-05-07 |  | 193 | 472693 | 20264 | 7.4 | 40.8 |  | 937 | 18987.368 | 0.5 |  | 109.4 | 63.3 | 0 | 172.7 | 3499.5928 | N | 443.0694 |  |  |  | 18927.1417 | 19012.7707 | 44291.433 | 131846.751 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-05-14 |  | 176 | 490892 | 18199 | 7.38 | 47.6 |  | 973 | 17707.627 | 0 |  | 124 | 68 | 53 | 245 | 4458.755 | n | 596.7832 |  |  |  | 18268.0863 | 19107.631 | 46927.655 | 130708.428 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-05-21 |  | 191 | 10265 | 19373 | 7.3 | 50 |  | 987 | 19121.151 | 1 |  | 106 | 88 | 0 | 194 | 3758.362 | n | 482.0347 |  |  |  | 18645.7865 | 18997.5343 | 45416.854 | 132029.589 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-05-28 |  | 200 | 30143 | 19878 | 7.3 | 29.6 |  | 1001 | 19897.878 | 1 |  | 127 | 81 | 0 | 208 | 4134.624 | n | 525.2623 |  |  |  | 18928.506 | 18905.9445 | 44285.976 | 133128.666 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-06-04 |  | 186 | 48522 | 18379 | 7.38 | 44 |  | 1163 | 21374.777 | 0.5 |  | 6 | 207 | 8 | 221 | 4061.759 | n | 564.2054 |  |  |  | 19525.3583 | 19081.4124 | 41898.567 | 131023.051 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-06-11 |  | 185 | 66858 | 18336 | 7.26 | 30.4 |  | 1071 | 19637.856 | 0.5 |  | 33 | 163 | 0 | 196 | 3593.856 | N | 486.6884 |  |  |  | 20007.9155 | 18844.4738 | 39968.338 | 133866.314 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-06-18 |  | 204 | 86775 | 19917 | 7.25 | 34.8 |  | 765 | 15236.505 | 0 |  | 18 | 136 | 61 | 215 | 4282.155 | N | 613.8703 |  |  |  | 19036.754 | 18763.0933 | 43852.984 | 134842.881 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-06-25 |  | 185 | 106332 | 19557 | 7.13 | 24 |  | 985 | 19263.645 | 1 |  | 133 | 10 | 61 | 204 | 3989.628 | n | 530.3225 |  |  |  | 18878.1957 | 18942.497 | 44487.217 | 132690.036 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-07-02 |  | 171 | 122319 | 15987 | 7.6 | 48.4 |  | 1228 | 19632.036 | 0.5 |  | 48 | 113 | 65 | 226 | 3613.062 | n | 509.4534 |  |  |  | 18442.5105 | 18965.0035 | 46229.958 | 132419.958 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-07-09 |  | 166 | 139245 | 16926 | 7.19 | 22.4 |  | 1013 | 17146.038 | 0 |  | 67 | 80 | 48 | 195 | 3300.57 | n | 454.1303 |  |  |  | 17819.556 | 18698.5193 | 48721.776 | 135617.769 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-07-16 |  | 193 | 158648 | 19403 | 7.32 | 20.8 |  | 979 | 18995.537 | 1 |  | 80 | 83 | 58 | 221 | 4288.063 | n | 590.0633 |  |  |  | 18759.314 | 18813.9515 | 44962.744 | 134232.582 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-07-23 |  | 201 | 179084 | 20436 | 7.25 | 33.2 |  | 982 | 20068.152 | 0.5 |  | 74 | 65 | 52 | 191 | 3903.276 | N | 536.0857 |  |  |  | 18960.4408 | 18922.3808 | 44158.237 | 132931.43 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-07-30 |  | 203 | 199766 | 20682 | 7.41 | 11.3 |  | 1004 | 20764.728 | 0 |  | 75 | 92 | 50 | 217 | 4487.994 | N | 615.7613 |  |  |  | 19243.6138 | 19070.4942 | 43025.545 | 131154.07 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-08-06 |  | 156 | 215482 | 15716 | 7.34 | 16 |  | 847 | 13311.452 | 1 |  | 88 | 51 | 0 | 139 | 2184.524 | N | 276.5894 |  |  |  | 18284.9673 | 18704.1463 | 46860.131 | 135550.245 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-08-13 |  | 213 | 236546 | 21064 | 7.26 | 32.4 |  | 839 | 17672.696 | 0.5 |  | 70 | 75 | 12 | 157 | 3307.048 | N | 436.091 |  |  |  | 17954.257 | 18583.4417 | 48182.972 | 136998.7 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-08-20 |  | 185 | 254815 | 18269 | 7.48 | 37.2 |  | 972 | 17757.468 | 1 |  | 27 | 89 | 70 | 186 | 3398.034 | n | 490.1896 |  |  |  | 17376.586 | 18405.0742 | 50493.656 | 139139.11 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-08-27 |  | 187 | 274761 | 19946 | 7.36 | 25.2 |  | 855 | 17053.83 | 0 |  | 62 | 69 | 64 | 195 | 3889.47 | n | 544.167 |  |  |  | 16448.8615 | 18044.9952 | 54204.554 | 143460.057 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-09-03 |  | 200 | 295829 | 21068 | 7.41 | 27.2 |  | 878 | 18497.704 | 0 |  | 40 | 88 | 52 | 180 | 3792.24 | n | 534.1193 |  |  |  | 17745.4245 | 17949.9826 | 49018.302 | 144600.209 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-09-10 |  | 209 | 317502 | 21673 | 7.19 | 34 |  | 859 | 18617.107 | 0 |  | 0 | 108 | 58 | 166 | 3597.718 | n | 526.7326 |  |  |  | 17981.5272 | 18231.6994 | 48073.891 | 141219.607 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-09-17 |  | 163 | 334141 | 16639 | 7.34 | 57.2 |  | 906 | 15074.934 | 1 |  | 0 | 116 | 67 | 183 | 3044.937 | N | 446.9371 |  |  |  | 17310.8937 | 17882.6402 | 50756.425 | 145408.318 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-09-24 |  | 207 | 355399 | 21258 | 7.26 | 28.8 |  | 866 | 18409.428 | 1 |  | 31 | 88 | 46 | 165 | 3507.57 | n | 495.518 |  |  |  | 17649.7932 | 17780.7562 | 49400.827 | 146630.926 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-10-01 |  | 167 | 372559 | 17160 | 7.61 | 40 |  | 954 | 16370.64 | 1 |  | 69 | 43 | 48 | 160 | 2745.6 | n | 376.5066 |  |  |  | 17118.0272 | 17716.1397 | 51527.891 | 147406.324 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-10-08 |  | 167 | 389699 | 17140 | 7.52 | 40.8 |  | 844 | 14466.16 | 0.5 |  | 63 | 72 | 53 | 188 | 3222.32 | n | 446.4524 |  |  |  | 16080.2905 | 17338.6916 | 55678.838 | 151935.701 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-10-15 |  | 182 | 408060 | 18361 | 7.29 | 39.6 |  | 895 | 16433.095 | 1.5 |  | 87 | 48 | 54 | 189 | 3470.229 | n | 472.8578 |  |  |  | 16419.8308 | 17035.7702 | 54320.677 | 155570.758 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-10-22 |  | 207 | 429345 | 21285 | 7.51 | 29.6 |  | 818 | 17411.13 | 0.5 |  | 85 | 53 | 45 | 183 | 3895.155 | N | 526.9922 |  |  |  | 16170.2563 | 16756.3037 | 55318.975 | 158924.356 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-10-29 |  | 176 | 447369 | 18024 | 7.38 | 45.2 |  | 992 | 17879.808 | 0.5 |  | 36 | 65 | 36 | 137 | 2469.288 | n | 344.4512 |  |  |  | 16547.5482 | 17137 | 53809.807 | 154356 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-11-05 |  | 172 | 464817 | 17448 | 7.46 | 36.4 |  | 1072 | 18704.256 | 0.5 |  | 61 | 71 | 3 | 135 | 2355.48 | n | 307.4946 |  |  |  | 17607.0723 | 17222.9633 | 49571.711 | 153324.44 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-11-12 |  | 203 | 486354 | 21537 | 7.34 | 26.8 |  | 827 | 17811.099 | 0 |  | 78 | 61 | 52 | 191 | 4113.567 | N | 563.3346 |  |  |  | 17951.5733 | 17227.4326 | 48193.707 | 153270.809 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-11-19 |  |  | 4158 | 17801 | 6.88 | 29.2 |  | 911 | 16216.711 | 0.5 |  | 120 | 54 | 58 | 232 | 4129.832 | N | 554.9899 |  |  |  | 17652.9685 | 17157.6727 | 49388.126 | 154107.928 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-11-26 |  | 145 | 18522 | 14364 | 6.71 | 30.8 |  | 934 | 13415.976 | 0 |  | 76 | 59 | 53 | 188 | 2700.432 | n | 370.6051 |  |  |  | 16537.0105 | 16734.1953 | 53851.958 | 159189.656 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-12-03 |  | 162 | 34610 | 16088 | 6.9 | 11.6 |  | 824 | 13256.512 | 0.5 |  | 96 | 44 | 63 | 203 | 3265.864 | n | 446.0256 |  |  |  | 15175.0745 | 16287.4791 | 59299.702 | 164550.251 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-12-10 |  | 193 | 53704 | 19094 | 7.2 | 21.2 |  | 955 | 18234.77 | 0.5 |  | 61 | 37 | 41 | 139 | 2654.066 | n | 363.274 |  |  |  | 15280.9922 | 16550.7988 | 58876.031 | 161390.415 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-12-17 |  | 188 | 72399 | 18695 | 7.5 | 27.2 |  | 973 | 18190.235 | 1 |  | 36 | 52 | 38 | 126 | 2355.57 | n | 329.6032 |  |  |  | 15774.3733 | 16532.5327 | 56902.507 | 161609.608 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-12-24 |  | 175 | 90064 | 17665 | 7.4 | 33.6 |  | 1043 | 18424.595 | 0 |  | 109 | 65 | 55 | 229 | 4045.285 | n | 545.9052 |  |  |  | 17026.528 | 16703.6956 | 51893.888 | 159555.653 | 8000 | 30000 | 100 | 6 | 10 | 35000
2004-12-31 |  | 172 | 106888 | 16824 | 7.8 | 34.4 |  | 1040 | 17496.96 | 0.5 |  | 67 | 74 | 56 | 197 | 3314.328 | n | 459.0599 |  |  |  | 18086.64 | 16956.2622 | 47653.44 | 156524.853 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-01-07 |  | 187 | 125004 | 18116 | 7.4 | 25.2 |  | 1038 | 18804.408 | 1 |  | 50 | 81 | 122 | 253 | 4583.348 | n | 667.4444 |  |  |  | 18229.0495 | 17153.8717 | 47083.802 | 154153.54 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-01-14 |  | 166 | 140642 | 15638 | 7.5 | 30 |  | 909 | 14214.942 | 0.5 |  | 87 | 92 | 62 | 241 | 3768.758 | N | 518.2393 |  |  |  | 17235.2262 | 16887.5227 | 51059.095 | 157349.728 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-01-21 |  | 157 | 155117 | 14475 | 7 | 29.6 |  | 903 | 13070.925 | 0 |  | 110 | 70 | 84 | 264 | 3821.4 | n | 526.6382 |  |  |  | 15896.8088 | 16486.7824 | 56412.765 | 162158.611 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-01-28 |  | 185 | 172291 | 17174 | 7.25 | 20.8 |  | 717 | 12313.758 | 1 |  | 105 | 65 | 51 | 221 | 3795.454 | n | 511.4572 |  |  |  | 14601.0083 | 15954.2409 | 61595.967 | 168549.109 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-02-04 |  | 158 | 187516 | 15225 | 7.39 | 41.6 |  | 1285 | 19564.125 | 0 |  | 239 | 157 | 8 | 404 | 6150.9 | n | 786.3412 |  |  |  | 14790.9375 | 16100.3264 | 60836.25 | 166796.083 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-02-11 |  | 166 | 203746 | 16230 | 7.3 | 32.8 |  | 968 | 15710.64 | 1.5 |  | 148 | 150 | 12 | 310 | 5031.3 | n | 656.2197 |  |  |  | 15164.862 | 16058.1538 | 59340.552 | 167302.154 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-02-18 |  | 185 | 220746 | 17000 | 7.22 | 27.2 |  | 1099 | 18683 | 0.5 |  | 102 | 68 | 34 | 204 | 3468 | n | 460.7363 |  |  |  | 16567.8808 | 16497.0725 | 53728.477 | 162035.13 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-02-25 |  | 177 | 237070 | 16324 | 7.2 | 47.6 |  | 906 | 14789.544 | 0 |  | 69 | 66 | 53 | 188 | 3068.912 | N | 423.3411 |  |  |  | 17186.8272 | 16624.8252 | 51252.691 | 160502.098 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-03-04 |  | 200 | 256781 | 19711 | 7.3 | 25.6 |  | 999 | 19691.289 | 0.5 |  | 75 | 58 | 53 | 186 | 3666.246 | n | 503.4721 |  |  |  | 17218.6182 | 16746.2018 | 51125.527 | 159045.579 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-03-11 |  | 189 | 277357 | 20576 | 7.3 | 14 |  | 971 | 19979.296 | 1 |  | 55 | 79 | 21 | 155 | 3189.28 | n | 430.2648 |  |  |  | 18285.7823 | 16895.2902 | 46856.871 | 157256.518 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-03-18 |  | 187 | 298699 | 21342 | 7.3 | 34 |  | 1035 | 22088.97 | 0 |  | 70 | 124 | 33 | 227 | 4844.634 | n | 658.9243 |  |  |  | 19137.2748 | 17200.6548 | 43450.901 | 153592.143 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-03-25 |  | 155 | 316264 | 17565 | 7.16 | 34.8 |  | 872 | 15316.68 | 0 |  | 45 | 182 | 4 | 231 | 4057.515 | n | 549.0119 |  |  |  | 19269.0588 | 17018.9647 | 42923.765 | 155772.423 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-04-01 |  | 163 | 334984 | 18720 | 6.95 | 31.2 |  | 899 | 16829.28 | 3 |  | 120 | 155 | 6 | 281 | 5260.32 | n | 689.0765 |  |  |  | 18553.5565 | 16854.3707 | 45785.774 | 157747.551 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-04-08 |  | 149 | 352071 | 17087 | 7.13 | 56.8 |  | 800 | 13669.6 | 0.5 |  | 44 | 183 | 65 | 292 | 4989.404 | n | 702.123 |  |  |  | 16976.1325 | 16808.9256 | 52095.47 | 158292.893 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-04-15 |  | 169 | 371576 | 19505 | 7.11 | 37.2 |  | 770 | 15018.85 | 0.5 |  | 7 | 144 | 61 | 212 | 4135.06 | n | 597.1279 |  |  |  | 15208.6025 | 16971.2527 | 59165.59 | 156344.968 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-04-22 |  | 191 | 393233 | 21657 | 7.59 | 32.4 |  | 849 | 18386.793 | 1 |  | 19 | 136 | 65 | 220 | 4764.54 | n | 684.0311 |  |  |  | 15976.1308 | 17477.3389 | 56095.477 | 150271.933 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-04-29 |  | 171 | 412902 | 19669 | 7.14 | 55.6 |  | 908 | 17859.452 | 0.5 |  | 4 | 143 | 64 | 211 | 4150.159 | n | 601.8569 |  |  |  | 16233.6737 | 17335.2828 | 55065.305 | 151976.606 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-05-06 |  | 162 | 431836 | 18934 | 7.22 | 60.4 |  | 961 | 18195.574 | 0.5 |  | 21 | 135 | 95 | 251 | 4752.434 | n | 691.3381 |  |  |  | 17365.1672 | 17542.3607 | 50539.331 | 149491.672 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-05-13 |  | 170 | 451846 | 20010 | 7.57 | 32 |  | 1061 | 21230.61 | 0.5 |  | 39 | 132 | 92 | 263 | 5262.63 | n | 755.7436 |  |  |  | 18918.1073 | 17754.6615 | 44327.571 | 146944.062 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-05-20 |  | 197 | 475044 | 23198 | 7.26 | 37.6 |  | 965 | 22386.07 | 0.5 |  | 52 | 139 | 66 | 257 | 5961.886 | n | 837.6853 |  |  |  | 19917.9265 | 18387.7053 | 40328.294 | 139347.536 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-05-27 |  | 174 | 495230 | 20186 | 7.23 | 56.4 |  | 1026 | 20710.836 | 0.5 |  | 73 | 164 | 73 | 310 | 6257.66 | n | 872.3348 |  |  |  | 20630.7725 | 18472.6676 | 37476.91 | 138327.989 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-06-03 |  | 143 | 10032 | 10055 | 7.1 | 50 |  | 889 | 8938.895 | 0 |  | 0 | 167 | 13 | 180 | 1809.9 | n | 253.7929 |  |  |  | 18316.6027 | 17552.6342 | 46733.589 | 149368.39 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-06-10 |  | 131 | 23014 | 12982 | 7.16 | 60 |  | 990 | 12852.18 | 0 |  | 0 | 148 | 0 | 148 | 1921.336 | n | 266.3238 |  |  |  | 16221.9952 | 16782.9017 | 55112.019 | 158605.18 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-06-17 |  | 138 | 36694 | 13680 | 7.02 | 56 |  | 898 | 12284.64 | 1 |  | 0 | 155 | 12 | 167 | 2284.56 | n | 320.3334 |  |  |  | 13696.6377 | 16530.2317 | 65213.449 | 161637.22 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-06-24 |  | 172 | 53764 | 17070 | 7.03 | 46.4 |  | 978 | 16694.46 | 0 |  | 47 | 112 | 11 | 170 | 2901.9 | n | 391.2239 |  |  |  | 12692.5438 | 16518.9967 | 69229.825 | 161772.04 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-07-01 |  | 159 | 69495 | 15731 | 6.93 | 42.2 |  | 1032 | 16234.392 | 1.5 |  | 13 | 112 | 46 | 171 | 2690.001 | n | 385.1359 |  |  |  | 14516.418 | 16732.7293 | 61934.328 | 159207.248 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-07-08 |  | 148 | 84597 | 15102 | 7.26 | 44 |  | 928 | 14014.656 | 1 |  | 46 | 105 | 63 | 214 | 3231.828 | n | 456.03 |  |  |  | 14807.037 | 16649.0465 | 60771.852 | 160211.442 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-07-15 |  | 177 | 102153 | 17556 | 7.26 | 48.8 |  | 1020 | 17907.12 | 1 |  | 25 | 111 | 96 | 232 | 4072.992 | N | 593.8469 |  |  |  | 16212.657 | 16609.0737 | 55149.372 | 160691.115 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-07-22 |  | 152 | 117338 | 15185 | 7.34 | 74.6 |  | 870 | 13210.95 | 0.5 |  | 19 | 114 | 61 | 194 | 2945.89 | n | 423.5336 |  |  |  | 15341.7795 | 16221.6986 | 58632.882 | 165339.617 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-07-29 |  | 145 | 131728 | 14390 | 7.3 | 34 |  | 864 | 12432.96 | 1 |  | 62 | 109 | 98 | 269 | 3870.91 | n | 551.1058 |  |  |  | 14391.4215 | 15741.4808 | 62434.314 | 171102.231 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-08-05 |  | 159 | 147260 | 15532 | 7.25 | 32.8 |  | 992 | 15407.744 | 0.5 |  | 41 | 98 | 87 | 226 | 3510.232 | n | 504.6369 |  |  |  | 14739.6935 | 15256.2419 | 61041.226 | 176925.097 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-08-12 |  | 138 | 160770 | 13510 | 7.3 | 25.2 |  | 941 | 12712.91 | 0.5 |  | 17 | 112 | 97 | 226 | 3053.26 | n | 448.1015 |  |  |  | 13441.141 | 14450.1452 | 66235.436 | 186598.257 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-08-19 |  | 143 | 175021 | 14251 | 7.3 | 41.6 |  | 999 | 14236.749 | 0.5 |  | 12 | 133 | 95 | 240 | 3420.24 | n | 501.0494 |  |  |  | 13697.5907 | 13910.638 | 65209.637 | 193072.344 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-08-26 |  | 167 | 191564 | 16543 | 7.36 | 20.8 |  | 1008 | 16675.344 | 1 |  | 42 | 118 | 0 | 160 | 2646.88 | n | 353.7237 |  |  |  | 14758.1868 | 14555.3421 | 60967.253 | 185335.895 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-09-02 |  | 183 | 209660 | 18096 | 7.3 | 39.6 |  | 855 | 15472.08 | 1.5 |  | 36 | 102 | 93 | 231 | 4180.176 | n | 604.6204 |  |  |  | 14774.2707 | 14773.6671 | 60902.917 | 182715.995 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-09-09 |  | 156 | 225524 | 15864 | 7.07 | 46.4 |  | 853 | 13531.992 | 0.5 |  | 15 | 61 | 130 | 206 | 3267.984 | n | 494.4786 |  |  |  | 14979.0413 | 14877.6131 | 60083.835 | 181468.643 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-09-16 |  | 159 | 241618 | 16094 | 7.47 | 11.6 |  | 1019 | 16399.786 | 0.5 |  | 66 | 107 | 57 | 230 | 3701.62 | n | 513.4233 |  |  |  | 15519.8005 | 14853.0569 | 57920.798 | 181763.317 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-09-23 |  | 161 | 258110 | 16492 | 7.43 | 33.2 |  | 1027 | 16937.284 | 2 |  | 38 | 124 | 49 | 211 | 3479.812 | n | 488.4961 |  |  |  | 15585.2855 | 14911.6313 | 57658.858 | 181060.425 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-09-30 |  | 151 | 274710 | 16600 | 7.23 | 30 |  | 1083 | 17977.8 | 1.5 |  | 128 | 53 | 128 | 309 | 5129.4 | n | 718.1239 |  |  |  | 16211.7155 | 15241.8932 | 55153.138 | 177097.281 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-10-07 |  | 153 | 287514 | 12804 | 7.1 | 26.4 |  | 962 | 12317.448 | 3 |  | 23 | 202 | 62 | 287 | 3674.748 | n | 521.496 |  |  |  | 15908.0795 | 14776.0873 | 56367.682 | 182686.953 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-10-14 |  | 176 | 302041 | 14527 | 7.68 | 25.2 |  | 902 | 13103.354 | 3 |  | 33 | 143 | 65 | 241 | 3501.007 | n | 497.2631 |  |  |  | 15083.9715 | 14767.1209 | 59664.114 | 182794.549 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-10-21 |  | 196 | 317605 | 15564 | 7.08 | 33.2 |  | 960 | 14941.44 | 2 |  | 51 | 70 | 106 | 227 | 3533.028 | n | 511.4798 |  |  |  | 14585.0105 | 14976.1609 | 61659.958 | 180286.069 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-10-28 |  | 171 | 332287 | 14682 | 7.17 | 44 |  | 1068 | 15680.376 | 0 |  | 104 | 110 | 55 | 269 | 3949.458 | n | 536.5176 |  |  |  | 14010.6545 | 14998.8803 | 63957.382 | 180013.437 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-11-04 |  | 201 | 354811 | 22524 | 7.29 | 24.4 |  | 906 | 20406.744 | 1 |  | 39 | 93 | 56 | 188 | 4234.512 | n | 598.4458 |  |  |  | 16032.9785 | 15640.0331 | 55868.086 | 172319.603 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-11-11 |  | 193 | 376802 | 21991 | 7.15 | 20 |  | 997 | 21925.027 | 1 |  | 44 | 105 | 43 | 192 | 4222.272 | n | 588.0163 |  |  |  | 18238.3967 | 16280.7229 | 47046.413 | 164631.325 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-11-18 |  | 162 | 393851 | 17049 | 6.79 | 51.2 |  | 1071 | 18259.479 | 2.5 |  | 149 | 85 | 68 | 302 | 5148.798 | n | 691.4012 |  |  |  | 19067.9065 | 16412.7342 | 43728.374 | 163047.19 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-11-25 |  | 121 | 406358 | 12507 | 7.33 | 30 |  | 1149 | 14370.543 | 1 |  | 36 | 38 | 39 | 113 | 1413.291 | n | 198.247 |  |  |  | 18740.4483 | 16320.9394 | 45038.207 | 164148.727 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-12-02 |  | 113 | 418466 | 12108 | 7.66 | 19.2 |  | 1085 | 13137.18 | 1 |  | 44 | 77 | 29 | 150 | 1816.2 | n | 249.484 |  |  |  | 16923.0573 | 16288.0384 | 52307.771 | 164543.539 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-12-09 |  | 145 | 433905 | 15439 | 7.22 | 18.8 |  | 970 | 14975.83 | 0 |  | 91 | 81 | 54 | 226 | 3489.214 | n | 475.618 |  |  |  | 15185.758 | 16169.3754 | 59256.968 | 165967.495 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-12-16 |  | 134 | 444347 | 10442 | 7.25 | 17.6 |  | 1085 | 11329.57 | 1 |  | 26 | 113 | 0 | 139 | 1451.438 | n | 196.0431 |  |  |  | 13453.2807 | 15702.0659 | 66186.877 | 171575.209 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-12-23 |  | 153 | 455486 | 11139 | 7.3 | 20.8 |  | 1235 | 13756.665 | 0.5 |  | 80 | 100 | 0 | 180 | 2005.02 | n | 261.0317 |  |  |  | 13299.8113 | 15350.3047 | 66800.755 | 175796.344 | 8000 | 30000 | 100 | 6 | 10 | 35000
2005-12-30 |  | 141 | 465620 | 10134 | 7.07 | 25.2 |  | 1039 | 10529.226 | 0.5 |  | 60 | 114 | 79 | 253 | 2563.902 | n | 361.7241 |  |  |  | 12647.8227 | 15201.2862 | 69408.709 | 177584.566 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-01-06 |  | 217 | 483250 | 17630 | 7.15 | 21.6 |  | 894 | 15761.22 | 0 |  | 101 | 45 | 0 | 146 | 2573.98 | n | 323.0361 |  |  |  | 12844.1702 | 15422.775 | 68623.319 | 174926.7 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-01-13 |  | 184 | 496448 | 13198 | 7.24 | 22.8 |  | 1135 | 14979.73 | 0.5 |  | 114.84 | 76.14 | 56.54 | 247.52 | 3266.769 | n | 440.7339 |  |  |  | 13756.7103 | 15425.9658 | 64973.159 | 174888.41 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-01-20 |  | 171 | 12056 | 15605 | 7.2 | 21.6 |  | 1192 | 18601.16 | 0.5 |  | 112 | 64 | 36 | 212 | 3308.26 | n | 437.9715 |  |  |  | 14967.834 | 15669.3645 | 60128.664 | 171967.626 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-01-27 |  | 148 | 26768 | 14712 | 7.2 | 20.8 |  | 1181 | 17374.872 | 0 |  | 127 | 58 | 60 | 245 | 3604.44 | n | 483.8977 |  |  |  | 16679.2455 | 15416.7085 | 53283.018 | 174999.498 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-02-03 |  | 137 | 40422 | 13654 | 6.8 | 16 |  | 1128 | 15401.712 | 0 |  | 141 | 62 | 63 | 266 | 3631.964 | n | 486.1341 |  |  |  | 16589.3685 | 14873.0989 | 53642.526 | 181522.813 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-02-10 |  | 150 | 55280 | 14858 | 7 | 15.2 |  | 1034 | 15363.172 | 0 |  | 124 | 69 | 59 | 252 | 3744.216 | n | 503.63 |  |  |  | 16685.229 | 14631.74 | 53259.084 | 184419.12 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-02-17 |  | 151 | 70392 | 15112 | 7.3 | 17.2 |  | 1199 | 18119.288 | 0 |  | 114 | 69 | 47 | 230 | 3475.76 | n | 464.9751 |  |  |  | 16564.761 | 14944.1354 | 53740.956 | 180670.375 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-02-24 |  | 114 | 81794 | 11402 | 7.02 | 27.6 |  | 1199 | 13670.998 | 0 |  | 161 | 104 | 67 | 332 | 3785.464 | n | 506.9604 |  |  |  | 15638.7925 | 14988.6202 | 57444.83 | 180136.557 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-03-03 |  | 177 | 99225 | 17431 | 7.6 | 26 |  | 1090 | 18999.79 | 0.5 |  | 127 | 57 | 44 | 228 | 3974.268 | n | 526.0333 |  |  |  | 16538.312 | 15323.9502 | 53846.752 | 176112.597 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-03-10 |  | 172 | 115829 | 16604 | 7.59 | 18.8 |  | 1097 | 18214.588 | 0 |  | 117 | 56 | 59 | 232 | 3852.128 | n | 518.9851 |  |  |  | 17251.166 | 15897.7018 | 50995.336 | 169227.579 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-03-17 |  | 149 | 130251 | 14422 | 7.53 | 20.8 |  | 1094 | 15777.668 | 0.5 |  | 100 | 47 | 46 | 193 | 2783.446 | n | 373.2841 |  |  |  | 16665.761 | 16066.1187 | 53336.956 | 167206.576 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-03-24 |  | 177 | 146716 | 16465 | 7.55 | 26.8 |  | 1044 | 17189.46 | 0 |  | 118 | 46 | 48 | 212 | 3490.58 | n | 464.6429 |  |  |  | 17545.3765 | 16621.1382 | 49818.494 | 160546.342 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-03-31 |  | 162 | 162454 | 15738 | 7.84 | 32.4 |  | 1226 | 19294.788 | 0 |  | 91 | 62 | 40 | 193 | 3037.434 | N | 407.9247 |  |  |  | 17619.126 | 16915.6022 | 49523.496 | 157012.774 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-04-07 |  | 180 | 179972 | 18148.648 | 7.83 | 12 |  | 1134 | 20580.5668 | 0 |  | 110 | 44 | 40 | 194 | 3520.8377 | N | 466.3873 |  |  |  | 18210.6207 | 17382.3386 | 47157.5172 | 151411.9372 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-04-14 |  | 178 | 197517 | 17825.72 | 7.41 | 21.2 |  | 1046 | 18645.7031 | 0 |  | 109 | 41 | 43 | 193 | 3440.364 | N | 457.1485 |  |  |  | 18927.6295 | 17386.0505 | 44289.482 | 151367.394 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-04-21 |  | 147 | 212113 | 14639.788 | 7.11 | 25.2 |  | 977 | 14303.0729 | 0 |  | 119 | 75 | 61 | 255 | 3733.1459 | N | 504.3619 |  |  |  | 18206.0327 | 17130.0672 | 47175.8692 | 154439.1932 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-04-28 |  | 149 | 227094 | 14771.266 | 7.69 | 21.2 |  | 1151 | 17001.7272 | 0 |  | 69 | 95 | 44 | 208 | 3072.4233 | n | 421.0577 |  |  |  | 17632.7675 | 17263.4018 | 49468.93 | 152839.178 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-05-05 |  | 171 | 245703 | 17120.28 | 7.54 | 16.8 |  | 1053 | 18027.6548 | 0 |  | 77 | 58 | 33 | 168 | 2876.207 | N | 386.2956 |  |  |  | 16994.5395 | 17485.4421 | 52021.842 | 150174.6952 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-05-12 |  | 173 | 263082 | 16822.872 | 7.43 | 18 |  | 1024 | 17226.6209 | 0 |  | 92 | 62 | 42 | 196 | 3297.2829 | N | 443.4715 |  |  |  | 16639.769 | 17411.0531 | 53440.9242 | 151067.3622 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-05-19 |  | 130 | 272658 | 13138.272 | 7.62 | 30.4 |  | 1202 | 15792.2029 | 0 |  | 52 | 140 | 59 | 251 | 3297.7063 | N | 461.4479 |  |  |  | 17012.0515 | 17587.8202 | 51951.7941 | 148946.1573 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-05-26 |  | 160 | 286066 | 16170.048 | 7.7 | 17.2 |  | 1223 | 19775.9687 | 0 |  | 45.7 | 67.7 | 29.9 | 143.3 | 2317.1679 | n | 317.9683 |  |  |  | 17705.6119 | 17652.5018 | 49177.5526 | 148169.9786 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-06-02 |  | 163 | 302276 | 16210 | 7.5 | 42.8 |  | 1191 | 19306.11 | 0 |  | 76 | 131.6 | 28.6 | 236.2 | 3828.802 | n | 517.7134 |  |  |  | 18025.2256 | 17743.462 | 47899.0974 | 147078.4566 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-06-09 |  | 160 | 318176 | 15900 | 7.46 | 54 |  | 1077 | 17124.3 | 0.5 |  | 88 | 90 | 45 | 223 | 3545.7 | n | 480.92 |  |  |  | 17999.6454 | 17855.6813 | 48001.4184 | 145731.8246 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-06-16 |  | 111 | 328776 | 10600 | 7.71 | 53.2 |  | 1326 | 14055.6 | 0 |  | 52 | 105 | 38 | 195 | 2067 | n | 285.0512 |  |  |  | 17565.4947 | 17594.5263 | 49738.0213 | 148865.6846 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-06-23 |  | 161 | 344816 | 16040 | 7.71 | 20.4 |  | 1235 | 19809.4 | 0 |  | 88 | 93 | 49 | 230 | 3689.2 | n | 502.1492 |  |  |  | 17573.8525 | 17637.4106 | 49704.59 | 148351.0726 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-06-30 |  | 194 | 364146 | 19330 | 7.46 | 25.2 |  | 1052 | 20335.16 | 0.5 |  | 118 | 67 | 37 | 222 | 4291.26 | n | 567.5445 |  |  |  | 17831.115 | 17616.96 | 48675.54 | 148596.4794 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-07-07 |  | 193 | 383356 | 19210 | 7.42 | 27.6 |  | 911 | 17500.31 | 0 |  | 69 | 53 | 32 | 154 | 2958.34 | n | 398.653 |  |  |  | 17925.1175 | 17521.5106 | 48299.53 | 149741.8725 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-07-14 |  | 148 | 398036 | 14680 | 7.72 | 30 |  | 1141 | 16749.88 | 0 |  | 0 | 140 | 28 | 168 | 2466.24 | n | 351.0236 |  |  |  | 18598.6875 | 17725.4112 | 45605.25 | 147295.0654 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-07-21 |  | 148 | 413846 | 15810 | 7.46 | 27.2 |  | 1048 | 16568.88 | 0 |  | 38 | 106 | 71 | 215 | 3399.15 | n | 484.8194 |  |  |  | 17788.5575 | 17689.3406 | 48845.77 | 147727.9126 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-07-28 |  | 156 | 429366 | 15520 | 7.52 | 29.6 |  | 1209.4 | 18769.888 | 0 |  | 8.5593 | 135.61 | 54.26 | 198.4293 | 3079.6229 | n | 443.1443 |  |  |  | 17397.2395 | 17751.1934 | 50411.042 | 146985.6794 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-08-04 |  | 186 | 447956 | 18590 | 7.4 | 31.2 |  | 1135 | 21099.65 | 0 |  | 81.49 | 65.85 | 44.09 | 191.43 | 3558.6837 | n | 482.8493 |  |  |  | 18297.0745 | 18073.9458 | 46811.702 | 143112.6504 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-08-11 |  | 32 | 451186 | 3230 | 7.58 | 72.4 |  | 1807 | 5836.61 | 0 |  | 448 | 407 | 105 | 960 | 3100.8 | n | 409.9491 |  |  |  | 15568.757 | 17244.3131 | 57724.972 | 153068.2433 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-08-18 |  | 84 | 458786 | 7600 | 7.34 | 35.6 |  | 1104 | 8390.4 | 0 |  | 197.6971 | 223.6257 | 4.0612 | 425.384 | 3232.9185 | n | 420.3348 |  |  |  | 13524.137 | 16295.5157 | 65903.452 | 164453.812 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-08-25 |  | 171 | 475926 | 17140 | 7.56 | 26.4 |  | 1075 | 18425.5 | 0 |  | 0 | 281 | 89 | 370 | 6341.8 | n | 913.0878 |  |  |  | 13438.04 | 16222.1315 | 66247.84 | 165334.422 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-09-01 |  | 181 | 494046 | 18120 | 7.54 | 27.2 |  | 1156.6 | 20957.592 | 0 |  | 68 | 86 | 16 | 170 | 3080.4 | n | 410.0965 |  |  |  | 13402.5255 | 16541.5725 | 66389.898 | 161501.13 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-09-08 |  | 148 | 8800 | 14754 | 7.25 | 32.8 |  | 1029.5 | 15189.243 | 0 |  | 17.5161 | 112.1293 | 0 | 129.6454 | 1912.7882 | n | 260.2402 |  |  |  | 15740.6838 | 16636.0428 | 57037.265 | 160367.487 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-09-15 |  | 199 | 28800 | 20000 | 7.4 | 20 |  | 1166 | 23320 | 0 |  | 63 | 55 | 50 | 168 | 3360 | n | 464.164 |  |  |  | 19473.0838 | 16928.5927 | 42107.665 | 156856.887 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-09-22 |  | 141 | 42850 | 14050 | 7.37 | 50.8 |  | 684 | 9610.2 | 0 |  | 52 | 86 | 47 | 185 | 2599.25 | n | 361.1726 |  |  |  | 17269.2588 | 16034.8461 | 50922.965 | 167581.847 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-09-29 |  | 143 | 57170 | 14320 | 7.38 | 37.6 |  | 1286 | 18415.52 | 0 |  | 30 | 96 | 17 | 143 | 2047.76 | n | 281.1346 |  |  |  | 16633.7408 | 16111.1136 | 53465.037 | 166666.637 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-10-06 |  | 164 | 73600 | 16430 | 7.33 | 34 |  | 1024 | 16824.32 | 0.5 |  | 61.9995 | 90.7559 | 5.6914 | 158.4468 | 2603.2801 | n | 343.6272 |  |  |  | 17042.51 | 16117.3169 | 51829.96 | 166592.197 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-10-13 |  | 167 | 90300 | 16700 | 7.53 | 25.2 |  | 1303 | 21760.1 | 1 |  | 62 | 152 | 8 | 222 | 3707.4 | n | 497.2503 |  |  |  | 16652.535 | 16549.9186 | 53389.86 | 161400.977 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-10-20 |  | 170 | 108160 | 17860 | 7.28 | 33.6 |  | 1253 | 22378.58 | 0 |  | 68 | 99 | 9 | 176 | 3143.36 | n | 416.2773 |  |  |  | 19844.63 | 16850.6429 | 40621.48 | 157792.285 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-10-27 |  | 153 | 123430 | 15270 | 7.21 | 23.2 |  | 993 | 15163.11 | 0 |  | 84 | 97 | 9 | 190 | 2901.3 | n | 380.9117 |  |  |  | 19031.5275 | 16355.9312 | 43873.89 | 163728.825 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-11-03 |  | 177 | 141140 | 17710 | 7.33 | 21.6 |  | 1119 | 19817.49 | 0 |  | 73 | 108 | 11 | 192 | 3400.32 | n | 451.1703 |  |  |  | 19779.82 | 17521.0046 | 40880.72 | 149747.945 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-11-10 |  | 183 | 158580 | 17440 | 7.24 | 26.4 |  | 1296 | 22602.24 | 0 | 67.5 | 100 | 85 | 10 | 195 | 3400.8 | n | 442.2293 |  |  |  | 19990.355 | 18705.3246 | 40038.58 | 135536.105 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-11-17 |  | 143 | 172910 | 14330 | 7.07 | 23.2 |  | 1272 | 18227.76 | 0 | 46.2 | 102 | 112 | 15 | 229 | 3281.57 | n | 431.9588 |  |  |  | 18952.65 | 18688.8462 | 44189.4 | 135733.845 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-11-24 |  | 164 | 189440 | 16530 | 7.18 | 22 |  | 1398 | 23108.94 | 0 | 28.6 | 111.6 | 78.5 | 5.5 | 195.6 | 3233.268 | n | 415.2351 |  |  |  | 20939.1075 | 18868.1253 | 36243.57 | 133582.497 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-12-01 |  | 158 | 205110 | 15670 | 7.39 | 26 |  | 1341 | 21013.47 | 0 | 82.6 | 87.5381 | 89.6256 | 8.8734 | 186.0371 | 2915.2007 | n | 381.1867 |  |  |  | 21238.1025 | 19353.4775 | 35047.59 | 127758.27 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-12-08 |  | 195 | 224610 | 19500 | 7.38 | 10.8 |  | 1245 | 24277.5 | 0 | 69.9 | 41 | 153 | 37 | 231 | 4504.5 | n | 625.3246 |  |  |  | 21656.9175 | 19433.2692 | 33372.33 | 126800.77 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-12-15 |  | 142 | 238860 | 14250 | 6.92 | 21.6 |  | 1268 | 18069 | 0 | 6.64 | 55 | 87 | 138 | 280 | 3990 | n | 582.0769 |  |  |  | 21617.2275 | 20138.1692 | 33531.09 | 118341.97 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-12-22 |  | 185 | 257370 | 18510 | 7.25 | 20 |  | 1227 | 22711.77 | 0.5 | 63.31 | 145 | 65 | 44 | 254 | 4701.54 | n | 618.989 |  |  |  | 21517.935 | 20496.19 | 33928.26 | 114045.72 | 8000 | 30000 | 100 | 6 | 10 | 35000
2006-12-29 |  | 160 | 273470 | 16100 | 7.34 | 28.4 |  | 1395 | 22459.5 | 1 | 62.6 | 101 | 127 | 43 | 271 | 4363.1 | n | 589.4044 |  |  |  | 21879.4425 | 20965.7883 | 32482.23 | 108410.54 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-01-05 |  | 148 | 288180 | 14710 | 7.23 | 22.4 |  | 1190 | 17504.9 |  | 6.22 | 190 | 91 | 57 | 338 | 4971.98 | n | 654.9086 |  |  |  | 20186.2925 | 20611.1883 | 39254.83 | 112665.74 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-01-12 |  | 169 | 305020 | 16840 | 7.3 | 20.4 |  | 1329 | 22380.36 |  | 53.9 | 184 | 88 | 42 | 314 | 5287.76 | n | 689.9977 |  |  |  | 21264.1325 | 20611.3367 | 34943.47 | 112663.96 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-01-19 |  | 170 | 322120 | 17100 | 7.35 | 21.2 |  | 1110 | 18981 |  | 49.25 | 283 | 75 | 38 | 396 | 6771.6 | n | 861.3993 |  |  |  | 20331.44 | 20929.4942 | 38674.24 | 108846.07 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-01-26 |  | 156 | 337720 | 15600 | 7.37 | 22 |  | 1177 | 18361.2 |  | 46.69 | 193 | 101 | 43 | 337 | 5257.2 | n | 686.6115 |  |  |  | 19306.865 | 20808.1367 | 42772.54 | 110302.36 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-02-02 |  | 137 | 351430 | 13710 | 7.24 | 20.8 |  | 1241 | 17014.11 |  | 14.6129 | 157 | 104 | 55 | 316 | 4332.36 | n | 576.5431 |  |  |  | 19184.1675 | 20342.4592 | 43263.33 | 115890.49 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-02-09 |  | 155 | 366900 | 15470 | 7.58 | 27.2 |  | 1219 | 18857.93 |  | 51.7145 | 171 | 73 | 37 | 281 | 4347.07 | n | 565.1868 |  |  |  | 18303.56 | 20394.9733 | 46785.76 | 115260.32 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-02-16 |  | 150 | 381800 | 14900 | 7.55 | 26 |  | 1333 | 19861.7 |  | 60.3494 | 165 | 89 | 37 | 291 | 4335.9 | n | 566.7103 |  |  |  | 18523.735 | 20124.37 | 45905.06 | 118507.56 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-02-23 |  | 189 | 399690 | 17890 | 7.7 | 33.6 |  | 1278 | 22863.42 |  | 58.0721 | 200 | 76 | 37 | 313 | 5599.57 | n | 723.1192 |  |  |  | 19649.29 | 20278.5325 | 41402.84 | 116657.61 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-03-02 |  | 165 | 416190 | 16500 | 7.7 | 16.4 |  | 1414 | 23331 |  | 63.6 | 212 | 83 | 41 | 336 | 5544 | n | 717.2579 |  |  |  | 21228.5125 | 20199.6575 | 35085.95 | 117604.11 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-03-09 |  | 166 | 432890 | 16700 | 7.73 | 21.6 |  | 1451 | 24231.7 |  | 66.52 | 265 | 74 | 36 | 375 | 6262.5 | n | 797.5908 |  |  |  | 22571.955 | 20713.2158 | 29712.18 | 111441.41 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-03-16 |  | 155 | 448350 | 15460 | 7.54 | 18.4 |  | 1419 | 21937.74 |  | 43.36 | 196 | 140 | 34 | 370 | 5720.2 | n | 747.1848 |  |  |  | 23090.965 | 20648.7133 | 27636.14 | 112215.44 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-03-23 |  | 160 | 464340 | 15990 | 7.58 | 28.8 |  | 1310 | 20946.9 |  | 72.4 | 178 | 75 | 35 | 288 | 4605.12 | n | 596.8646 |  |  |  | 22611.835 | 20522.6633 | 29552.66 | 113728.04 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-03-30 |  | 158 | 480190 | 15850 | 7.6 | 18 |  | 1384 | 21936.4 |  | 65.3 | 133 | 98 | 35 | 266 | 4216.1 | n | 556.8243 |  |  |  | 22263.185 | 20891.955 | 30947.26 | 109296.54 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-04-06 |  | 164 | 496610 | 16420 | 7.41 | 28.8 |  | 1294 | 21247.48 |  | 59.12 | 220 | 88 | 32 | 340 | 5582.8 | n | 717.098 |  |  |  | 21517.13 | 20797.5483 | 33931.48 | 110429.42 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-04-13 |  | 179 | 14420 | 17810 | 7.52 | 19.6 |  | 1313 | 23384.53 |  | 58.45 | 146 | 136 | 17 | 299 | 5325.19 | n | 695.6088 |  |  |  | 21878.8275 | 21164.5092 | 32484.69 | 106025.89 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-04-20 |  | 151 | 29330 | 14910 | 8.17 | 42.8 |  | 1407 | 20978.37 |  | 73.07 | 179 | 94 | 35 | 308 | 4592.28 | n | 597.6031 |  |  |  | 21886.695 | 21382.6067 | 32453.22 | 103408.72 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-04-27 |  | 180 | 47430 | 18100 | 7.94 | 28 |  | 1238 | 22407.8 |  | 63.1 | 110 | 116 | 40 | 266 | 4814.6 | n | 645.7787 |  |  |  | 22004.545 | 21832.0808 | 31981.82 | 98015.03 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-05-04 |  | 140 | 61380 | 13950 | 7.81 | 28.4 |  | 1195 | 16670.25 |  | 34.14 | 176 | 60 | 32 | 268 | 3738.6 | n | 481.6389 |  |  |  | 20860.2375 | 21649.7742 | 36559.05 | 100202.71 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-05-11 |  | 169 | 78320 | 16940 | 7.89 | 39.2 |  | 1286 | 21784.84 |  | 63.1 | 152 | 121 | 16 | 289 | 4895.66 | n | 635.8433 |  |  |  | 20460.315 | 21810.0358 | 38158.74 | 98279.57 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-05-18 |  | 170 | 95340 | 17020 | 7.79 | 46.4 |  | 1305 | 22211.1 |  | 62.07 | 173 | 85 | 15 | 273 | 4646.46 | n | 593.944 |  |  |  | 20768.4975 | 21755.6758 | 36926.01 | 98931.89 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-05-25 |  | 129 | 108250 | 12910 | 7.67 | 35.2 |  | 1287 | 16615.17 |  | 41.32 | 55 | 177 | 34 | 266 | 3434.06 | n | 472.3396 |  |  |  | 19320.34 | 21196.0233 | 42718.64 | 105647.72 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-06-01 |  | 189 | 127100 | 18850 | 7.67 | 31.6 |  | 1256 | 23675.6 |  | 60.83 | 130 | 73 | 26 | 229 | 4316.65 | n | 562.8285 |  |  |  | 21071.6775 | 21149.6817 | 35713.29 | 106203.82 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-06-08 |  | 121 | 139280 | 12180 | 7.29 | 34.8 |  | 1324 | 16126.32 |  | 36.91 | 139 | 128 | 54 | 321 | 3909.78 | n | 524.5281 |  |  |  | 19657.0475 | 20665.3967 | 41371.81 | 112015.24 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-06-15 |  | 158 | 155050 | 15770 | 7.88 | 75.6 |  | 1278 | 20154.06 |  | 70.41 | 87 | 134 | 12 | 233 | 3674.41 | n | 487.5382 |  |  |  | 19142.7875 | 20599.3267 | 43428.85 | 112808.08 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-06-22 |  | 181 | 173210 | 18160 | 7.73 | 38.4 |  | 1101 | 19994.16 |  | 60.92 | 38 | 179 | 13 | 230 | 4176.8 | n | 571.1473 |  |  |  | 19987.535 | 20437.4733 | 40049.86 | 114750.32 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-06-29 |  | 189 | 192050 | 18840 | 7.66 | 38.8 |  | 1134 | 21364.56 |  | 61.68 | 142 | 116 | 9 | 267 | 5030.28 | n | 650.3368 |  |  |  | 19409.775 | 20447.23 | 42360.9 | 114633.24 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-07-06 |  | 146 | 206630 | 14580 | 7.65 | 72 |  | 1348 | 19653.84 |  | 70.3 | 128 | 141 | 52 | 321 | 4680.18 | n | 630.2731 |  |  |  | 20291.655 | 20136.3392 | 38833.38 | 118363.93 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-07-13 |  | 178 | 223480 | 16850 | 7.61 | 52.8 |  | 1327 | 22359.95 |  | 70.7 | 108 | 107 | 44 | 259 | 4364.15 | n | 586.9735 |  |  |  | 20843.1275 | 20251.4708 | 36627.49 | 116982.35 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-07-20 |  | 151 | 238600 | 15120 | 7.4 | 38.4 |  | 1212 | 18325.44 |  | 43.8 | 142 | 95 | 62 | 299 | 4520.88 | n | 606.8681 |  |  |  | 20425.9475 | 19911.2742 | 38296.21 | 121064.71 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-07-27 |  | 164 | 255020 | 16420 | 7.65 | 38 |  | 1274 | 20919.08 |  | 69.15 | 168 | 95 | 48 | 311 | 5106.62 | n | 673.1382 |  |  |  | 20314.5775 | 20265.3433 | 38741.69 | 116815.88 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-08-03 |  | 161 | 271120 | 16100 | 7.59 | 34 |  | 1193 | 19207.3 |  | 51.9 | 145 | 110 | 59 | 314 | 5055.4 | n | 677.6845 |  |  |  | 20202.9425 | 20050.5483 | 39188.23 | 119393.42 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-08-10 |  | 163 | 287400 | 16280 | 7.44 | 30 |  | 1082 | 17614.96 |  | 43.4 | 54 | 198 | 73 | 325 | 5291 | n | 743.2505 |  |  |  | 19016.695 | 19667.5367 | 43933.22 | 123989.56 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-08-17 |  | 156 | 303020 | 15620 | 7.8 | 43.6 |  | 1256 | 19618.72 |  | 67.5 | 150 | 124 | 58 | 332 | 5185.84 | n | 694.6241 |  |  |  | 19340.015 | 19917.8325 | 42639.94 | 120986.01 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-08-24 |  | 178 | 320840 | 17820 | 7.69 | 26.8 |  | 1130 | 20136.6 |  | 57.4 | 141 | 132 | 55 | 328 | 5844.96 | n | 784.4257 |  |  |  | 19144.395 | 19622.9158 | 43422.42 | 124525.01 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-08-31 |  | 163 | 337150 | 16310 | 7.41 | 44.4 |  | 1229 | 20044.99 |  | 74.8 | 122 | 123 | 28 | 273 | 4452.63 | n | 589.6643 |  |  |  | 19353.8175 | 19949.4717 | 42584.73 | 120606.34 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-09-07 |  | 152 | 352280 | 15130 | 7.76 | 62 |  | 1325 | 20047.25 |  | 71.7 | 115 | 133 | 52 | 300 | 4539 | n | 613.7355 |  |  |  | 19961.89 | 19940.5708 | 40152.44 | 120713.15 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-09-14 |  | 138 | 365900 | 13620 | 7.93 | 46.8 |  | 1363 | 18564.06 |  | 55 | 311 | 81 | 39 | 431 | 5870.22 | n | 745.2491 |  |  |  | 19698.225 | 19821.3958 | 41207.1 | 122143.25 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-09-21 |  | 156 | 381590 | 15690 | 7.55 | 33.2 |  | 1231 | 19314.39 |  | 50 | 167 | 133 | 70 | 370 | 5805.3 | n | 779.525 |  |  |  | 19492.6725 | 19650.5483 | 42029.31 | 124193.42 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-09-28 |  | 171 | 398690 | 17100 | 7.61 | 25.2 |  | 1165 | 19921.5 |  | 60.5 | 178 | 96 | 80 | 354 | 6053.4 | n | 811.9018 |  |  |  | 19461.8 | 19672.8533 | 42152.8 | 123925.76 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-10-05 |  | 141 | 412710 | 14020 | 7.68 | 46.4 |  | 1269 | 17791.38 |  | 50.5 | 96 | 151 | 48 | 295 | 4135.9 | n | 562.791 |  |  |  | 18897.8325 | 19292.1392 | 44408.67 | 128494.33 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-10-12 |  | 159 | 428690 | 15980 | 7.67 | 33.6 |  | 1348 | 21541.04 |  | 67.9 | 211 | 98 | 32 | 341 | 5449.18 | n | 702.8235 |  |  |  | 19642.0775 | 19560.1058 | 41431.69 | 125278.73 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-10-19 |  | 133 | 441930 | 13240 | 7.76 | 37.2 |  | 1311 | 17357.64 |  | 77.1 | 134 | 161 | 36 | 331 | 4382.44 | n | 584.4682 |  |  |  | 19152.89 | 19263.3192 | 43388.44 | 128840.17 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-10-26 |  | 152 | 457180 | 15250 | 7.59 | 44.4 |  | 1230 | 18757.5 |  | 69.44 | 174 | 85 | 32 | 291 | 4437.75 | n | 575.7198 |  |  |  | 18861.89 | 19225.8358 | 44552.44 | 129289.97 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-11-02 |  | 162 | 473400 | 16220 | 7.56 | 46.4 |  | 1139 | 18474.58 |  | 80.9 | 196 | 72 | 33 | 301 | 4882.22 | n | 628.4201 |  |  |  | 19032.69 | 19297.4708 | 43869.24 | 128430.35 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-11-09 |  | 152 | 488570 | 15170 | 7.47 | 26.8 |  | 1262 | 19144.54 |  | 71.85 | 133 | 108 | 35 | 276 | 4186.92 | n | 553.9631 |  |  |  | 18433.565 | 19257.9558 | 46265.74 | 128904.53 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-11-16 |  | 159 | 4520 | 15950 | 7.51 | 24.4 |  | 1258 | 20065.1 |  | 58.9 | 169.5928 | 85 | 32 | 286.5928 | 4571.1548 | n | 593.7349 |  |  |  | 19110.43 | 19251.9975 | 43558.28 | 128976.03 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-11-23 |  | 142 | 18680 | 14160 | 7.56 | 39.6 |  | 1376 | 19484.16 |  | 57.92 | 123.3171 | 133.7425 | 47.7133 | 304.773 | 4315.5857 | n | 580.1702 |  |  |  | 19292.095 | 19205.2617 | 42831.62 | 129536.86 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-11-30 |  | 147 | 33450 | 14770 | 7.74 | 29.2 |  | 1389 | 20515.53 |  | 59.89 | 162 | 95 | 34 | 291 | 4298.07 | n | 561.6174 |  |  |  | 19802.3325 | 19244.285 | 40790.67 | 129068.58 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-12-07 |  | 177 | 51090 | 17640 | 7.56 | 23.2 |  | 1316 | 23214.24 |  | 63.3 | 129 | 114 | 26 | 269 | 4745.16 | n | 624.8403 |  |  |  | 20819.7575 | 19631.8 | 36720.97 | 124418.4 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-12-14 |  | 143 | 65380 | 14290 | 7.74 | 30 |  | 1265 | 18076.85 |  | 62.6 | 168 | 80.44 | 6.24 | 254.68 | 3639.3772 | n | 460.9497 |  |  |  | 20322.695 | 19528.6717 | 38709.22 | 125655.94 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-12-21 |  | 154 | 80820 | 15440 | 7.68 | 21.2 |  | 1362 | 21029.28 |  | 74.8 | 129 | 127 | 6 | 262 | 4045.28 | n | 525.043 |  |  |  | 20708.975 | 19620.9867 | 37164.1 | 124548.16 | 8000 | 30000 | 100 | 6 | 10 | 35000
2007-12-28 |  | 145 | 95350 | 14530 | 7.8 | 29.2 |  | 1404 | 20400.12 |  | 78.6 | 159 | 88 | 5 | 252 | 3661.56 | n | 465.3706 |  |  |  | 20680.1225 | 19838.3817 | 37279.51 | 121939.42 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-01-04 |  | 152 | 110550 | 15200 | 7.6 | 21.2 |  | 1330 | 20216 |  | 65.71 | 144 | 146 | 8 | 298 | 4529.6 | n | 589.0874 |  |  |  | 19930.5625 | 19727.9617 | 40277.75 | 123264.46 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-01-11 |  | 179 | 128490 | 17940 | 7.48 | 21.2 |  | 1123 | 20146.62 |  | 53.06 | 174 | 90 | 7.6 | 271.6 | 4872.504 | n | 619.2664 |  |  |  | 20448.005 | 19960.3767 | 38207.98 | 120475.48 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-01-18 |  | 166 | 145020 | 16530 | 7.77 | 33.2 |  | 1217 | 20117.01 |  | 76.81 | 150 | 154 | 5 | 309 | 5107.77 | n | 662.8505 |  |  |  | 20219.9375 | 20073.6692 | 39120.25 | 119115.97 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-01-25 |  | 176 | 162640 | 17620 | 7.55 | 40.4 |  | 1147 | 20210.14 |  | 72.04 | 170 | 91 | 4 | 265 | 4669.3 | n | 592.0218 |  |  |  | 20172.4425 | 20218.2992 | 39310.23 | 117380.41 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-02-01 |  | 121 | 174780 | 12140 | 7.52 | 31.6 |  | 1201 | 14580.14 |  | 54.52 | 80.558 | 184.55 | 4.756 | 269.864 | 3276.149 | n | 436.8693 |  |  |  | 18763.4775 | 19837.9325 | 44946.09 | 121944.81 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-02-08 |  | 154 | 190130 | 15350 | 7.43 | 30 |  | 1094.98 | 16807.943 |  | 33.64 | 179 | 93 | 9.7 | 281.7 | 4324.095 | n | 550.617 |  |  |  | 17928.8082 | 19566.5027 | 48284.767 | 125201.967 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-02-15 |  | 179 | 208080 | 17950 | 7.61 | 55.2 |  | 1096 | 19673.2 |  | 62.07 | 112 | 134 | 5 | 251 | 4505.45 | n | 588.4111 |  |  |  | 17817.8557 | 19582.2561 | 48728.577 | 125012.927 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-02-22 |  | 161 | 224210 | 16130 | 7.9 | 27.6 |  | 1249 | 20146.37 |  | 69.7 | 212 | 92 | 5 | 309 | 4984.17 | n | 627.8537 |  |  |  | 17801.9133 | 19551.4928 | 48792.347 | 125382.087 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-02-29 |  | 187 | 242840 | 18630 | 7.71 | 24.8 |  | 1141 | 21256.83 |  | 69.6 | 141 | 142 | 4 | 287 | 5346.81 | n | 693.0107 |  |  |  | 19471.0857 | 19388.3753 | 42115.657 | 127339.497 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-03-07 |  | 155 | 258400 | 15560 | 7.71 | 28 |  | 1175 | 18283 |  | 59.1 | 165 | 110 | 5 | 280 | 4356.8 | n | 556.9813 |  |  |  | 19839.85 | 19405.5544 | 40640.6 | 127133.347 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-03-14 |  | 147 | 273120 | 14720 | 7.61 | 29.2 |  | 1241 | 18267.52 |  | 83.4 | 90.5 | 180.32 | 4.27 | 275.09 | 4049.3248 | n | 537.4425 |  |  |  | 19488.43 | 19175.4077 | 42046.28 | 129895.107 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-03-21 |  | 171 | 290180 | 17060 | 7.35 | 25.6 |  | 1165 | 19874.9 |  | 70.97 | 165.6661 | 147.2514 | 4.3145 | 317.232 | 5411.9772 | n | 698.2429 |  |  |  | 19420.5625 | 19131.6394 | 42317.75 | 130420.327 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-03-28 |  | 157 | 305900 | 15720 | 7.56 | 36.4 |  | 1174 | 18455.28 |  | 52.08 | 127 | 158 | 11 | 296 | 4653.12 | n | 611 |  |  |  | 18720.175 | 18984.9127 | 45119.3 | 132181.047 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-04-04 |  | 149 | 320830 | 14930 | 7.68 | 55.2 |  | 1333 | 19901.69 |  | 85.5 | 165.68 | 118.98 | 4.78 | 289.44 | 4321.3392 | n | 553.7004 |  |  |  | 19124.8475 | 18964.5019 | 43500.61 | 132425.977 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-04-11 |  | 172 | 338030 | 17200 | 7.69 | 38.8 |  | 1199 | 20622.8 |  | 75.45 | 72 | 157 | 5 | 234 | 4024.8 | n | 536.3366 |  |  |  | 19713.6675 | 19006.6511 | 41145.33 | 131920.187 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-04-18 |  | 165 | 354560 | 16530 | 7.73 | 53.2 |  | 1329 | 21968.37 |  | 72.04 | 197 | 110 | 5 | 312 | 5157.36 | n | 654.9975 |  |  |  | 20237.035 | 19153.1702 | 39051.86 | 130161.957 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-04-25 |  | 157 | 370270 | 15710 | 7.75 | 50.8 |  | 1353 | 21255.63 |  | 75.94 | 86 | 198 | 7 | 291 | 4571.61 | n | 610.5311 |  |  |  | 20937.1225 | 19709.4611 | 36251.51 | 123486.467 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-05-02 |  | 159 | 386130 | 15860 | 7.55 | 75.2 |  | 1362 | 21601.32 |  | 81.78 | 110 | 141 | 4 | 255 | 4044.3 | n | 528.9409 |  |  |  | 21362.03 | 20108.9092 | 34551.88 | 118693.09 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-05-09 |  | 177 | 403800 | 17670 | 7.58 | 13.2 |  | 1201 | 21221.67 |  | 66.51 | 55 | 189 | 4 | 248 | 4382.16 | n | 590.5825 |  |  |  | 21511.7475 | 20237.9483 | 33953.01 | 117144.62 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-05-16 |  | 172 | 421010 | 17210 | 7.71 | 82 |  | 1263 | 21736.23 |  | 71.07 | 121 | 149 | 7 | 277 | 4767.17 | n | 624.0094 |  |  |  | 21453.7125 | 20370.4367 | 34185.15 | 115554.76 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-05-23 |  | 152 | 436230 | 15220 | 7.69 | 54 |  | 1338 | 20364.36 |  | 73.21 | 160 | 124 | 4 | 288 | 4383.36 | n | 562.7914 |  |  |  | 21230.895 | 20296.0642 | 35076.42 | 116447.23 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-05-30 |  | 167 | 452950 | 16720 | 7.56 | 56 |  | 1189 | 19880.08 |  | 65.71 | 149 | 126 | 5 | 280 | 4681.6 | n | 603.5753 |  |  |  | 20800.585 | 20429.1542 | 36797.66 | 114850.15 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-06-06 |  | 140 | 466890 | 13940 | 7.37 | 77.6 |  | 1327 | 18498.38 |  | 54.81 | 125 | 117 | 4 | 246 | 3429.24 | n | 443.5536 |  |  |  | 20119.7625 | 20448.3925 | 39520.95 | 114619.29 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-06-13 |  | 182 | 484550 | 17660 | 7.67 | 44.4 |  | 1087 | 19196.42 |  | 50.04 | 145 | 97 | 6 | 248 | 4379.68 | n | 560.9079 |  |  |  | 19484.81 | 20391.8525 | 42060.76 | 115297.77 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-06-20 |  | 148 | 499460 | 14910 | 7.62 | 37.6 |  | 1248 | 18607.68 |  | 60.94 | 138 | 100 | 6 | 244 | 3638.04 | n | 467.2753 |  |  |  | 19045.64 | 20404.5525 | 43817.44 | 115145.37 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-06-27 |  | 180 | 17430 | 17970 | 7.42 | 42.4 |  | 1199 | 21546.03 |  | 58.9 | 158 | 107 | 6 | 271 | 4869.87 | n | 623.6162 |  |  |  | 19462.1275 | 20541.5808 | 42151.49 | 113501.03 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-07-04 |  | 166 | 34050 | 16620 | 7.42 | 56 |  | 1214 | 20176.68 |  | 67.37 | 68.7698 | 156.0578 | 5.9796 | 230.8072 | 3836.0155 | n | 512.2761 |  |  |  | 19881.7025 | 20504.4042 | 40473.19 | 113947.15 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-07-11 |  | 196 | 53610 | 19560 | 7.47 | 47.2 |  | 1101 | 21535.56 |  | 68.24 | 72.6 | 123 | 6 | 201.6 | 3943.296 | n | 522.2951 |  |  |  | 20466.4875 | 20468.3367 | 38134.05 | 114379.96 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-07-18 |  | 166 | 70290 | 16680 | 7.56 | 58.8 |  | 1323 | 22067.64 |  | 58.02 | 161 | 122 | 9 | 292 | 4870.56 | n | 627.5704 |  |  |  | 21331.4775 | 20536.0042 | 34674.09 | 113567.95 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-07-25 |  | 152 | 85450 | 15160 | 7.6 | 53.2 |  | 1524 | 23103.84 |  | 80.61 | 107.692 | 184.0956 | 13.6 | 305.3876 | 4629.6765 | n | 615.3889 |  |  |  | 21720.93 | 20661.2142 | 33116.28 | 112065.43 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-08-01 |  | 155 | 100950 | 15500 | 7.58 | 61.2 |  | 1567 | 24288.5 |  | 69.31 | 104 | 351 | 6 | 461 | 7145.5 | n | 961.9831 |  |  |  | 22748.885 | 20916.7833 | 29004.46 | 108998.6 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-08-08 |  | 161 | 117080 | 16130 | 7.61 | 129.2 |  | 1193 | 19243.09 |  | 70.1 | 70 | 214 | 7 | 291 | 4693.83 | n | 631.7455 |  |  |  | 22175.7675 | 20709.0217 | 31296.93 | 111491.74 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-08-15 |  | 167 | 133780 | 16700 | 7.62 | 50.4 |  | 1218 | 20340.6 |  | 66.5 | 184 | 150 | 5 | 339 | 5661.3 | n | 728.35 |  |  |  | 21744.0075 | 20707.0417 | 33023.97 | 111515.5 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-08-22 |  | 124 | 146190 | 12410 | 7.54 | 65.2 |  | 1152 | 14296.32 |  | 71.9 | 111 | 157 | 10 | 278 | 3449.98 | n | 454.8715 |  |  |  | 19542.1275 | 20241.7283 | 41831.49 | 117099.26 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-08-29 |  | 149 | 161060 | 14870 | 7.57 | 43.6 |  | 1345 | 20000.15 |  | 54.5 | 56 | 260 | 8 | 324 | 4817.88 | n | 654.6936 |  |  |  | 18470.04 | 20366.8758 | 46119.84 | 115597.49 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-09-05 |  | 168 | 177910 | 16850 | 7.43 | 58 |  | 1190 | 20051.5 |  | 75.15 | 111 | 152 | 8 | 271 | 4566.35 | n | 600.5123 |  |  |  | 18672.1425 | 20438.1325 | 45311.43 | 114742.41 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-09-12 |  | 167 | 194620 | 16710 | 7.68 | 66.4 |  | 1182 | 19751.22 |  | 91.15 | 81 | 181 | 17 | 279 | 4662.09 | n | 626.9099 |  |  |  | 18524.7975 | 20533.4275 | 45900.81 | 113598.87 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-09-19 |  | 168 | 211330 | 16710 | 7.53 | 58 |  | 1079 | 18030.09 |  | 56.06 | 120 | 128 | 9 | 257 | 4294.47 | n | 560.6176 |  |  |  | 19458.24 | 20240.4325 | 42167.04 | 117114.81 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-09-26 |  | 157 | 227050 | 15720 | 7.65 | 64.4 |  | 1259 | 19791.48 |  | 82.2 | 83 | 196 | 7 | 286 | 4495.92 | n | 600.9187 |  |  |  | 19406.0725 | 20208.3325 | 42375.71 | 117500.01 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-10-03 |  | 154 | 242430 | 15380 | 7.41 | 49.2 |  | 1203 | 18502.14 |  | 73.36 | 145 | 150 | 11 | 306 | 4706.28 | n | 613.8561 |  |  |  | 19018.7325 | 19955.5475 | 43925.07 | 120533.43 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-10-10 |  | 157 | 258150 | 15720 | 7.77 | 48.8 |  | 1312 | 20624.64 |  | 86.23 | 150 | 132 | 6 | 288 | 4527.36 | n | 584.9611 |  |  |  | 19237.0875 | 19835.2975 | 43051.65 | 121976.43 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-10-17 |  | 158 | 273970 | 15820 | 7.52 | 70.4 |  | 1219 | 19284.58 |  | 75.05 | 137 | 156 | 9 | 302 | 4777.64 | n | 624.3395 |  |  |  | 19550.71 | 19517.0258 | 41797.16 | 125795.69 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-10-24 |  | 155 | 289470 | 15500 | 7.5 | 72 |  | 1249 | 19359.5 |  | 84.49 | 107 | 172 | 8.8 | 287.8 | 4460.9 | n | 589.947 |  |  |  | 19442.715 | 19106.2758 | 42229.14 | 130724.69 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-10-31 |  | 147 | 304130 | 14660 | 7.69 | 66.4 |  | 1277 | 18720.82 |  | 88.96 | 215 | 81.6 | 7 | 303.6 | 4450.776 | n | 559.4817 |  |  |  | 19497.385 | 19062.7533 | 42010.46 | 131246.96 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-11-07 |  | 149 | 319020 | 14890 | 7.66 | 60.4 |  | 1417 | 21099.13 |  | 84.2 | 204.7 | 110.53 | 6.4 | 321.63 | 4789.0707 | n | 608.1804 |  |  |  | 19616.0075 | 19125.9642 | 41535.97 | 130488.43 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-11-14 |  | 128 | 331880 | 12860 | 7.37 | 43.6 |  | 1328 | 17078.08 |  | 51.3 | 181 | 87 | 10 | 278 | 3575.08 | n | 454.3016 |  |  |  | 19064.3825 | 19357.7775 | 43742.47 | 127706.67 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-11-21 |  | 137 | 345140 | 13260 | 7.67 | 77.2 |  | 1407 | 18656.82 |  | 80.4 | 70 | 213 | 9 | 292 | 3871.92 | n | 521.769 |  |  |  | 18888.7125 | 19245.8333 | 44445.15 | 129050 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-11-28 |  | 156 | 360710 | 15570 | 7.59 | 43.6 |  | 1303 | 20287.71 |  | 81.2 | 262 | 94 | 5 | 361 | 5620.77 | n | 703.5262 |  |  |  | 19280.435 | 19265.5175 | 42878.26 | 128813.79 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-12-05 |  | 152 | 375940 | 15230 | 7.23 | 43.6 |  | 1362 | 20743.26 |  | 83 | 178 | 132 | 10 | 320 | 4873.6 | n | 627.5578 |  |  |  | 19191.4675 | 19348.1875 | 43234.13 | 127821.75 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-12-12 |  | 111 | 387040 | 11100 | 7.51 | 114 |  | 1239 | 13752.9 |  | 64.64 | 191 | 106 | 6 | 303 | 3363.3 | n | 427.4975 |  |  |  | 18360.1725 | 18991.755 | 46559.31 | 132098.94 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-12-19 |  | 125 | 399540 | 12500 | 7.49 | 50.4 |  | 1284 | 16050 |  | 88.47 | 175 | 144 | 4 | 323 | 4037.5 | n | 519.3031 |  |  |  | 17708.4675 | 18679.965 | 49166.13 | 135840.42 | 8000 | 30000 | 100 | 6 | 10 | 35000
2008-12-26 |  | 124 | 411930 | 12390 | 7.44 | 53.2 |  | 1373 | 17011.47 |  | 74.55 | 57 | 192 | 5 | 254 | 3147.06 | n | 424.2209 |  |  |  | 16889.4075 | 18555.7425 | 52442.37 | 137331.09 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-01-02 |  | 101 | 422100 | 10170 | 7.57 | 32.4 |  | 1340 | 13627.8 |  | 66.3 | 105 | 179 | 6 | 290 | 2949.3 | n | 389.9331 |  |  |  | 15110.5425 | 17972.6725 | 59557.83 | 144327.93 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-01-09 |  | 136 | 435690 | 13590 | 7.5 | 28.4 |  | 1295 | 17599.05 |  | 76.34 | 202 | 82 | 5 | 289 | 3927.51 | n | 493.8861 |  |  |  | 16072.08 | 17832.2117 | 55711.68 | 146013.46 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-01-16 |  | 107 | 446370 | 10680 | 7.3 | 64.4 |  | 1254 | 13392.72 |  | 46.72 | 90 | 218 | 9 | 317 | 3385.56 | n | 453.2093 |  |  |  | 15407.76 | 17334.98 | 58368.96 | 151980.24 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-01-23 |  | 104 | 456690 | 10320 | 7.1 | 22.3 |  | 993 | 10247.76 |  | 6.6 | 113 | 136 | 15 | 264 | 2724.48 | n | 358.9982 |  |  |  | 13716.8325 | 16628.8917 | 65132.67 | 160453.3 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-01-30 |  | 123 | 469050 | 12360 | 7.36 | 28.8 |  | 1308 | 16166.88 |  | 90.36 | 127 | 172 | 6 | 305 | 3769.8 | n | 494.4455 |  |  |  | 14351.6025 | 16217.8708 | 62593.59 | 165385.55 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-02-06 |  | 126 | 481650 | 12600 | 7.72 | 24 |  | 1364.2 | 17188.92 |  | 81.31 | 234 | 86 | 5 | 325 | 4095 | n | 513.1399 |  |  |  | 14249.07 | 16227.1075 | 63003.72 | 165274.71 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-02-13 |  | 120 | 493670 | 12020 | 7.67 | 35.2 |  | 1465 | 17609.3 |  | 85.19 | 237 | 97 | 4.5396 | 338.5396 | 4069.2456 | n | 511.271 |  |  |  | 15303.215 | 16139.8142 | 58787.14 | 166322.23 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-02-20 |  | 103 | 3830 | 10160 | 7.58 | 42.4 |  | 1536 | 15605.76 |  | 98.51 | 167 | 125 | 5 | 297 | 3017.52 | n | 387.2406 |  |  |  | 16642.715 | 15749.6517 | 53429.14 | 171004.18 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-02-27 |  | 98 | 13620 | 9790 | 7.51 | 54 |  | 1188 | 11630.52 |  | 81.43 | 139 | 126 | 12 | 277 | 2711.83 | n | 352.7225 |  |  |  | 15508.625 | 14990.2567 | 57965.5 | 180116.92 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-03-06 |  | 70 | 20600 | 6980 | 7.63 | 62.4 |  | 1440 | 10051.2 |  | 44.23 | 221 | 168 | 12 | 401 | 2798.98 | n | 360.605 |  |  |  | 13724.195 | 14681.7817 | 65103.22 | 183818.62 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-03-13 |  | 118 | 32390 | 11790 | 7.4 | 66.8 |  | 1210 | 14265.9 |  | 73.76 | 179 | 106 | 5 | 290 | 3419.1 | n | 435.2452 |  |  |  | 12888.345 | 14533.1067 | 68446.62 | 185602.72 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-03-20 |  | 110 | 43360 | 10970 | 7.5 | 76.4 |  | 1137 | 12472.89 |  | 64.41 | 7 | 183 | 128 | 318 | 3488.46 | n | 513.414 |  |  |  | 12105.1275 | 14154.8917 | 71579.49 | 190141.3 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-03-27 |  | 74 | 50780 | 7420 | 7.11 | 50 |  | 678 | 5030.76 |  | 4.37 | 20 | 65 | 12 | 97 | 719.74 | n | 98.939 |  |  |  | 10455.1875 | 13438.4717 | 78179.25 | 198738.34 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-04-03 |  | 108 | 61550 | 10770 | 7.08 | 40.4 |  | 760 | 8185.2 |  | 3.98 | 223 | 63 | 7.6 | 293.6 | 3162.072 | n | 394.6066 |  |  |  | 9988.6875 | 12653.9842 | 80045.25 | 208152.19 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-04-10 |  | 96 | 70530 | 8980 | 7.5 | 50 |  | 1738 | 15607.24 |  | 74.45 | 288 | 106 | 9 | 403 | 3618.94 | n | 454.4139 |  |  |  | 10324.0225 | 12838.5275 | 78703.91 | 205937.67 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-04-17 |  | 94 | 79790 | 9260 | 7.75 | 34.8 |  | 1763 | 16325.38 |  | 108 | 259 | 157 | 6 | 422 | 3907.72 | n | 497.4411 |  |  |  | 11287.145 | 13344.9958 | 74851.42 | 199860.05 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-04-24 |  | 104 | 90220 | 10430 | 7.77 | 67.6 |  | 1527 | 15926.61 |  | 91 | 262 | 138 | 5.59 | 405.59 | 4230.3037 | n | 535.8796 |  |  |  | 14011.1075 | 13324.9733 | 63955.57 | 200100.32 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-05-01 |  | 129 | 103120 | 12900 | 7.62 | 34.4 |  | 1383 | 17840.7 |  | 74.3515 | 243 | 140 | 5 | 388 | 5005.2 | n | 635.8083 |  |  |  | 16424.9825 | 13379.2883 | 54300.07 | 199448.54 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-05-08 |  | 83 | 111400 | 8280 | 7.71 | 66 |  | 1442 | 11939.76 |  | 104.27 | 171 | 208 | 6 | 385 | 3187.8 | n | 416.1424 |  |  |  | 15508.1125 | 12906.8267 | 57967.55 | 205118.08 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-05-15 |  | 87 | 120110 | 8710 | 7.78 | 64 |  | 1519 | 13230.49 |  | 102.58 | 214.8 | 188 | 16 | 418.8 | 3647.748 | n | 473.2725 |  |  |  | 14734.39 | 12708.8875 | 61062.44 | 207493.35 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-05-22 |  | 83 | 128460 | 8350 | 7.68 | 54.8 |  | 955.76 | 7980.596 |  | 38.77 | 67 | 171 | 7 | 245 | 2045.75 | n | 274.2683 |  |  |  | 12747.8865 | 12404.7272 | 69008.454 | 211143.274 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-05-29 |  | 87 | 137150 | 8690 | 7.66 | 46.8 |  | 874.49 | 7599.3181 |  | 30.42 | 88 | 161 | 9 | 258 | 2242.02 | n | 298.0237 |  |  |  | 10187.541 | 12200.4037 | 79249.8359 | 213595.1559 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-06-05 |  | 118 | 148960 | 11810 | 7.58 | 83.2 |  | 1215 | 14349.15 |  | 86.38 | 87.14 | 185.26 | 5.4 | 277.8 | 3280.818 | n | 436.6816 |  |  |  | 10789.8885 | 12207.3412 | 76840.4459 | 213511.9059 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-06-12 |  | 157 | 164620 | 15660 | 7.53 | 43.2 |  | 1230.25 | 19265.715 |  | 69.78 | 221.27 | 193.95 | 12.92 | 428.14 | 6704.6724 | n | 868.1903 |  |  |  | 12298.6948 | 12773.4099 | 70805.2209 | 206719.0809 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-06-19 |  | 119 | 176540 | 11920 | 7.68 | 55.2 |  | 1324.49 | 15787.9208 |  | 87.77 | 77.44 | 226.1 | 10.2424 | 313.7824 | 3740.2864 | n | 503.6811 |  |  |  | 14250.526 | 13669.84 | 62997.8961 | 195961.9201 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-06-26 |  | 103 | 186860 | 10320 | 7.71 | 68.8 |  | 1063.56 | 10975.9392 |  | 98.31 | 30.6 | 175.42 | 8.32 | 214.34 | 2211.9888 | n | 302.5415 |  |  |  | 15094.6812 | 13902.4016 | 59621.275 | 193171.1809 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-07-03 |  | 104 | 197260 | 10400 | 7.85 | 67.2 |  | 1105.7 | 11499.28 |  | 101.49 | 33 | 142 | 6.53 | 181.53 | 1887.912 | n | 256.7 |  |  |  | 14382.2138 | 13560.0716 | 62471.145 | 197279.1409 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-07-10 |  | 137 | 210990 | 13730 | 7.48 | 55.6 |  | 998.98 | 13715.9954 |  | 80.51 | 32.9652 | 148.66 | 4.18 | 185.8052 | 2551.1057 | n | 346.3192 |  |  |  | 12994.7838 | 13342.6229 | 68020.8646 | 199888.5255 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-07-17 |  | 166 | 227580 | 16590 | 7.57 | 35.2 |  | 1173.6 | 19470.024 |  | 62.72 | 85 | 188 | 7 | 280 | 4645.2 | n | 619.749 |  |  |  | 13915.3096 | 13637.9074 | 64338.7614 | 196345.1115 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-07-24 |  | 181 | 245680 | 18100 | 7.56 | 52.4 |  | 1088.16 | 19695.696 |  | 60.33 | 109 | 157 | 6 | 272 | 4923.2 | n | 647.4484 |  |  |  | 16095.2488 | 13792.4904 | 55619.0046 | 194490.1155 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-07-31 |  | 131 | 258750 | 13070 | 7.71 | 62.8 |  | 993.89 | 12990.1423 |  | 61.57 | 148 | 58 | 10 | 216 | 2823.12 | n | 357.5717 |  |  |  | 16467.9644 | 13880.0222 | 54128.1423 | 193439.7332 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-08-07 |  | 133 | 272070 | 13320 | 7.59 | 61.6 |  | 924.35 | 12312.342 |  | 78.87 | 72.8202 | 118.16 | 5.4276 | 196.4077 | 2616.151 | n | 345.861 |  |  |  | 16117.0511 | 13803.5099 | 55531.7957 | 194357.8812 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-08-14 |  | 129 | 284990 | 12920 | 7.78 | 48 |  | 1116.71 | 14427.8932 |  | 84.43 | 12 | 48 | 179 | 239 | 3087.88 | n | 476.67 |  |  |  | 14856.5184 | 14340.7847 | 60573.9265 | 187910.584 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-08-21 |  | 153 | 300270 | 15280 | 7.46 | 50.4 |  | 1073 | 16395.44 |  | 67.85 | 33 | 191 | 6 | 230 | 3514.4 | n | 479.6313 |  |  |  | 14031.4544 | 15073.7948 | 63874.1825 | 179114.4621 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-08-28 |  | 175 | 317760 | 17490 | 7.6 | 35.8 |  | 997 | 17437.53 |  | 61.91 | 62.48 | 164.56 | 5 | 232.04 | 4058.3796 | n | 543.7839 |  |  |  | 15143.3013 | 15331.1598 | 59426.7948 | 176026.0821 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-09-04 |  | 157 | 333530 | 15770 | 7.52 | 44.8 |  | 1067 | 16826.59 |  | 69.29 | 41.4 | 189.15 | 4.29 | 234.84 | 3703.4268 | n | 502.4796 |  |  |  | 16271.8633 | 15127.8994 | 54912.5468 | 178465.2071 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-09-11 |  | 174 | 350920 | 17390 | 7.67 | 69.6 |  | 1008 | 17529.12 |  | 66.79 | 26.6 | 206 | 12.9 | 245.5 | 4269.245 | n | 588.012 |  |  |  | 17047.17 | 15272.9993 | 51811.32 | 176724.0079 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-09-18 |  | 144 | 365410 | 14490 | 7.7 | 84.8 |  | 1182 | 17127.18 |  | 82.03 | 65.4999 | 180.9463 | 4.0508 | 250.497 | 3629.701 | n | 486.4453 |  |  |  | 17230.105 | 15785.6027 | 51079.58 | 170572.7671 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-09-25 |  | 164 | 381730 | 16320 | 7.66 | 70.8 |  | 1137 | 18555.84 |  | 71.78 | 65.306 | 174.9547 | 9.0687 | 249.3294 | 4069.055 | n | 547.1258 |  |  |  | 17509.6825 | 16373.6494 | 49961.27 | 163516.2071 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-10-02 |  | 130 | 394780 | 13050 | 7.64 | 72.4 |  | 1151 | 15020.55 |  | 47.15 | 52 | 199 | 6 | 257 | 3353.85 | n | 453.7733 |  |  |  | 17058.1725 | 16482.3623 | 51767.31 | 162211.6525 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-10-09 |  | 159 | 410880 | 16100 | 7.51 | 42.8 |  | 953 | 15343.3 |  | 39.2 | 63.4913 | 152.7225 | 6.517 | 222.7308 | 3585.9657 | n | 480.0282 |  |  |  | 16511.7175 | 16138.4686 | 53953.13 | 166338.3765 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-10-16 |  | 140 | 424460 | 13580 | 7.66 | 51.6 |  | 1292 | 17545.36 |  | 81.84 | 130 | 163 | 7 | 300 | 4074 | n | 533.3688 |  |  |  | 16616.2625 | 15959.274 | 53534.95 | 168488.7125 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-10-23 |  | 153 | 438740 | 14280 | 7.67 | 66 |  | 1031 | 14722.68 |  | 86.54 | 43 | 195 | 6 | 244 | 3484.32 | n | 473.2466 |  |  |  | 15657.9725 | 16103.6521 | 57368.11 | 166756.1748 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-10-30 |  | 137 | 452420 | 13680 | 7.72 | 42.8 |  | 1348 | 18440.64 |  | 74.65 | 105 | 190 | 5 | 300 | 4104 | n | 543.169 |  |  |  | 16512.995 | 16614.3436 | 53948.02 | 160627.8768 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-11-06 |  | 147 | 467190 | 14770 | 7.68 | 156.8 |  | 1190.65 | 17585.9005 |  | 88.72 | 110.2654 | 142.899 | 5.4263 | 258.5907 | 3819.3846 | n | 500.3357 |  |  |  | 17073.6451 | 16877.5109 | 51705.4195 | 157469.8695 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-11-13 |  | 110 | 476980 | 9790 | 7.44 | 71.2 |  | 1328.66 | 13007.5814 |  | 18.97 | 166 | 129 | 10 | 305 | 2985.95 | n | 385.2721 |  |  |  | 15939.2005 | 16595.1893 | 56243.1981 | 160857.7281 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-11-20 |  | 118 | 488300 | 11320 | 7.82 | 43.2 |  | 1654.3 | 18726.676 |  | 48.78 | 427.59 | 139.66 | 10 | 577.25 | 6534.47 | n | 816.5413 |  |  |  | 16940.1995 | 16702.6182 | 52239.2021 | 159568.5821 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-11-27 |  | 123 | 500700 | 12400 | 7.49 | 144.4 |  | 1415 | 17546 |  | 68.52 | 183 | 150 | 4 | 337 | 4178.8 | n | 537.3316 |  |  |  | 16716.5395 | 16762.569 | 53133.8421 | 158849.1721 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-12-04 |  | 116 | 12260 | 11560 | 7.72 | 93 |  | 1412.84 | 16332.4304 |  | 75.42 | 181 | 143 | 4 | 328 | 3791.68 | n | 486.9486 |  |  |  | 16403.1719 | 16662.8449 | 54387.3122 | 160045.8617 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-12-11 |  | 144 | 26630 | 14370 | 7.78 | 50 |  | 1441.61 | 20715.9357 |  | 81.94 | 239.9556 | 137.8337 | 4.6733 | 382.4627 | 5495.9887 | n | 697.9557 |  |  |  | 18330.2605 | 16961.9078 | 46678.9579 | 156457.106 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-12-18 |  | 136 | 40250 | 13620 | 7.78 | 33.2 |  | 1448 | 19721.76 |  | 85 | 223.1874 | 119.6833 | 4.9833 | 347.8541 | 4737.7724 | n | 600.613 |  |  |  | 18579.0315 | 17059.0678 | 45683.8739 | 155291.186 | 8000 | 30000 | 100 | 6 | 10 | 35000
2009-12-25 |  | 126 | 52880 | 12630 | 7.32 | 50 |  | 1569 | 19816.47 |  | 69.57 | 365 | 176 | 7 | 548 | 6921.24 | n | 873.9668 |  |  |  | 19146.649 | 17458.7278 | 43413.4039 | 150495.266 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-01-01 |  | 112 | 64010 | 11130 | 7.39 | 23 |  | 1498 | 16672.74 |  | 30.57 | 279.23 | 191.28 | 8.999 | 479.509 | 5336.9352 | n | 683.0961 |  |  |  | 19231.7264 | 17569.5145 | 43073.0943 | 149165.826 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-01-08 |  | 139 | 77990 | 13980 | 7.79 | 32 |  | 1513 | 21151.74 |  | 77.14 | 292 | 138 | 5 | 435 | 6081.3 | n | 767.1313 |  |  |  | 19340.6775 | 17870.0462 | 42637.29 | 145559.446 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-01-15 |  | 133 | 91170 | 13180 | 7.82 | 26.8 |  | 1424 | 18768.32 |  | 75.52 | 289.699 | 135.5436 | 6.0297 | 431.2723 | 5684.1684 | n | 717.2998 |  |  |  | 19102.3175 | 18207.1828 | 43590.73 | 141513.806 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-01-22 |  | 139 | 105050 | 13880 | 7.74 | 27.2 |  | 1558.4016 | 21630.6147 |  | 85.19 | 307 | 166 | 7 | 480 | 6662.4 | n | 844.8948 |  |  |  | 19555.8537 | 18473.0141 | 41776.5853 | 138323.8313 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-01-29 |  | 142 | 119250 | 14200 | 7.7 | 36.8 |  | 1460 | 20732 |  | 81.84 | 255 | 132 | 5 | 392 | 5566.4 | n | 704.5252 |  |  |  | 20570.6687 | 18735.189 | 37717.3253 | 135177.7318 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-02-05 |  | 125 | 131820 | 12570 | 7.71 | 40 |  | 1563 | 19646.91 |  | 52.04 | 306 | 138 | 6 | 450 | 5656.5 | n | 712.8399 |  |  |  | 20194.4612 | 19288.4664 | 39222.1553 | 128538.4032 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-02-12 |  | 128 | 144570 | 12750 | 7.82 | 53.52 |  | 1622 | 20680.5 |  | 77.43 | 285 | 149 | 5 | 439 | 5597.25 | n | 708.398 |  |  |  | 20672.5062 | 19451.2851 | 37309.9753 | 126584.5792 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-02-19 |  | 107 | 155300 | 10730 | 7.67 | 45.2 |  | 1506 | 16159.38 |  | 59.9 | 294.1 | 166.4 | 6 | 466.5 | 5005.545 | n | 635.4555 |  |  |  | 19304.6975 | 19335.7334 | 42781.21 | 127971.1992 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-02-26 |  | 143 | 169660 | 14360 | 7.85 | 32.8 |  | 1313 | 18854.68 |  | 61.81 | 256 | 99 | 8 | 363 | 5212.68 | n | 655.4278 |  |  |  | 18835.3675 | 19545.9209 | 44658.53 | 125448.9496 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-03-05 |  | 148 | 184470 | 14810 | 7.73 | 42 |  | 1298.85 | 19235.9685 |  | 72.83 | 232.8909 | 104.9485 | 4.7222 | 342.5617 | 5073.3383 | n | 639.4145 |  |  |  | 18732.6321 | 19422.5903 | 45069.4715 | 126928.9168 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-03-12 |  | 164 | 200840 | 16370 | 7.56 | 33.6 |  | 1274.49 | 20863.4013 |  | 67.95 | 212.9268 | 118.1686 | 11.7461 | 342.8415 | 5612.3152 | n | 716.1614 |  |  |  | 18778.3574 | 19517.727 | 44886.5702 | 125787.2755 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-03-19 |  | 145 | 215340 | 14500 | 7.64 | 34.8 |  | 1384 | 20068 |  | 75.52 | 187 | 133 | 9 | 329 | 4770.5 | n | 612.7698 |  |  |  | 19755.5124 | 19538.6879 | 40977.9502 | 125535.7455 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-03-26 |  | 159 | 231250 | 15910 | 7.68 | 44 |  | 1301.5 | 20706.865 |  | 66.6 | 222.7833 | 140.3696 | 11.4246 | 374.5775 | 5959.5275 | n | 762.9392 |  |  |  | 20218.5587 | 19874.865 | 39125.7652 | 121501.6205 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-04-02 |  | 129 | 244160 | 12910 | 7.67 | 29.2 |  | 1398 | 18048.18 |  | 65.64 | 176 | 29 | 19 | 224 | 2891.84 | n | 363.25 |  |  |  | 19921.6116 | 19616.235 | 40313.5537 | 124605.1805 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-04-09 |  | 169 | 261170 | 17010 | 7.52 | 26.4 |  | 1052.24 | 17898.6024 |  | 61.43 | 159.8053 | 99.8744 | 19.9374 | 279.6171 | 4756.2869 | n | 615.3248 |  |  |  | 19180.4119 | 19543.7585 | 43278.3526 | 125474.8981 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-04-16 |  | 148 | 275920 | 14750 | 7.53 | 36.4 |  | 1145 | 16888.75 |  | 64.97 | 171 | 124 | 23 | 318 | 4690.5 | n | 609.9244 |  |  |  | 18385.5994 | 19148.6031 | 46457.6026 | 130216.7628 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-04-23 |  | 160 | 291940 | 16020 | 7.54 | 53.2 |  | 981 | 15715.62 |  | 72.26 | 80 | 117 | 26 | 223 | 3572.46 | n | 480.1896 |  |  |  | 17137.7881 | 18730.5714 | 51448.8476 | 135233.1428 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-04-30 |  | 158 | 307740 | 15800 | 7.58 | 74 |  | 960 | 15168 |  | 66.12 | 39.376 | 162.9681 | 24.9559 | 227.3 | 3591.3397 | n | 494.8115 |  |  |  | 16417.7431 | 18357.3289 | 54329.0276 | 139712.0528 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-05-07 |  | 176 | 325330 | 17590 | 7.5 | 65.2 |  | 1056 | 18575.04 |  | 63.63 | 121.4212 | 88.92 | 24.8813 | 235.2225 | 4137.5643 | n | 542.8005 |  |  |  | 16586.8525 | 18181.8739 | 53652.59 | 141817.5128 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-05-14 |  | 163 | 341630 | 16300 | 7.52 | 59.6 |  | 1102 | 17962.6 |  | 68.42 | 144 | 128 | 28 | 300 | 4890 | n | 643.5092 |  |  |  | 16855.315 | 18332.1423 | 52578.74 | 140014.2928 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-05-21 |  | 146 | 356270 | 14640 | 7.28 | 80 |  | 1024 | 14991.36 |  | 40.73 | 65.79 | 126.9467 | 20.0919 | 212.8285 | 3115.8095 | n | 420.198 |  |  |  | 16674.25 | 18010.1989 | 53303 | 143877.6128 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-05-28 |  | 170 | 373290 | 17020 | 7.59 | 69.6 |  | 1066 | 18143.32 |  | 68.9 | 24 | 190 | 33 | 247 | 4203.94 | n | 587.5095 |  |  |  | 17418.08 | 17919.1449 | 50327.68 | 144970.2613 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-06-04 |  | 167 | 389920 | 16630 | 7.46 | 67.6 |  | 1092 | 18159.96 |  | 58.7 | 57 | 92 | 17 | 166 | 2760.58 | n | 370.9924 |  |  |  | 17314.31 | 17693.8581 | 50742.76 | 147673.7026 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-06-11 |  | 180 | 407930 | 18010 | 7.55 | 43.6 |  | 992.47 | 17874.3847 |  | 66.22 | 72.7441 | 93.5802 | 24.6307 | 190.955 | 3439.0997 | n | 461.7673 |  |  |  | 17292.2562 | 17511.0568 | 50830.9753 | 149867.3179 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-06-18 |  | 171 | 425100 | 17170 | 7.29 | 46.4 |  | 975.93 | 16756.7181 |  | 69 | 37.1981 | 120.4252 | 26.522 | 184.1453 | 3161.7745 | n | 436.3165 |  |  |  | 17733.5957 | 17181.8779 | 49065.6172 | 153817.4648 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-06-25 |  | 164 | 441450 | 16350 | 7.56 | 61.2 |  | 1098.11 | 17954.0985 |  | 69.96 | 51.7133 | 179.568 | 25.5749 | 256.8561 | 4199.5976 | n | 575.4222 |  |  |  | 17686.2903 | 17174.0378 | 49254.8387 | 153911.5463 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-07-02 |  | 150 | 456530 | 15080 | 7.55 | 54.8 |  | 1042 | 15713.36 |  | 70.82 | 22 | 140 | 18 | 180 | 2714.4 | n | 376.0194 |  |  |  | 17074.6403 | 16991.9343 | 51701.4387 | 156096.7887 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-07-09 |  | 156 | 472130 | 15600 | 7.56 | 46 |  | 1080.16 | 16850.496 |  | 69.48 | 13 | 166 | 19 | 198 | 3088.8 | n | 430.9177 |  |  |  | 16818.6682 | 16988.7464 | 52725.3274 | 156135.0427 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-07-16 |  | 166 | 488640 | 16510 | 7.53 | 54 |  | 1109.92 | 18324.7792 |  | 66.12 | 57.7936 | 182.293 | 22.1169 | 262.2036 | 4328.9806 | n | 590.1146 |  |  |  | 17210.6834 | 17206.1764 | 51157.2663 | 153525.8835 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-07-23 |  | 162 | 4920 | 16280 | 7.57 | 58.4 |  | 1186.66 | 19318.8248 |  | 73.11 | 75.4465 | 165.2902 | 34.4987 | 275.2353 | 4480.8308 | n | 610.3503 |  |  |  | 17551.865 | 17552.0784 | 49792.54 | 149375.0587 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-07-30 |  | 151 | 19940 | 15020 | 7.66 | 61.6 |  | 1111.11 | 16688.8722 |  | 91.16 | 84.26 | 174.8 | 38.4 | 297.46 | 4467.8492 | n | 608.1809 |  |  |  | 17795.7431 | 17394.8978 | 48817.0278 | 151261.2265 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-08-06 |  | 151 | 35140 | 15200 | 7.37 | 42.4 |  | 1088 | 16537.6 |  | 79.47 | 56.8467 | 164.6339 | 38.6828 | 260.1633 | 3954.4822 | n | 544.8822 |  |  |  | 17717.519 | 17276.1478 | 49129.9238 | 152686.2265 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-08-13 |  | 149 | 50520 | 15380 | 7.6 | 50.4 |  | 1123 | 17271.74 |  | 69.75 | 88 | 180 | 15 | 283 | 4352.54 | n | 582.8128 |  |  |  | 17454.2592 | 17466.1795 | 50182.963 | 150405.8465 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-08-20 |  | 92 | 66650 | 16130 | 7.61 | 57.6 |  | 1140 | 18388.2 |  | 75.26 | 72 | 121 | 6 | 199 | 3209.87 | n | 425.0768 |  |  |  | 17221.6031 | 17486.5861 | 51113.5878 | 150160.9665 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-08-27 |  | 147 | 82970 | 16320 | 7.62 | 65.6 |  | 1130 | 18441.6 |  | 68.25 | 10 | 141 | 52 | 203 | 3312.96 | n | 475.0581 |  |  |  | 17659.785 | 17510.0561 | 49360.86 | 149879.3265 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-09-03 |  | 137 | 97030 | 14060 | 7.24 | 56.8 |  | 1031.25 | 14499.375 |  | 66.66 | 70.6834 | 128.2731 | 17.8049 | 216.7614 | 3047.6654 | n | 409.1942 |  |  |  | 17150.2287 | 17228.8053 | 51399.085 | 153254.3362 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-09-10 |  | 147 | 111510 | 14480 | 7.58 | 112.4 |  | 1007 | 14581.36 |  | 52.17 | 51 | 182 | 17 | 250 | 3620 | n | 493.2745 |  |  |  | 16477.6338 | 17047.5255 | 54089.465 | 155429.6943 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-09-17 |  | 154 | 126860 | 15350 | 7.61 | 64.8 |  | 1148 | 17621.8 |  | 69.28 | 53.554 | 179.2663 | 24.6009 | 257.4212 | 3951.4147 | n | 540.5614 |  |  |  | 16286.0338 | 17019.8339 | 54855.865 | 155761.9928 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-09-24 |  | 153 | 142170 | 15310 | 7.55 | 50 |  | 1047 | 16029.57 |  | 76.48 | 40.7868 | 158.77 | 28.4729 | 228.0297 | 3491.1344 | n | 481.8063 |  |  |  | 15683.0263 | 17046.1848 | 57267.895 | 155445.7828 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-10-01 |  | 144 | 156570 | 14400 | 7.32 | 53.2 |  | 1107 | 15940.8 |  | 77.13 | 102.9168 | 133.3384 | 40.4057 | 276.6609 | 3983.9167 | n | 537.112 |  |  |  | 16043.3825 | 16970.3768 | 55826.47 | 156355.4788 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-10-08 |  | 119 | 168520 | 11950 | 7.14 | 71.2 |  | 1127 | 13467.65 |  | 61.43 | 114.7608 | 102.324 | 31.1879 | 248.2727 | 2966.8585 | n | 393.5652 |  |  |  | 15764.955 | 16565.616 | 56940.18 | 161212.608 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-10-15 |  | 120 | 180470 | 11950 | 7.7 | 65.6 |  | 1236 | 14770.2 |  | 74.42 | 84.3302 | 188.5044 | 22.8906 | 295.7252 | 3533.9164 | n | 476.8488 |  |  |  | 15052.055 | 16186.5639 | 59791.78 | 165761.2328 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-10-22 |  | 151 | 195550 | 15080 | 7.5 | 53.2 |  | 1211 | 18261.88 |  | 87.94 | 192 | 144 | 23 | 359 | 5413.72 | n | 703.2694 |  |  |  | 15610.1325 | 16317.6479 | 57559.47 | 164188.225 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-10-29 |  | 158 | 211320 | 15770 | 7.59 | 51.2 |  | 1190 | 18766.3 |  | 74.67 | 123 | 191 | 35 | 349 | 5503.73 | n | 738.4362 |  |  |  | 16316.5075 | 16503.3729 | 54733.97 | 161959.525 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-11-05 |  | 145 | 225800 | 14480 | 7.59 | 46 |  | 1192 | 17260.16 |  | 66.73 | 88 | 188 | 31 | 307 | 4445.36 | n | 602.0469 |  |  |  | 17264.635 | 16502.4079 | 50941.46 | 161971.105 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-11-12 |  | 161 | 241940 | 16140 | 7.6 | 65.6 |  | 1189 | 19190.46 |  | 77.38 | 173.6519 | 130.5752 | 39.8227 | 344.0499 | 5552.9649 | n | 730.9266 |  |  |  | 18369.7 | 16569.2629 | 46521.2 | 161168.845 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-10-19 |  | 161 | 257990 | 16050 | 7.74 | 44 |  | 1308 | 20993.4 |  | 73.31 | 201 | 177 | 19 | 397 | 6371.85 | n | 828.8767 |  |  |  | 19052.58 | 16781.9129 | 43789.68 | 158617.045 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-11-26 |  | 168 | 274840 | 16850 | 7.91 | 43.2 |  | 1283 | 21618.55 |  | 81.35 | 200 | 153 | 21 | 374 | 6301.9 | n | 817.5427 |  |  |  | 19765.6425 | 17375.1775 | 40937.43 | 151497.87 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-12-03 |  | 169 | 291740 | 16900 | 7.7 | 147.2 |  | 1226 | 20719.4 |  | 69.63 | 146 | 164 | 20 | 330 | 5577 | n | 733.8174 |  |  |  | 20630.4525 | 17886.6808 | 37478.19 | 145359.83 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-12-10 |  | 168 | 308080 | 16340 | 7.86 | 59.6 |  | 712 | 11634.08 |  | 53.36 | 99.7348 | 74.9623 | 24.4198 | 199.1169 | 3253.5708 | n | 428.9989 |  |  |  | 18741.3575 | 17387.7042 | 45034.57 | 151347.55 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-12-17 |  | 145 | 322560 | 14480 | 7.45 | 36.4 |  | 1359 | 19678.32 |  | 58.59 | 271.3174 | 136.4767 | 31.9416 | 439.7357 | 6367.3732 | n | 818.4519 |  |  |  | 18412.5875 | 17691.7667 | 46349.65 | 147698.8 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-12-24 |  | 161 | 337870 | 15310 | 7.61 | 56.4 |  | 1444 | 22107.64 |  | 74.09 | 254.8601 | 142.9542 | 28.8231 | 426.6374 | 6531.818 | n | 841.28 |  |  |  | 18534.86 | 18205.67 | 45860.56 | 141531.96 | 8000 | 30000 | 100 | 6 | 10 | 35000
2010-12-31 |  | 144 | 352250 | 14380 | 7.6 | 37.2 |  | 1549 | 22274.62 |  | 84.22 | 289 | 86 | 29 | 404 | 5809.52 | n | 735.8053 |  |  |  | 18923.665 | 18939.5842 | 44305.34 | 132724.99 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-01-07 |  | 147 | 366930 | 14680 | 7.6 | 28.4 |  | 1478 | 21697.04 |  | 73.55 | 217 | 99 | 75 | 391 | 5739.88 | n | 759.8008 |  |  |  | 21439.405 | 19516.8208 | 34242.38 | 125798.15 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-01-14 |  | 142 | 381150 | 14220 | 7.54 | 39.2 |  | 1637 | 23278.14 |  | 83.12 | 83.2432 | 380.3714 | 0 | 463.6145 | 6592.5988 | n | 891.3873 |  |  |  | 22339.36 | 19934.8425 | 30642.56 | 120781.89 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-01-21 |  | 148 | 395950 | 14800 | 7.79 | 81.2 |  | 1879 | 27809.2 |  | 98.5 | 421 | 237 | 0 | 659 | 9753.2 | n | 1231.7678 |  |  |  | 23764.75 | 20688.4175 | 24941 | 111738.99 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-01-28 |  | 127 | 408680 | 12730 | 7.5 | 37.6 |  | 1426 | 18152.98 |  | 101.8 | 178 | 135 | 8 | 321 | 4086.33 | n | 525.741 |  |  |  | 22734.34 | 20762.8192 | 29062.64 | 110846.17 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-02-04 |  | 107 | 419410 | 10730 | 7.63 | 66.8 |  | 1433 | 15376.09 |  | 87.45 | 244.7821 | 159.606 | 10.1703 | 414.5584 | 4448.2114 | n | 569.2304 |  |  |  | 21154.1025 | 20444.955 | 35383.59 | 114660.54 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-02-11 |  | 150 | 434360 | 14950 | 7.66 | 53.2 |  | 1271 | 19001.45 |  | 101.7 | 140.7911 | 154.4453 | 3.7611 | 298.9975 | 4470.0128 | n | 580.9614 |  |  |  | 20084.93 | 20278.9592 | 39660.28 | 116652.49 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-02-18 |  | 140 | 448420 | 14060 | 7.74 | 49 |  | 1282 | 18024.92 |  | 87.7 | 116.3577 | 88.1325 | 0 | 204.4902 | 2875.1318 | n | 367.5217 |  |  |  | 17638.86 | 19979.49 | 49444.56 | 120246.12 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-02-25 |  | 126 | 460760 | 12340 | 7.64 | 46.8 |  | 1231 | 15190.54 |  | 114.2 | 119 | 139 | 3 | 261 | 3220.74 | n | 419.4292 |  |  |  | 16898.25 | 19518.7517 | 52407 | 125774.98 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-03-04 |  | 148 | 475010 | 14250 | 7.91 | 60.4 |  | 1454 | 20719.5 |  | 135.7 | 191.988 | 134.5165 | 3.3774 | 329.8819 | 4700.8169 | n | 600.8122 |  |  |  | 18234.1025 | 20275.87 | 47063.59 | 116689.56 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-03-11 |  | 123 | 487250 | 12240 | 7.61 | 52.8 |  | 1353 | 16560.72 |  | 102.1 | 178.1906 | 154.6483 | 7.1036 | 339.9425 | 4160.8956 | n | 537.3538 |  |  |  | 17623.92 | 20016.07 | 49504.32 | 119807.16 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-03-18 |  | 136 | 910 | 13660 | 7.58 | 66.8 |  | 1449 | 19793.34 |  | 129.3 | 169 | 179 | 8 | 356 | 4862.96 | n | 632.7511 |  |  |  | 18066.025 | 19823.2117 | 47735.9 | 122121.46 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-03-25 |  | 148 | 15710 | 14800 | 7.48 | 64 |  | 1361 | 20142.8 |  | 131.166 | 149.2765 | 194.2765 | 32.0015 | 375.5544 | 5558.2053 | n | 739.13 |  |  |  | 19304.09 | 19645.56 | 42783.64 | 124253.28 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-04-01 |  | 140 | 29700 | 13990 | 7.68 | 57.6 |  | 1351 | 18900.49 |  | 134.568 | 142.9907 | 125.6409 | 33.737 | 302.3686 | 4230.1362 | n | 558.9635 |  |  |  | 18849.3375 | 19412.5142 | 44602.65 | 127049.83 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-04-08 |  | 134 | 43100 | 13400 | 7.69 | 70 |  | 1298 | 17393.2 |  | 115.29 | 135.2366 | 155.8134 | 24.5491 | 315.599 | 4229.0271 | n | 559.1884 |  |  |  | 19057.4575 | 18922.1025 | 43770.17 | 132934.77 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-04-15 |  | 147 | 57760 | 14660 | 7.73 | 44.4 |  | 1279 | 18750.14 |  | 134.568 | 106.9578 | 183.4275 | 35.9656 | 326.3509 | 4784.3045 | n | 645.2091 |  |  |  | 18796.6575 | 18167.1808 | 44813.37 | 141993.83 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-04-22 |  | 144 | 72180 | 14420 | 7.43 | 61.6 |  | 1309 | 18875.78 |  | 137.214 | 9.8623 | 232.0183 | 13.9704 | 255.851 | 3689.371 | n | 513.1958 |  |  |  | 18479.9025 | 18227.4142 | 46080.39 | 141271.03 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-04-29 |  | 127 | 84850 | 12670 | 7.4 | 56 |  | 1243 | 15748.81 |  | 117.558 | 13 | 182 | 25 | 220 | 2787.4 | n | 390.3154 |  |  |  | 17691.9825 | 18258.4742 | 49232.07 | 140898.31 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-05-06 |  | 134 | 98190 | 13340 | 7.5 | 59.6 |  | 1244.05 | 16595.627 |  | 117.558 | 32.4332 | 237.4828 | 16.1086 | 286.0246 | 3815.5678 | n | 525.4824 |  |  |  | 17492.5893 | 18057.9889 | 50029.643 | 143304.133 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-05-13 |  | 131 | 111250 | 13060 | 7.46 | 67.6 |  | 1163.47 | 15194.9182 |  | 90.342 | 56.8703 | 238.5097 | 27.5987 | 322.9786 | 4218.1009 | n | 578.6482 |  |  |  | 16603.7838 | 17822.1554 | 53584.8648 | 146134.1348 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-05-20 |  | 134 | 124650 | 13400 | 7.54 | 78.4 |  | 1454.24 | 19486.816 |  | 68.04 | 68.1539 | 200.3589 | 41.1817 | 309.6944 | 4149.9054 | n | 570.2319 |  |  |  | 16756.5428 | 18180.1784 | 52973.8288 | 141837.8588 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-05-27 |  | 140 | 138640 | 13990 | 7.62 | 64.4 |  | 1449 | 20271.51 |  | 130.32 | 63 | 272 | 40 | 375 | 5246.25 | n | 722.9782 |  |  |  | 17887.2178 | 18142.8459 | 48451.1288 | 142285.8488 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-06-03 |  | 133 | 151970 | 13330 | 7.68 | 59.2 |  | 1481.8 | 19752.394 |  | 127.764 | 74.9303 | 207.9839 | 34.6727 | 317.5869 | 4233.4334 | n | 578.1886 |  |  |  | 18676.4096 | 18408.8188 | 45294.3618 | 139094.1748 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-06-10 |  | 128 | 164730 | 12760 | 7.6 | 81.2 |  | 1478.3058 | 18863.1818 |  | 124.362 | 14.8642 | 249.4865 | 26.1358 | 290.4865 | 3706.6079 | n | 517.6307 |  |  |  | 19593.4755 | 18331.3056 | 41626.0982 | 140024.333 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-08-17 |  | 142 | 179010 | 14280 | 7.54 | 72.4 |  | 1440.7 | 20573.196 |  | 139.104 | 122.1567 | 253.479 | 0 | 375.6357 | 5364.0784 | n | 710.4693 |  |  |  | 19865.0705 | 18367.1719 | 40539.7182 | 139593.937 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-06-24 |  | 135 | 192570 | 13560 | 7.7 | 58.4 |  | 1446 | 19607.76 |  | 123.228 | 95.6445 | 269.8548 | 34.8195 | 400.3188 | 5428.3233 | n | 738.3881 |  |  |  | 19699.133 | 18426.1111 | 41203.4682 | 138886.667 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-07-01 |  | 129 | 205510 | 12940 | 7.59 | 67.6 |  | 1456 | 18840.64 |  | 101.304 | 36.4118 | 292.6375 | 19.688 | 348.7374 | 4512.662 | n | 622.2688 |  |  |  | 19471.1945 | 18546.7311 | 42115.2222 | 137439.227 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-07-08 |  | 136 | 218730 | 13220 | 7.49 | 66.8 |  | 1252 | 16551.44 |  | 110.376 | 33.2864 | 216.5836 | 30.5561 | 280.4261 | 3707.2332 | n | 514.5429 |  |  |  | 18893.259 | 18363.5061 | 44426.964 | 139637.927 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-07-15 |  | 114 | 230140 | 11410 | 7.55 | 66 |  | 1017 | 11603.97 |  | 82.404 | 95 | 222 | 23 | 340 | 3879.4 | n | 523.0452 |  |  |  | 16650.9525 | 17757.5219 | 53396.19 | 146909.737 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-07-22 |  | 166 | 246740 | 16600 | 7.78 | 86 |  | 1375 | 22825 |  | 110.376 | 156.6143 | 217.0956 | 28.617 | 402.327 | 6678.6275 | n | 887.0654 |  |  |  | 17455.2625 | 18347.2044 | 50178.95 | 139833.547 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-07-29 |  | 141 | 260840 | 14100 | 7.41 | 75.6 |  | 1397 | 19697.7 |  | 97.14 | 108.2372 | 194.7139 | 28.9508 | 331.9019 | 4679.8166 | n | 628.8636 |  |  |  | 17669.5275 | 18605.7105 | 49321.89 | 136731.474 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-08-05 |  | 116 | 272410 | 11570 | 7.42 | 105.2 |  | 1419 | 16417.83 |  | 104 | 38 | 277 | 29 | 344 | 3980.08 | n | 550.8444 |  |  |  | 17636.125 | 18707.6198 | 49455.5 | 135508.5622 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-08-12 |  | 53 | 274660 | 2250 | 7.1 | 76.4 |  | 748 | 1683 |  | 21.82 | 166.3862 | 115.9303 | 6.3627 | 288.6792 | 649.5282 | n | 83.2565 |  |  |  | 15155.8825 | 17223.9685 | 59376.47 | 153312.3782 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-08-19 |  | 98 | 284470 | 9810 | 7.65 | 56 |  | 1039 | 10192.59 |  | 26.37 | 161 | 221 | 22.5 | 404.5 | 3968.145 | n | 525.0244 |  |  |  | 11997.78 | 16384.0585 | 72008.88 | 163391.2982 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-08-26 |  | 139 | 298020 | 13550 | 7.49 | 60.4 |  | 2201 | 29823.55 |  | 104.7 | 510 | 208 | 51 | 769 | 10419.95 | n | 1328.7702 |  |  |  | 14529.2425 | 17223.3215 | 61883.03 | 153320.1422 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-09-02 |  | 191 | 317090 | 19070 | 7.75 | 51.2 |  | 1268 | 24180.76 |  | 84.8 | 322 | 164 | 24 | 510 | 9725.7 | n | 1241.9272 |  |  |  | 16469.975 | 17666.453 | 54120.1 | 148002.564 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-09-09 |  | 189 | 336060 | 18970 | 7.67 | 59.2 |  | 1209 | 22934.73 |  | 100.9 | 321 | 127 | 2 | 450 | 8536.5 | n | 1068.695 |  |  |  | 21782.9075 | 17863.2475 | 32868.37 | 145641.03 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-09-16 |  | 182 | 354160 | 18100 | 7.42 | 72 |  | 1120 | 20272 |  | 47.7 | 214.7731 | 101.0206 | 7.9257 | 323.7194 | 5859.321 | n | 741.6946 |  |  |  | 24302.76 | 17918.6008 | 22788.96 | 144976.79 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-09-23 |  | 160 | 370100 | 15940 | 7.78 | 63.2 |  | 1424 | 22698.56 |  | 121 | 177.5757 | 100.1671 | 19.1893 | 296.9321 | 4733.0975 | n | 609.2404 |  |  |  | 22521.5125 | 18240.0942 | 29913.95 | 141118.87 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-09-30 |  | 157 | 385850 | 15750 | 7.37 | 58.4 |  | 1339 | 21089.25 |  | 87.82 | 259.8595 | 58.3501 | 7.2587 | 325.4683 | 5126.1253 | n | 635.5203 |  |  |  | 21748.635 | 18618.245 | 33005.46 | 136581.06 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-10-07 |  | 159 | 401720 | 15870 | 7.62 | 65.2 |  | 1265 | 20075.55 |  | 103 | 249.5142 | 50.5674 | 14.2152 | 314.2968 | 4987.8901 | n | 621.362 |  |  |  | 21033.84 | 19324.21 | 35864.64 | 128109.48 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-10-14 |  | 181 | 419220 | 17500 | 7.92 | 62.8 |  | 1516 | 26530 |  | 121 | 217.3777 | 122.4951 | 15.6544 | 355.5272 | 6221.7262 | n | 796.4185 |  |  |  | 22598.34 | 19632.96 | 29606.64 | 124404.48 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-10-21 |  | 106 | 432250 | 13030 | 7.64 | 76 |  | 1652 | 21525.56 |  | 107.7 | 279 | 191 | 10 | 480 | 6254.4 | n | 800.9418 |  |  |  | 22305.09 | 19785.2817 | 30779.64 | 122576.62 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-10-28 |  | 114 | 443610 | 11360 | 7.91 | 72.4 |  | 1873 | 21277.28 |  | 72.56 | 19 | 181 | 102 | 302 | 3430.72 | n | 497.3 |  |  |  | 22352.0975 | 20190.2358 | 30591.61 | 117717.17 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-11-04 |  | 125 | 456100 | 12490 | 8.09 | 84.4 |  | 2036 | 25429.64 |  | 181.3 | 256.9366 | 174.5305 | 66.9532 | 498.4202 | 6225.2685 | n | 820.7299 |  |  |  | 23690.62 | 22169.1225 | 25237.52 | 93970.53 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-11-11 |  | 135 | 469570 | 13470 | 7.54 | 63.2 |  | 1568 | 21120.96 |  | 98.8 | 123.5722 | 196.0024 | 29.3004 | 348.875 | 4699.3456 | n | 628.6458 |  |  |  | 22338.36 | 23079.82 | 30646.56 | 83042.16 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-11-18 |  | 124 | 482030 | 12460 | 7.82 | 68 |  | 1540 | 19188.4 |  | 97.97 | 169.8419 | 115.6851 | 28.2318 | 313.7588 | 3909.4351 | n | 509.6336 |  |  |  | 21754.07 | 22193.5575 | 32983.72 | 93677.31 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-11-25 |  | 130 | 495010 | 12980 | 7.96 | 66 |  | 1687 | 21897.26 |  | 72.28 | 155 | 160 | 60 | 375 | 4867.5 | n | 653.9376 |  |  |  | 21909.065 | 22003.2658 | 32363.74 | 95960.81 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-12-02 |  | 108 | 5830 | 10820 | 7.88 | 80.4 |  | 1952.1 | 21121.722 |  | 164.4 | 184.3088 | 141.3999 | 48.604 | 374.3127 | 4050.0634 | n | 535.3234 |  |  |  | 20832.0855 | 21852.1818 | 36671.658 | 97773.818 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-12-09 |  | 126 | 17580 | 11750 | 7.59 | 64.4 |  | 1554 | 18259.5 |  | 81.4 | 149.5858 | 150.9686 | 21.0707 | 321.6251 | 3779.0949 | n | 496.0402 |  |  |  | 20116.7205 | 21684.4735 | 39533.118 | 99786.318 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-12-16 |  | 109 | 28560 | 10980 | 8.07 | 97 |  | 2193 | 24079.14 |  | 152.44 | 144.3355 | 356.3893 | 53.3381 | 554.0628 | 6083.6095 | n | 826.2949 |  |  |  | 21339.4055 | 21799.5218 | 34642.378 | 98405.738 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-12-23 |  | 134 | 41940 | 13380 | 7.53 | 62.8 |  | 1914 | 25609.32 |  | 175.5 | 159.7508 | 176.3221 | 68.3788 | 404.4517 | 5411.5632 | n | 730.0081 |  |  |  | 22267.4205 | 22176.1943 | 30930.318 | 93885.668 | 8000 | 30000 | 100 | 6 | 10 | 35000
2011-12-30 |  | 156 | 57500 | 15560 | 7.67 | 43.6 |  | 1529 | 23791.24 |  | 141.7 | 161.8591 | 108.3201 | 61.8697 | 332.0489 | 5166.6807 | n | 689.9065 |  |  |  | 22934.8 | 22485.8352 | 28260.8 | 90169.978 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-01-06 |  | 133 | 70860 | 13360 | 7.71 | 46 |  | 1377 | 18396.72 |  | 78.63 | 144.9726 | 145.5178 | 27.8346 | 318.3249 | 4252.8212 | n | 561.0807 |  |  |  | 22969.105 | 21808.0618 | 28123.58 | 98303.258 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-01-13 |  | 135 | 84380 | 13520 | 7.75 | 45.2 |  | 1579.9 | 21360.248 |  | 108.7 | 184.9939 | 179.5662 | 45.603 | 410.1632 | 5545.4061 | n | 735.0122 |  |  |  | 22289.382 | 21794.2858 | 30842.472 | 98468.57 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-01-20 |  | 154 | 99140 | 14760 | 7.59 | 78 |  | 1530.4 | 22588.704 |  | 139.3 | 81.7861 | 169.5687 | 47.0224 | 298.3772 | 4404.047 | n | 603.0606 |  |  |  | 21534.228 | 21903.5712 | 33863.088 | 97157.146 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-01-27 |  | 143 | 113500 | 14360 | 7.82 | 33.2 |  | 1407 | 20204.52 |  | 89.68 | 156 | 198 | 31 | 385 | 5528.6 | n | 733.8063 |  |  |  | 20637.548 | 21468.1445 | 37449.808 | 102382.266 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-02-03 | 9:15 | 127 | 126120 | 12620 | 7.81 | 34.8 |  | 1340 | 16910.8 |  | 96.59 | 187.1321 | 152.4045 | 28.7421 | 368.2787 | 4647.6768 | n | 607.5573 |  |  |  | 20266.068 | 21117.2978 | 38935.728 | 106592.426 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-02-10 | 9:30 | 133 | 139490 | 13370 | 7.7 | 51.6 |  | 1517 | 20282.29 |  | 96.5 | 197.1925 | 183.7599 | 30.5827 | 411.535 | 5502.2231 | n | 721.8289 |  |  |  | 19996.5785 | 21208.4553 | 40013.686 | 105498.536 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-02-17 | 8:50 | 147 | 154180 | 14690 | 7.58 | 47.6 |  | 1557 | 22872.33 |  | 93.83 | 166.7608 | 255.0308 | 33.4755 | 455.267 | 6687.8728 | n | 891.5646 |  |  |  | 20067.485 | 21289.7112 | 39730.06 | 104523.466 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-02-24 | 8:59 | 145 | 168680 | 14500 | 7.63 | 54.8 |  | 1690 | 24505 |  | 132.3 | 223.4497 | 192.7276 | 68.3603 | 484.5376 | 7025.7956 | n | 934.5656 |  |  |  | 21142.605 | 21571.651 | 35429.58 | 101140.188 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-03-02 | 8:54 | 140 | 182690 | 14010 | 7.27 | 64.8 |  | 1764 | 24713.64 |  | 149 | 207.2605 | 211.7993 | 57.1872 | 476.2471 | 6672.2212 | n | 887.6913 |  |  |  | 23093.315 | 22109.496 | 27626.74 | 94686.048 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-03-09 | 8:59 | 127 | 195350 | 12660 | 7.69 | 47.6 |  | 1416 | 17926.56 |  | 63.26 | 93.6357 | 82.8537 | 8.6597 | 185.1491 | 2343.9875 | n | 304.8839 |  |  |  | 22504.3825 | 21596.781 | 29982.47 | 100838.628 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-03-16 | 8:49 | 147 | 210080 | 14730 | 7.87 | 52.8 |  | 1460 | 21505.8 |  | 104.5 | 135.4749 | 140.7166 | 37.883 | 314.0745 | 4626.3177 | n | 615.8916 |  |  |  | 22162.75 | 21254.821 | 31349 | 104942.148 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-03-23 | 9:43 | 155 | 225570 | 15490 | 7.87 | 60.8 |  | 1542 | 23885.58 |  | 143 | 95.938 | 150.4285 | 4.7757 | 251.1422 | 3890.1922 | n | 512.7149 |  |  |  | 22007.895 | 21262.6827 | 31968.42 | 104847.808 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-03-30 | 9:27 | 130 | 238550 | 12980 | 7.75 | 57.2 |  | 1521 | 19742.58 |  | 115.2 | 119.4429 | 107.4355 | 33.2627 | 260.1411 | 3376.6315 | n | 448.29 |  |  |  | 20765.13 | 21374.8377 | 36939.48 | 103501.948 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-04-06 | 9:10 | 130 | 251610 | 13060 | 7.8 | 54 |  | 1625.6868 | 21231.4698 |  | 139.5 | 148 | 127 | 69 | 344 | 4492.64 | n | 606.2035 |  |  |  | 21591.3574 | 21364.1061 | 33634.5702 | 103630.7262 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-04-13 | 7:59 | 156 | 267150 | 15540 | 7.77 | 52.4 |  | 1474 | 22905.96 |  | 132.9 | 98.976 | 75.8695 | 59.8938 | 234.7393 | 3647.8484 | n | 497.2478 |  |  |  | 21941.3974 | 21390.5441 | 32234.4102 | 103313.4702 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-04-20 | 7:57 | 133 | 280520 | 13370 | 7.75 | 57.2 |  | 1305 | 17447.85 |  | 78.73 | 120.498 | 180.6232 | 20.6758 | 321.797 | 4302.4263 | n | 572.0032 |  |  |  | 20331.9649 | 21160.8216 | 38672.1402 | 106070.1402 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-04-27 | 9:00 | 127 | 293220 | 12700 | 7.74 | 50.8 |  | 1279 | 16243.3 |  | 98.41 | 131 | 77 | 36 | 244 | 3098.8 | n | 408.1981 |  |  |  | 19457.1449 | 21105.1966 | 42171.4202 | 106737.6402 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-05-04 | 8:01 | 150 | 308210 | 14990 | 7.73 | 48.8 |  | 1482 | 22215.18 |  | 125.5 | 171.5522 | 169.775 | 51.8554 | 393.1826 | 5893.8075 | n | 785.5559 |  |  |  | 19703.0725 | 21266.2708 | 41187.71 | 104804.7502 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-05-11 | 7:55 | 123 | 320530 | 12320 | 7.54 | 54.8 |  | 1329 | 16373.28 |  | 104 | 192.3455 | 86.1005 | 35.528 | 313.9741 | 3868.1605 | n | 501.0246 |  |  |  | 18069.9025 | 20724.6833 | 47720.39 | 111303.8002 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-05-18 | 8:45 | 116 | 332100 | 11570 | 7.36 | 76.8 |  | 1832 | 21196.24 |  | 117.4 | 251.975 | 264.0008 | 40.5038 | 556.4796 | 6438.4689 | n | 847.6515 |  |  |  | 19007 | 20448.9533 | 43972 | 114612.5602 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-05-25 | 8:47 | 126 | 344740 | 12640 | 7.5 | 62.4 |  | 1695 | 21424.8 |  | 110.1 | 115 | 364 | 17 | 496 | 6269.44 | n | 846.2703 |  |  |  | 20302.375 | 20174.8833 | 38790.5 | 117901.4002 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-06-01 | 8:48 | 141 | 358170 | 13430 | 7.63 | 95.6 |  | 1942 | 26081.06 |  | 135.4 | 31.5567 | 292.4997 | 95.1428 | 419.1992 | 5629.8458 | n | 800.8426 |  |  |  | 21268.845 | 20854.425 | 34924.62 | 109746.9002 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-06-08 | 8:49 | 126 | 370810 | 12640 | 7.98 | 62.8 |  | 1999 | 25267.36 |  | 133.4 | 97.9303 | 380.6319 | 105.2977 | 583.8599 | 7379.9893 | n | 1029.1927 |  |  |  | 23492.365 | 21167.8883 | 26030.54 | 105985.3402 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-06-15 | 8:58 | 117 | 382500 | 11690 | 7.56 | 51.2 |  | 1740 | 20340.6 |  | 115.1 | 157 | 253 | 18 | 428 | 5003.32 | n | 663.433 |  |  |  | 23278.455 | 20872.4733 | 26886.18 | 109530.3202 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-06-22 | 8:17 | 113 | 393900 | 11400 | 7.64 | 47.2 |  | 1650 | 18810 |  | 113.3 | 56.6516 | 309.8303 | 18.6729 | 385.1549 | 4390.7655 | n | 601.1271 |  |  |  | 22624.755 | 20794.7583 | 29500.98 | 110462.9002 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-06-29 | 8:00 | 132 | 407090 | 13190 | 7.73 | 48.8 |  | 1759 | 23201.21 |  | 130.8 | 14.5314 | 353.0103 | 29.1 | 396.6417 | 5231.7043 | n | 730.1151 |  |  |  | 21904.7925 | 20958.9033 | 32380.83 | 108493.16 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-07-06 | 9:04 | 132 | 420410 | 13320 | 7.65 | 29.6 |  | 1651 | 21991.32 |  | 127.1 | 113.6 | 231.1367 | 35.5116 | 380.2483 | 5064.9068 | n | 683.9343 |  |  |  | 21085.7825 | 20882.6833 | 35656.87 | 109407.8 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-07-13 | 8:51 | 115 | 431920 | 11510 | 7.63 | 44 |  | 1636 | 18830.36 |  | 114 | 108.6075 | 278.0655 | 17.0379 | 403.7108 | 4646.7119 | n | 624.7769 |  |  |  | 20708.2225 | 20997.8925 | 37167.11 | 108025.29 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-07-20 | 8:08 | 147 | 446570 | 14650 | 7.57 | 80 |  | 1365 | 19997.25 |  | 96.96 | 128.4364 | 220.7226 | 34.6366 | 383.7955 | 5622.6045 | n | 755.0224 |  |  |  | 21005.035 | 21310.7217 | 35979.86 | 104271.34 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-07-27 | 7:57 | 130 | 458860 | 12290 | 7.53 | 66.8 |  | 1362 | 16738.98 |  | 58.1 | 216.3749 | 136.7916 | 32.2094 | 385.3759 | 4736.2699 | n | 614.9344 |  |  |  | 19389.4775 | 20854.3717 | 42442.09 | 109747.54 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-08-03 | 7:53 | 149 | 473820 | 14960 | 7.25 | 55.6 |  | 1516 | 22679.36 |  | 123 | 148.5156 | 210.7218 | 47.423 | 406.6605 | 6083.6406 | n | 816.9859 |  |  |  | 19561.4875 | 21379.8783 | 41754.05 | 103441.46 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-08-10 | 8:50 | 160 | 489780 | 15960 | 7.68 | 48.8 |  | 1609 | 25679.64 |  | 165.6 | 125.028 | 246.7383 | 69.3731 | 441.1394 | 7040.585 | n | 962.7942 |  |  |  | 21273.8075 | 21753.495 | 34904.77 | 98958.06 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-08-17 | 8:02 | 138 | 3600 | 13820 | 7.73 | 58.4 |  | 1322 | 18270.04 |  | 123.3 | 63.9113 | 207.1997 | 38.9829 | 310.094 | 4285.4984 | n | 589.3038 |  |  |  | 20842.005 | 21490.5983 | 36631.98 | 102112.82 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-08-24 | 7:58 | 153 | 18930 | 15330 | 7.69 | 66.4 |  | 1486 | 22780.38 |  | 97.58 | 215.6402 | 257.9499 | 15.3498 | 488.9399 | 7495.4484 | n | 981.5586 |  |  |  | 22352.355 | 21215.5417 | 30590.58 | 105413.5 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-08-31 | 8:43 | 146 | 33530 | 14600 | 7.69 | 73.2 |  | 1437 | 20980.2 |  | 99.45 | 202.1704 | 208.1431 | 12.6225 | 422.936 | 6174.865 | n | 804.0811 |  |  |  | 21927.565 | 20858.2783 | 32289.74 | 109700.66 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-09-07 | 8:46 | 129 | 46450 | 12920 | 7.67 | 112.8 |  | 1336 | 17261.12 |  | 114 | 92.0131 | 219.9652 | 44.5717 | 356.5501 | 4606.6268 | n | 628.8527 |  |  |  | 19822.935 | 20601.655 | 40708.26 | 112780.14 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-09-14 | 8:45 | 161 | 61690 | 15240 | 7.66 | 52.4 |  | 2346 | 35753.04 |  | 97.77 | 778.4827 | 418.3646 | 44.3053 | 1241.1526 | 18915.1649 | n | 2412.0728 |  |  |  | 24193.685 | 22013.575 | 23225.26 | 95837.1 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-09-21 | 8:40 | 158 | 77560 | 15870 | 7.44 | 64 |  | 1343 | 21313.41 |  | 93.55 | 128 | 138 | 10 | 276 | 4380.12 | n | 572.1793 |  |  |  | 23826.9425 | 21856.2583 | 24692.23 | 97724.9 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-09-28 | 7:58 | 150 | 92520 | 14960 | 7.63 | 62.4 |  | 1341 | 20061.36 |  | 108.5 | 115.9863 | 223.0018 | 49.2457 | 388.2338 | 5807.9776 | n | 788.608 |  |  |  | 23597.2325 | 21695.4283 | 25611.07 | 99654.86 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-10-05 | 8:07 | 164 | 108920 | 16400 | 7.56 | 64.8 |  | 1485 | 24354 |  | 142.7 | 137.2348 | 163.7798 | 55.511 | 356.5256 | 5847.0202 | n | 788.122 |  |  |  | 25370.4525 | 22155.7317 | 18518.19 | 94131.22 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-10-12 | 7:59 | 165 | 124490 | 15570 | 7.35 | 56.8 |  | 1166 | 18154.62 |  | 63.3 | 118.0604 | 145.611 | 20.8973 | 284.5686 | 4430.7339 | n | 586.5743 |  |  |  | 20970.8475 | 22002.1792 | 36116.61 | 95973.85 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-10-19 | 8:48 | 154 | 139660 | 15170 | 7.6 | 46 |  | 1246 | 18901.82 |  | 89.84 | 139.3731 | 96.5706 | 20.8487 | 256.7923 | 3895.5398 | n | 506.9526 |  |  |  | 20367.95 | 22182.4158 | 38528.2 | 93811.01 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-10-26 | 8:04 | 142 | 153860 | 14200 | 7.15 | 54.4 |  | 1292 | 18346.4 |  | 91.99 | 94.8357 | 56.4813 | 17.2102 | 168.5272 | 2393.0862 | n | 311.6391 |  |  |  | 19939.21 | 21821.3358 | 40243.16 | 98143.97 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-11-02 | 8:55 | 133 | 167110 | 13250 | 7.61 | 60 |  | 1196 | 15847 |  | 76.87 | 104.9872 | 132.4858 | 27.4105 | 264.8835 | 3509.7064 | n | 468.2262 |  |  |  | 17812.46 | 21001.9492 | 48750.16 | 107976.61 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-11-09 | 9:10 | 159 | 183080 | 15970 | 7.58 | 50 |  | 1185 | 18924.45 |  | 75.75 | 104.4001 | 161.6309 | 29.3587 | 295.3897 | 4717.3727 | n | 632.7471 |  |  |  | 18004.9175 | 21056.4833 | 47980.33 | 107322.2 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-11-16 | 9:10 | 145 | 196600 | 13520 | 7.71 | 57.2 |  | 1345 | 18184.4 |  | 85.46 | 131 | 117 | 30 | 278 | 3758.56 | n | 496.4628 |  |  |  | 17825.5625 | 20673.485 | 48697.75 | 111918.18 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-11-23 | 7:06 | 142 | 210820 | 14220 | 7.34 | 57.2 |  | 1265 | 17988.3 |  | 92.55 | 88.4881 | 153.7682 | 32.4225 | 274.6787 | 3905.9318 | n | 527.8482 |  |  |  | 17736.0375 | 20424.16 | 49055.85 | 114910.08 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-11-30 | 8:40 | 137 | 224440 | 13620 | 7.39 | 45.6 |  | 1209 | 16466.58 |  | 39.84 | 124 | 134 | 29 | 287 | 3908.94 | n | 518.6296 |  |  |  | 17890.9325 | 20357.9483 | 48436.27 | 115704.62 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-12-07 | 9:07 | 132 | 237870 | 13430 | 7.66 | 36.4 |  | 1252.4 | 16819.732 |  | 68.15 | 170 | 180 | 19 | 369 | 4955.67 | n | 649.3384 |  |  |  | 17364.753 | 18780.1727 | 50540.988 | 134637.928 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-12-14 | 9:45 | 129 | 249810 | 11940 | 7.59 | 55.6 |  | 1269 | 15151.86 |  | 60.08 | 110.7886 | 132.7929 | 21.3721 | 264.9535 | 3163.5448 | n | 419.1282 |  |  |  | 16606.618 | 18266.7102 | 53573.528 | 140799.478 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-12-21 | 9:11 | 153 | 265040 | 15230 | 7.84 | 50.8 |  | 1415 | 21550.45 |  | 102.5 | 160.7216 | 133.1166 | 35.4467 | 329.2849 | 5015.0092 | n | 660.7919 |  |  |  | 17497.1555 | 18390.801 | 50011.378 | 139310.388 | 8000 | 30000 | 100 | 6 | 10 | 35000
2012-12-28 | 9:44 | 140 | 279130 | 14090 | 7.17 | 57.6 |  | 1297 | 18274.73 |  | 54.86 | 200.6451 | 155.7668 | 13.683 | 370.0949 | 5214.6376 | n | 673.5319 |  |  |  | 17949.193 | 17884.1952 | 48203.228 | 145389.658 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-01-04 | 9:44 | 124 | 291530 | 12400 | 7.4 | 69.6 |  | 1261.4583 | 15642.0829 |  | 47.49 | 86.4398 | 183.0316 | 18.0867 | 287.5581 | 3565.7204 | n | 478.9431 |  |  |  | 17654.7807 | 17674.8171 | 49380.8771 | 147902.1951 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-01-11 | 9:03 | 158 | 306340 | 14810 | 7.62 | 72.4 |  | 1435 | 21252.35 |  | 100.8 | 146.204 | 164.2468 | 34.163 | 344.6138 | 5103.7307 | n | 677.689 |  |  |  | 19179.9032 | 17870.6946 | 43280.3871 | 145551.6651 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-01-18 | 8:16 | 145 | 320780 | 14440 | 7.45 | 52 |  | 1239 | 17891.16 |  | 75.66 | 262.2041 | 89.0023 | 24.2541 | 375.4605 | 5421.6498 | n | 687.5572 |  |  |  | 18265.0807 | 17832.7579 | 46939.6771 | 146006.9051 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-01-25 | 8:56 | 131 | 333910 | 13130 | 7.52 | 42.4 |  | 1234 | 16202.42 |  | 60.17 | 125.9591 | 125.9591 | 24.427 | 276.3452 | 3628.413 | n | 478.7525 |  |  |  | 17747.0032 | 17862.3762 | 49011.9871 | 145651.4851 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-02-01 | 9:22 | 143 | 348220 | 14310 | 7.62 | 47.2 |  | 1356 | 19404.36 |  | 79.86 | 148.5851 | 162.2319 | 27.9266 | 338.7436 | 4847.4209 | n | 640.529 |  |  |  | 18687.5725 | 17902.3687 | 45249.71 | 145171.5751 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-02-08 | 8:31 | 130 | 361300 | 13080 | 7.57 | 64.4 |  | 1230 | 16088.4 |  | 50.38 | 149.3784 | 181.2205 | 25.3703 | 355.9693 | 4656.0787 | n | 615.762 |  |  |  | 17396.585 | 17727.7021 | 50413.66 | 147267.5751 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-02-15 | 8:43 | 155 | 375740 | 14440 | 7.42 | 68 |  | 1543 | 22280.92 |  | 106.8 | 244.1116 | 156.9328 | 41.2314 | 442.2758 | 6386.462 | n | 831.7141 |  |  |  | 18494.025 | 18085.4204 | 46023.9 | 142974.9551 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-02-22 | 8:38 | 131 | 388900 | 13160 | 7.73 | 49.6 |  | 1455 | 19147.8 |  | 103.5 | 211.9959 | 162.9945 | 32.321 | 407.3114 | 5360.2187 | n | 699.6042 |  |  |  | 19230.37 | 18308.8554 | 43078.52 | 140293.7351 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-03-01 | 8:34 | 125 | 401380 | 12480 | 7.65 | 50 |  | 1415 | 17659.2 |  | 78.55 | 171.031 | 185.2897 | 24.7726 | 381.0933 | 4756.0439 | n | 625.6893 |  |  |  | 18794.08 | 18378.8111 | 44823.68 | 139454.2671 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-03-08 | 9:18 | 147 | 416060 | 14680 | 7.43 | 60.4 | 1325 | 1347 | 19773.96 |  | 71.43 | 156.1866 | 155.9245 | 9.4443 | 321.5553 | 4720.4325 | n | 613.9478 |  |  |  | 19715.47 | 18763.9861 | 41138.12 | 134832.1671 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-03-15 | 8:40 | 154 | 430460 | 14400 | 7.82 | 71.6 | 1362.4 | 1432 | 20620.8 |  | 97.86 | 109.7332 | 179.5624 | 33.6128 | 322.9084 | 4649.881 | n | 625.3814 |  |  |  | 19300.44 | 18686.5152 | 42798.24 | 135761.8171 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-03-22 | 9:15 | 143 | 444770 | 14310 | 7.71 | 64.8 | 1263.2 | 1503 | 21507.93 |  | 109 | 158.1548 | 184.8788 | 26.7953 | 369.8289 | 5292.2513 | n | 699.2318 |  |  |  | 19890.4725 | 18955.9486 | 40438.11 | 132528.6171 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-03-29 | 9:55 | 138 | 458640 | 13870 | 7.15 | 51.6 | 1107.2 | 1359 | 18849.33 |  | 101.2 | 59.0006 | 176.7056 | 11.8393 | 247.5455 | 3433.4566 | n | 464.0753 |  |  |  | 20188.005 | 19223.2192 | 39247.98 | 129321.37 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-04-05 | 9:03 | 141 | 472830 | 14190 | 7.68 | 50 | 1191.6 | 1332.4 | 18906.756 |  | 100.3 | 117.0743 | 142.364 | 16.8243 | 276.2626 | 3920.1666 | n | 517.2238 |  |  |  | 19971.204 | 19027.753 | 40115.184 | 131666.964 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-05-12 | 7:41 | 156 | 488360 | 15530 | 7.62 | 51.6 | 1194.4 | 1285 | 19956.05 |  | 80.14 | 133.0268 | 197.4977 | 20.9252 | 351.4496 | 5458.0128 | n | 724.6441 |  |  |  | 19805.0165 | 19199.8272 | 40779.934 | 129602.074 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-04-19 | 7:39 | 127 | 140 | 11780 | 7.12 | 85.2 | 1148 | 1261 | 14854.58 |  | 75.19 | 55.941 | 183.4095 | 20.4791 | 259.8296 | 3060.7929 | n | 417.1579 |  |  |  | 18141.679 | 19087.5072 | 47433.284 | 130949.914 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-04-26 | 7:40 | 182 | 13640 | 13500 | 7.86 | 89.2 | 1339.8 | 1487.6 | 20082.6 |  | 102.3 | 136.4186 | 206.5699 | 31.2603 | 374.2488 | 5052.3588 | n | 674.8304 |  |  |  | 18449.9965 | 19144.0272 | 46200.014 | 130271.674 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-05-03 | 9:30 | 134 | 27300 | 13660 | 7.47 | 56.8 | 1586 | 1617.3823 | 22093.4418 |  | 114.4 | 184.3346 | 245.1775 | 44.7238 | 474.2359 | 6478.0617 | n | 863.8455 |  |  |  | 19246.668 | 19644.4473 | 43013.3282 | 124266.6322 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-05-10 | 9:16 | 136 | 40860 | 13560 | 7.59 | 64 | 1509.6 | 1469 | 19919.64 |  | 88.91 | 163.3955 | 241.625 | 37.7786 | 442.7991 | 6004.3562 | n | 801.7145 |  |  |  | 19237.5655 | 19447.674 | 43049.7382 | 126627.9122 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-05-17 | 7:36 | 141 | 54280 | 13420 | 7.4 | 83.6 | 1300 | 1347.5 | 18083.45 |  | 51.54 | 253.4276 | 150.0834 | 19.8185 | 423.3294 | 5681.0807 | n | 728.9406 |  |  |  | 20044.783 | 19358.9782 | 39820.8682 | 127692.2622 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-05-24 | 7:43 | 166 | 68260 | 13980 | 7.62 | 62.8 | 1665.2 | 1535 | 21459.3 |  | 83.96 | 208.9709 | 158.6843 | 29.7819 | 397.437 | 5556.1694 | n | 724.0715 |  |  |  | 20388.958 | 19675.6532 | 38444.1682 | 123892.1622 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-05-31 |  | 129 | 81160 | 12900 | 7.33 | 65.6 | 1613 | 1577.8 | 20353.62 |  | 96.65 | 226.7561 | 159.79 | 39.7704 | 426.3165 | 5499.4829 | n | 718.2998 |  |  |  | 19954.0025 | 19723.9582 | 40183.99 | 123312.5022 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-06-07 | 7:45 | 135 | 94710 | 13550 | 7.54 | 62.8 | 1836 | 1591 | 21558.05 |  | 97.02 | 168.2874 | 190.5607 | 34.511 | 393.3591 | 5330.0158 | n | 706.0201 |  |  |  | 20363.605 | 19802.0623 | 38545.58 | 122375.2522 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-06-14 | 8:28 | 145 | 109220 | 14510 | 7.6 | 57.6 | 1902.8 | 1525 | 22127.75 |  | 98.05 | 185.4927 | 199.9403 | 35.4274 | 420.8604 | 6106.6841 | n | 806.918 |  |  |  | 21374.68 | 19853.714 | 34501.28 | 121755.4322 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-06-21 | 7:39 | 132 | 122330 | 13110 | 7.54 | 70.4 | 1500 | 1420 | 18616.2 |  | 100.9 | 70.9377 | 207.6159 | 33.3179 | 311.8715 | 4088.6355 | n | 558.8559 |  |  |  | 20663.905 | 19834.2865 | 37344.38 | 121988.5622 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-06-28 | 9:16 | 140 | 135660 | 13330 | 7.44 | 63.6 |  | 1602 | 21354.66 |  | 113.7 | 94.7537 | 244.7865 | 39.9911 | 379.5314 | 5059.1532 | n | 689.2171 |  |  |  | 20914.165 | 20038.2785 | 36343.34 | 119540.6582 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-07-05 | 9:22 | 129 | 148510 | 12850 | 7.6 | 46 | 2543 | 1584 | 20354.4 |  | 90.59 | 118.8968 | 276.605 | 38.5634 | 434.0652 | 5577.7381 | n | 755.2441 |  |  |  | 20613.2525 | 20071.4743 | 37546.99 | 119142.3082 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-07-12 | 9:14 | 142 | 162730 | 14220 | 7.4 | 58 |  | 1479 | 21031.38 |  | 100.1 | 182.9446 | 181.1805 | 48.8418 | 412.9669 | 5872.3899 | n | 780.1738 |  |  |  | 20339.16 | 20586.2077 | 38643.36 | 112965.5082 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-07-19 | 7:41 | 134 | 175460 | 12730 | 7.63 | 84.8 |  | 1494 | 19018.62 |  | 110 | 36.7054 | 261.0506 | 37.5555 | 335.3115 | 4268.5149 | n | 593.482 |  |  |  | 20439.765 | 20497.5427 | 38240.94 | 114029.4882 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-07-26 | 7:46 | 142 | 189660 | 14200 | 7.61 | 97.6 |  | 1379 | 19581.8 |  | 96.76 | 48.2116 | 205.3033 | 35.796 | 289.3109 | 4108.2155 | n | 567.8165 |  |  |  | 19996.55 | 20288.2392 | 40013.8 | 116541.13 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-08-02 | 7:38 | 147 | 204320 | 14660 | 7.54 | 68 | 821.4 | 1230 | 18031.8 |  | 86.66 | 25.9183 | 209.1052 | 28.9004 | 263.9239 | 3869.1239 | n | 538.5622 |  |  |  | 19415.9 | 20130.9192 | 42336.4 | 118428.97 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-08-09 | 7:38 | 76 | 211940 | 7620 | 7.51 | 117 | 811 | 1288.6 | 9819.132 |  | 91.09 | 34.7553 | 220.9689 | 20.8651 | 276.5893 | 2107.6107 | n | 290.6703 |  |  |  | 16612.838 | 19442.226 | 53548.648 | 126693.288 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-08-16 | 7:43 | 136 | 225540 | 13600 | 7.7 | 97.2 | 1024 | 1272.5 | 17306 |  | 81.84 | 41.82 | 188.6789 | 4.2657 | 234.7646 | 3192.7988 | n | 433.0791 |  |  |  | 16184.683 | 19096.1177 | 55261.268 | 130846.588 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-08-23 | 7:43 | 148 | 239500 | 13960 | 7.32 | 75.2 | 1136 | 1310 | 18287.6 |  | 100.4 | 5.4887 | 175.032 | 5.0156 | 185.5364 | 2590.0877 | n | 359.1314 |  |  |  | 15861.133 | 18923.9493 | 56555.468 | 132912.608 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-08-30 | 8:18 | 123 | 251830 | 12330 | 7.44 | 56.8 | 991 | 1127 | 13895.91 |  | 59.05 | 0 | 165.8244 | 5.8798 | 171.7042 | 2117.1132 | n | 295.0783 |  |  |  | 14827.1605 | 18285.4377 | 60691.358 | 140574.748 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-09-06 | 7:40 | 152 | 267020 | 15190 | 7.53 | 50.8 | 1195 | 1304 | 19807.76 |  | 82.97 | 105.3817 | 118.5983 | 9.315 | 233.295 | 3543.7504 | n | 464.0257 |  |  |  | 17324.3175 | 18092.1052 | 50702.73 | 142894.738 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-09-13 | 7:38 | 145 | 281450 | 14430 | 7.73 | 67.6 | 1432 | 1525 | 22005.75 |  | 102.1 | 219.94 | 108.96 | 8.453 | 337.353 | 4868.0038 | n | 617.3331 |  |  |  | 18499.255 | 18374.5677 | 46002.98 | 139505.188 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-09-20 | 7:47 | 141 | 295580 | 14130 | 7.6 | 63.6 | 1454 | 1598 | 22579.74 |  | 107.3 | 135.6725 | 118.6834 | 9.6877 | 264.0436 | 3730.9366 | n | 483.8738 |  |  |  | 19572.29 | 18476.6577 | 41710.84 | 138280.108 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-09-27 | 8:17 | 143 | 309930 | 14350 | 7.61 | 76.8 | 1303 | 1352 | 19401.2 |  | 94.32 | 104.5225 | 122.6726 | 8.7948 | 235.9898 | 3386.4541 | n | 443.7929 |  |  |  | 20948.6125 | 18397.2243 | 36205.55 | 139233.308 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-10-04 | 7:40 | 146 | 324480 | 14550 | 7.62 | 72 | 1692.2 | 1474 | 21446.7 |  | 100.4 | 133 | 161.0449 | 6 | 300.0449 | 4365.6537 | n | 570.4052 |  |  |  | 21358.3475 | 18431.8343 | 34566.61 | 138817.988 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-10-11 | 7:45 | 146 | 338400 | 13920 | 7.77 | 71.6 | 810.4 | 1545 | 21506.4 |  | 111 | 130.2123 | 175.3413 | 6.5734 | 312.1269 | 4344.8066 | n | 569.9331 |  |  |  | 21233.51 | 18639.1493 | 35065.96 | 136330.208 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-10-18 | 8:18 | 141 | 352530 | 14130 | 7.87 | 49.2 |  | 1496 | 21138.48 |  | 101.5 | 103.4503 | 195.9669 | 5.7307 | 305.1479 | 4311.7395 | n | 571.7645 |  |  |  | 20873.195 | 18768.8727 | 36507.22 | 134773.528 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-10-25 | 7:45 | 145 | 366370 | 13840 | 7.67 | 56.4 |  | 1360 | 18822.4 |  | 99.49 | 137.7159 | 174.0135 | 4.9823 | 316.7118 | 4383.2908 | n | 572.9935 |  |  |  | 20728.495 | 18834.756 | 37086.02 | 133982.928 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-11-01 | 9:20 | 141 | 380440 | 14070 | 7.55 | 48 |  | 1468 | 20654.76 |  | 90.24 | 145.3282 | 195.9243 | 5.7772 | 347.0297 | 4882.7083 | n | 639.8641 |  |  |  | 20530.51 | 19737.725 | 37877.96 | 123147.3 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-11-08 | 8:34 | 125 | 392920 | 12480 | 7.52 | 48.8 | 853.8 | 1422 | 17746.56 |  | 62.21 | 163.5618 | 164.1508 | 7.1164 | 334.829 | 4178.6665 | n | 542.5087 |  |  |  | 19590.55 | 19774.4383 | 41637.8 | 122706.74 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-11-15 | 9:20 | 127 | 405630 | 12710 | 7.42 | 34.4 | 992.8 | 1359 | 17272.89 |  | 74.07 | 161.5214 | 151.7759 | 7.2497 | 320.547 | 4074.1526 | n | 527.8744 |  |  |  | 18624.1525 | 19689.8792 | 45503.39 | 123721.45 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-11-22 | 9:24 | 145 | 419330 | 13700 | 7.59 | 31.6 | 874.8 | 1477 | 20234.9 |  | 103.7 | 157.0082 | 146.3807 | 2.2717 | 305.6605 | 4187.5489 | n | 540.3725 |  |  |  | 18977.2775 | 20218.1283 | 44090.89 | 117382.46 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-11-29 | 9:27 | 137 | 433050 | 13720 | 7.6 | 42 | 881 | 1630 | 22363.6 |  | 116.8 | 230 | 147 | 0 | 377 | 5172.44 | n | 657.1551 |  |  |  | 19404.4875 | 20431.115 | 42382.05 | 114826.62 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-12-06 | 9:24 | 134 | 446440 | 13390 | 7.64 | 34 | 1622.6 | 1575 | 21089.25 |  | 112.3 | 177.6294 | 174.9921 | 0 | 352.6216 | 4721.603 | n | 609.3942 |  |  |  | 20240.16 | 20354.74 | 39039.36 | 115743.12 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-12-13 | 9:30 | 120 | 458420 | 11980 | 7.09 | 51.2 | 839.8 | 1309 | 15681.82 |  | 21.595 | 220.0677 | 128.4477 | 11.5169 | 360.0323 | 4313.1866 | n | 550.9699 |  |  |  | 19842.3925 | 19779.9133 | 40630.43 | 122641.04 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-12-20 | 9:24 | 139 | 472410 | 13990 | 7.51 | 22.8 |  | 1574 | 22020.26 |  | 109.2 | 166.8306 | 197.6924 | 0 | 364.523 | 5099.6768 | n | 662.6439 |  |  |  | 20288.7325 | 19998.1683 | 38845.07 | 120021.98 | 8000 | 30000 | 100 | 6 | 10 | 35000
2013-12-27 | 9:27 | 132 | 484730 | 12320 | 7.37 | 18.8 |  | 1494 | 18406.08 |  | 72.21 | 177.5618 | 143.3136 | 7.1198 | 327.9952 | 4040.9006 | n | 520.6146 |  |  |  | 19299.3525 | 19744.7833 | 42802.59 | 123062.6 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-01-03 | 8:51 | 112 | 495950 | 11220 | 7.45 | 20 | 1063 | 1324 | 14855.28 |  | 39.84 | 172 | 161 | 15 | 348 | 3904.56 | n | 508.3986 |  |  |  | 17740.86 | 19190.5233 | 49036.56 | 129713.72 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-01-10 | 9:45 | 147 | 10650 | 14700 | 7.54 | 20.8 |  | 1521 | 22358.7 |  | 106.2 | 218 | 175 | 13 | 406 | 5968.2 | n | 770.7923 |  |  |  | 19410.08 | 19292.2083 | 42359.68 | 128493.5 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-01-17 | 9:24 | 133 | 23980 | 13330 | 7.62 | 37.2 | 1556 | 1451 | 19341.83 |  | 115 | 131.5896 | 186.0591 | 2.7851 | 320.4337 | 4271.3819 | n | 559.6508 |  |  |  | 18740.4725 | 19335.4942 | 45038.11 | 127974.07 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-01-24 | 9:18 | 121 | 36110 | 12130 | 7.36 | 35.2 | 901.4 | 1341 | 16266.33 |  | 64.28 | 139.2438 | 149.5023 | 9.3024 | 298.0485 | 3615.3279 | n | 471.6347 |  |  |  | 18205.535 | 18969.7917 | 47177.86 | 132362.5 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-01-31 | 9:16 | 116 | 46940 | 10830 | 7.34 | 34.8 | 1031 | 1422 | 15400.26 |  | 14.52 | 140.2007 | 168.6824 | 6.6001 | 315.4832 | 3416.6829 | n | 446.4121 |  |  |  | 18341.78 | 18774.2667 | 46632.88 | 134708.8 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-02-07 | 9:20 | 135 | 60450 | 13510 | 7.39 | 40.8 | 912 | 1422 | 19211.22 |  | 99.15 | 240.1367 | 159.279 | 6.8354 | 406.2511 | 5488.4525 | n | 701.3383 |  |  |  | 17554.91 | 18935.7942 | 49780.36 | 132770.47 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-02-14 | 8:50 | 131 | 73520 | 13070 | 7.43 | 25.2 | 974.2 | 1402 | 18324.14 |  | 94.9 | 106.5506 | 167.5537 | 8.212 | 282.3163 | 3689.8746 | n | 487.4638 |  |  |  | 17300.4875 | 18776.5642 | 50798.05 | 134681.23 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-02-21 | 8:55 | 132 | 86740 | 13220 | 7.61 | 20 | 972.8 | 1484 | 19618.48 |  | 131.5 | 124.2654 | 170.9548 | 11.2862 | 306.5064 | 4052.0143 | n | 533.8532 |  |  |  | 18138.525 | 18547.8042 | 47445.9 | 137426.35 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-02-28 | 9:06 | 146 | 101270 | 14530 | 7.6 | 34.4 | 1115.6 | 1473 | 21402.69 |  | 114.3 | 116.9489 | 86.596 | 99.6043 | 303.1493 | 4404.7595 | n | 610.6317 |  |  |  | 19639.1325 | 18573.9242 | 41443.47 | 137112.91 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-03-07 | 9:01 | 151 | 116380 | 15110 | 7.61 | 50.4 |  | 1479 | 22347.69 |  | 116.9 | 173.5355 | 181.5868 | 15.3331 | 370.4555 | 5597.5822 | n | 731.3661 |  |  |  | 20423.25 | 19129.4133 | 38307 | 130447.04 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-03-14 | 8:54 | 130 | 128650 | 12270 | 7.55 | 64.4 |  | 1402 | 17202.54 |  | 78.96 | 122.994 | 187.2957 | 14.3809 | 324.6706 | 3983.7083 | n | 527.5263 |  |  |  | 20142.85 | 18727.9367 | 39428.6 | 135264.76 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-03-21 | 9:18 | 142 | 142840 | 14190 | 7.52 | 41.2 | 881.4 | 1449.9319 | 20574.5334 |  | 107.7 | 146.2071 | 167.7165 | 4.5852 | 318.5088 | 4519.6396 | n | 588.6089 |  |  |  | 20381.8633 | 18908.6411 | 38472.5466 | 133096.3066 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-03-28 | 9:21 | 135 | 156340 | 13500 | 7.59 | 35.2 |  | 1498 | 20223 |  | 115.6 | 142.1197 | 133.2106 | 5.8994 | 281.2298 | 3796.6018 | n | 491.6693 |  |  |  | 20086.9408 | 19355.9511 | 39652.2366 | 127728.5866 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-04-04 | 8:50 | 130 | 169360 | 13020 | 7.63 | 40.8 |  | 1500 | 19530 |  | 113.8 | 104.5247 | 154.4954 | 40.8863 | 299.9065 | 3904.7821 | n | 527.334 |  |  |  | 19382.5183 | 19120.2261 | 42469.9266 | 130557.2866 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-04-11 | 8:21 | 118 | 181120 | 11760 | 7.37 | 42.4 |  | 1364 | 16040.64 |  | 71.13 | 167.3427 | 172.24 | 46.7767 | 386.3594 | 4543.5871 | n | 604.7704 |  |  |  | 19092.0433 | 18845.1269 | 43631.8266 | 133858.4766 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-04-18 | 8:23 | 135 | 193880 | 12760 | 7.58 | 38 |  | 1367 | 17442.92 |  | 108.4 | 124.1224 | 141.2617 | 36.0476 | 301.4317 | 3846.2681 | n | 513.3838 |  |  |  | 18309.14 | 18943.1761 | 46763.44 | 132681.8866 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-04-25 | 8:56 | 134 | 207280 | 13400 | 7.54 | 36.8 |  | 1393 | 18666.2 |  | 102.4 | 156.2238 | 132.1857 | 37.074 | 325.4835 | 4361.4786 | n | 575.9608 |  |  |  | 17919.94 | 19215.3378 | 48320.24 | 129415.9466 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-05-02 | 9:07 | 119 | 219190 | 11910 | 7.42 | 50 |  | 1277 | 15209.07 |  | 68.04 | 70.8787 | 132.1887 | 48.5904 | 251.6579 | 2997.2457 | n | 412.3666 |  |  |  | 16839.7075 | 18881.8253 | 52641.17 | 133418.0966 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-05-09 | 9:37 | 131 | 232400 | 13210 | 7.25 | 43.6 |  | 1289 | 17027.69 |  | 35.85 | 244.4929 | 137.6496 | 57.8025 | 439.945 | 5811.6731 | n | 761.3881 |  |  |  | 17086.47 | 18773.7878 | 51654.12 | 134714.5466 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-05-16 | 9:00 | 128 | 245120 | 12720 | 7.52 | 56 |  | 1335 | 16981.2 |  | 97.8 | 58.2278 | 171.2028 | 40.0262 | 269.4568 | 3427.4906 | n | 472.4146 |  |  |  | 16971.04 | 18554.0144 | 52115.84 | 137351.8266 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-05-23 | 9:24 | 116 | 256740 | 11620 | 7.2 | 40 |  | 1242 | 14432.04 |  | 50.74 | 26.2983 | 175.1423 | 54.1261 | 255.5667 | 2969.6851 | n | 419.876 |  |  |  | 15912.5 | 17973.1269 | 56350 | 144322.4766 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-05-30 | 9:34 | 141 | 270840 | 14100 | 7.76 | 49.2 |  | 1299 | 18315.9 |  | 102 | 55.5779 | 123.2305 | 39.7249 | 218.5333 | 3081.32 | n | 424.7529 |  |  |  | 16689.2075 | 17637.1444 | 53243.17 | 148354.2666 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-06-06 | 8:47 | 130 | 283860 | 13020 | 7.39 | 44.4 | 1152 | 1367 | 17798.34 |  | 111.3 | 84.3134 | 103.4853 | 28.1827 | 215.9814 | 2812.078 | n | 377.1689 |  |  |  | 16881.87 | 17686.7944 | 52472.52 | 147758.4666 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-06-13 | 9:23 | 139 | 297750 | 13890 | 7.4 | 69.2 | 1214.6 | 1287 | 17876.43 |  | 80.81 | 4.747 | 235.4669 | 34.9062 | 275.1201 | 3821.4185 | n | 539.2665 |  |  |  | 17105.6775 | 17461.9525 | 51577.29 | 150456.57 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-06-20 | 9:20 | 125 | 310330 | 12580 | 7.47 | 45.6 | 1214.8 | 1456 | 18316.48 |  | 106.2 | 121.9334 | 187.5989 | 41.4364 | 350.9688 | 4415.187 | n | 594.5567 |  |  |  | 18076.7875 | 17303.0758 | 47692.85 | 152363.09 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-06-27 | 9:47 | 135 | 323860 | 13530 | 7.43 | 55.2 | 1234 | 1490 | 20159.7 |  | 114.3 | 72.0969 | 252.8141 | 52.9397 | 377.8507 | 5112.3196 | n | 706.1246 |  |  |  | 18537.7375 | 17355.5508 | 45849.05 | 151733.39 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-07-04 | 8:52 | 127 | 336630 | 12770 | 7.4 | 73.6 | 1231 | 1417 | 18095.09 |  | 121.4 | 6 | 241 | 19 | 266 | 3396.82 | n | 474.806 |  |  |  | 18611.925 | 17526.755 | 45552.3 | 149678.94 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-07-11 | 9:22 | 146 | 351240 | 14610 | 7.72 | 57.2 | 1164.4 | 1306 | 19080.66 |  | 108.4 | 58.3347 | 151.6525 | 20.2003 | 230.1875 | 3363.0397 | n | 456.5915 |  |  |  | 18912.9825 | 17663.2333 | 44348.07 | 148041.2 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-07-18 | 9:21 | 137 | 364930 | 13690 | 7.38 | 36 | 1202.2 | 1426 | 19521.94 |  | 101 | 3.4252 | 245.5552 | 0 | 248.9804 | 3408.5413 | n | 471.5822 |  |  |  | 19214.3475 | 17734.545 | 43142.61 | 147185.46 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-07-25 | 8:33 | 126 | 377570 | 12640 | 7.58 | 48 | 1183.6 | 1241 | 15686.24 |  | 68.13 | 0 | 183 | 8 | 191 | 2414.24 | n | 336.9027 |  |  |  | 18095.9825 | 17774.3092 | 47616.07 | 146708.29 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-08-01 | 9:19 | 148 | 391390 | 13820 | 7.13 | 61.2 | 1108.4 | 1282 | 17717.24 |  | 99.35 | 2.922 | 175.296 | 10.5339 | 188.7519 | 2608.5515 | n | 364.0632 |  |  |  | 18001.52 | 17831.7717 | 47993.92 | 146018.74 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-08-08 | 9:00 | 143 | 405680 | 14290 | 7.52 | 54 | 1291.4 | 1362 | 19462.98 |  | 105.8 | 0 | 220.501 | 8.0833 | 228.5844 | 3266.4704 | n | 455.3546 |  |  |  | 18097.1 | 18038.5867 | 47611.6 | 143536.96 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-08-15 | 9:24 | 156 | 421380 | 15700 | 7.29 | 53.2 | 1017.8 | 1242 | 19499.4 |  | 89.52 | 4.0248 | 238.8859 | 11.2927 | 254.2034 | 3990.9928 | n | 555.9638 |  |  |  | 18091.465 | 18460.8667 | 47634.14 | 138469.6 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-08-22 | 8:50 | 146 | 435930 | 14550 | 7.75 | 48.8 | 3029.6 | 1404 | 20428.2 |  | 108.9 | 0 | 171.0078 | 6.7811 | 177.7888 | 2586.8278 | n | 360.771 |  |  |  | 19276.955 | 18636.8917 | 42892.18 | 136357.3 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-08-29 | 9:25 | 142 | 450190 | 14260 | 7.62 | 47.2 | 3121 | 1304 | 18595.04 |  | 107.2 | 111.2417 | 97.3665 | 12.9936 | 221.6018 | 3160.0412 | n | 412.0889 |  |  |  | 19496.405 | 18703.2833 | 42014.38 | 135560.6 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-09-05 | 8:55 | 150 | 465080 | 14890 | 7.5 | 53.2 | 3397 | 1212 | 18046.68 |  | 102.1 | 86.9562 | 109.5898 | 16.9273 | 213.4732 | 3178.6164 | n | 421.6789 |  |  |  | 19142.33 | 18717.4708 | 43430.68 | 135390.35 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-09-12 | 8:55 | 136 | 478750 | 13670 | 7.51 | 67.6 | 4281 | 1461 | 19971.87 |  | 107.9 | 155.1941 | 176.0224 | 5.1954 | 336.4119 | 4598.7503 | n | 598.82 |  |  |  | 19260.4475 | 18855.42 | 42958.21 | 133734.96 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-09-19 | 9:39 | 125 | 491200 | 12450 | 7.65 | 53.2 | 1242.4 | 1317 | 16396.65 |  | 94.25 | 44.8224 | 135.8057 | 24.6813 | 205.3094 | 2556.102 | n | 350.5873 |  |  |  | 18252.56 | 18541.8325 | 46989.76 | 137498.01 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-09-26 | 9:07 | 111 | 2290 | 11089 | 7.52 | 78 | 1151 | 1257 | 13938.873 |  | 70.64 | 16.4384 | 181.1767 | 5.4332 | 203.0483 | 2251.6029 | n | 309.9919 |  |  |  | 17088.5183 | 18195.4811 | 51645.927 | 141654.227 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-10-03 | 9:33 | 100 | 12380 | 10090 | 7.46 | 60.4 | 1306 | 1618.8 | 16333.692 |  | 21 | 28.1057 | 235.2319 | 38.1186 | 301.4562 | 3041.6935 | n | 424.8244 |  |  |  | 16660.2713 | 17966.5671 | 53358.915 | 144401.195 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-10-10 | 8:58 | 116 | 23900 | 11520 | 7.24 | 38.4 | 1278 | 1250 | 14400 |  | 26.71 | 119.3961 | 135.7716 | 22.7963 | 277.964 | 3202.1448 | n | 423.6469 |  |  |  | 15267.3037 | 17539.7388 | 58930.785 | 149523.135 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-10-17 | 9:14 | 132 | 37140 | 13240 | 7.55 | 19.6 | 1646.4 | 1315 | 17410.6 |  | 93.57 | 160.6223 | 129.126 | 6.9843 | 296.7326 | 3928.7392 | n | 506.3283 |  |  |  | 15520.7913 | 17683.4354 | 57916.835 | 147798.775 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-10-24 | 9:29 | 122 | 49350 | 12210 | 7.57 | 43.2 | 1466.4 | 1324 | 16166.04 |  | 101.2 | 96.8836 | 152.3858 | 11.5969 | 260.8663 | 3185.1775 | n | 422.2445 |  |  |  | 16077.583 | 17554.1688 | 55689.668 | 149349.975 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-10-31 | 9:05 | 127 | 62050 | 12700 | 7.41 | 84 | 1679.2 | 1443 | 18326.1 |  | 109.5 | 65.1498 | 217.0323 | 12.3239 | 294.506 | 3740.2267 | n | 506.2544 |  |  |  | 16575.685 | 17459.4287 | 53697.26 | 150486.855 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-11-07 | 8:55 | 148 | 75820 | 13770 | 7.51 | 65.6 | 1476.8 | 1447 | 19925.19 |  | 100.9 | 122.9497 | 164.0319 | 11.2209 | 298.2025 | 4106.2479 | n | 540.537 |  |  |  | 17956.9825 | 17494.9113 | 48172.07 | 150061.065 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-11-14 | 9:22 | 136 | 89390 | 13570 | 7.53 | 30.4 | 1358.6 | 1304 | 17695.28 |  | 79.08 | 138.7415 | 149.7608 | 4.5864 | 293.0887 | 3977.2135 | n | 516.9968 |  |  |  | 18028.1525 | 17267.1679 | 47887.39 | 152793.985 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-11-21 | 9:31 | 139 | 103300 | 13910 | 7.4 | 34.4 | 1460 | 1382 | 19223.62 |  | 107.9 | 109.3833 | 165.8298 | 6.8448 | 282.0579 | 3923.4259 | n | 517.1234 |  |  |  | 18792.5475 | 17319.5496 | 44829.81 | 152165.405 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-11-28 | 9:28 | 140 | 117250 | 13950 | 7.58 | 35.6 | 1153.4 | 1414 | 19725.3 |  | 91.74 | 109.185 | 162.6677 | 8.9987 | 280.8514 | 3917.8765 | n | 517 |  |  |  | 19142.3475 | 17459.4346 | 43430.61 | 150486.785 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-12-05 | 9:02 | 130 | 130170 | 12920 | 7.44 | 52.8 | 2737 | 1514 | 19560.88 |  | 114.1 | 184.192 | 138.648 | 9.5312 | 332.3712 | 4294.2364 | n | 552.8774 |  |  |  | 19051.27 | 17425.1854 | 43794.92 | 150897.775 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-12-12 | 9:00 | 104 | 140450 | 10280 | 7.62 | 51.2 | 1255.8 | 1298 | 13343.44 |  | 59.85 | 108.6008 | 191.7532 | 6.4103 | 306.7643 | 3153.5371 | n | 417.4314 |  |  |  | 17963.31 | 17170.7513 | 48146.76 | 153950.985 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-12-19 | 9:22 | 123 | 152810 | 12360 | 7.52 | 33.2 | 1236.6 | 1537 | 18997.32 |  | 108 | 153.7576 | 204.6425 | 2.1941 | 360.5942 | 4456.9443 | n | 582.3748 |  |  |  | 17906.735 | 17592.2885 | 48373.06 | 148892.538 | 8000 | 30000 | 100 | 6 | 10 | 35000
2014-12-26 | 8:51 | 135 | 166330 | 13520 | 7.3 | 45.6 | 1686.4 | 1319 | 17832.88 |  | 114.6 | 35.2417 | 203.2754 | 2.577 | 241.0941 | 3259.5926 | n | 443.5701 |  |  |  | 17433.63 | 17717.2208 | 50265.48 | 147393.35 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-01-02 | 8:30 | 115 | 177760 | 11430 | 7.53 | 46 |  | 1337.5 | 15287.625 |  | 72.73 | 111 | 141 | 6 | 258 | 2948.94 | n | 386.244 |  |  |  | 16365.3162 | 17791.1896 | 54538.735 | 146505.725 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-01-09 | 9:25 | 126 | 190360 | 12600 | 7.52 | 34.8 | 1274.2 | 1357.7 | 17107.02 |  | 94.21 | 118.7565 | 172.9453 | 4.645 | 296.3468 | 3733.9698 | n | 490.5214 |  |  |  | 17306.2113 | 17765.8913 | 50775.155 | 146809.305 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-01-16 | 9:22 | 134 | 203800 | 13440 | 7.47 | 51.6 | 1783 | 1375.9 | 18492.096 |  | 101.3 | 142.0144 | 202.3325 | 5.0957 | 349.4427 | 4696.5092 | n | 616.3486 |  |  |  | 17179.9052 | 17959.7293 | 51280.379 | 144483.249 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-01-23 | 8:22 | 178 | 216650 | 12850 | 7.55 | 43.2 | 1198.6 | 1441.5 | 18523.275 |  | 123.9 | 131.2842 | 152.7843 | 3.8311 | 287.8995 | 3699.5087 | n | 481.9229 |  |  |  | 17352.504 | 17976.1605 | 50589.984 | 144286.074 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-01-30 | 9:03 | 136 | 230070 | 13420 | 7.62 | 63.2 | 1245.2 | 1573.7 | 21119.054 |  | 137.1 | 129.8701 | 185.5748 | 11.5467 | 326.9916 | 4388.2271 | n | 578.6884 |  |  |  | 18810.3613 | 18075.6492 | 44758.555 | 143092.21 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-02-06 | 8:22 | 145 | 244540 | 14470 | 7.58 | 60.4 | 1036 | 1387.5 | 20077.125 |  | 119.4 | 112.7336 | 157.3632 | 7.769 | 277.8658 | 4020.7175 | n | 528.9131 |  |  |  | 19552.8875 | 18274.1362 | 41788.45 | 140710.365 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-02-13 | 9:27 | 104 | 254610 | 10070 | 7.42 | 96 | 1133.2 | 1345.2 | 13546.164 |  | 82.5 | 71.0931 | 184.4221 | 6.3261 | 261.8413 | 2636.7414 | n | 353.3393 |  |  |  | 18316.4045 | 17801.0149 | 46734.382 | 146387.821 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-02-20 | 9:26 | 137 | 268250 | 13640 | 7.49 | 39.2 | 1262.2 | 1455.15 | 19848.246 |  | 98.02 | 246.9381 | 162.0471 | 8.1922 | 417.1774 | 5690.2997 | n | 727.3995 |  |  |  | 18647.6473 | 17811.2604 | 45409.411 | 146264.875 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-02-27 | 9:24 | 119 | 280210 | 11960 | 7.39 | 44.8 | 1199.8 | 1381.634 | 16524.3426 |  | 116.6 | 118.055 | 139.5623 | 5.2238 | 262.841 | 3143.5788 | n | 410.3729 |  |  |  | 17498.9694 | 17558.2156 | 50004.1224 | 149301.4124 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-03-06 | 9:00 | 98 | 289930 | 9720 | 7.6 | 96.4 | 1583.8 | 1854.28 | 18023.6016 |  | 150.9 | 172.7917 | 160.9057 | 8.3054 | 342.0027 | 3324.2665 | n | 430.7533 |  |  |  | 16985.5886 | 17948.2291 | 52057.6458 | 144621.2508 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-03-13 | 8:49 | 120 | 300800 | 10870 | 7.66 | 91.6 | 1463 | 1687.24 | 18340.2988 |  | 143 | 133.8796 | 202.5923 | 15.3472 | 351.819 | 3824.273 | n | 506.2326 |  |  |  | 18184.1223 | 17893.4773 | 47263.511 | 145278.272 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-03-20 | 9:21 | 120 | 312850 | 12050 | 7.6 | 60 | 1686.97 | 1404 | 16918.2 |  | 166.3 | 172.7827 | 174.2331 | 12.1882 | 359.2039 | 4328.4074 | n | 563.7868 |  |  |  | 17451.6108 | 17817.254 | 50193.557 | 146192.952 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-03-27 | 9:39 | 112 | 323110 | 10260 | 7.51 | 63.2 | 2395.4 | 1848.14 | 18961.9164 |  | 137.5 | 209.9674 | 185.3464 | 10.2683 | 405.5821 | 4161.2728 | n | 538.3243 |  |  |  | 18061.0042 | 18123.445 | 47755.9832 | 142518.6606 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-04-02 | 8:47 | 108 | 332060 | 8950 | 7.82 | 58.4 |  | 1912.5 | 19969.6875 |  | 139.5 | 187.8418 | 144.7584 | 12.4665 | 345.0666 | 3603.0706 | n | 398.7083 |  |  |  | 18547.5257 | 18362.0006 | 45809.8973 | 139655.9931 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-04-10 | 9:37 | 144 | 346560 | 14500 | 7.79 | 36.8 | 1910 | 1965.6 | 24938.55 |  | 183.1 | 246.9654 | 200.7354 | 6.505 | 454.2057 | 5762.7352 | n | 847.132 | 0 |  |  | 20197.0885 | 18899.2051 | 39211.6461 | 133209.5391 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-04-17 | 9:19 | 103 | 356790 | 10230 | 7.77 | 64 | 1516.6 | 1910.96 | 19549.1208 |  | 131.4 | 179.8569 | 232.2141 | 5.7557 | 417.8267 | 4274.3669 | n | 558.9225 | 0 |  |  | 20854.8187 | 18984.6922 | 36580.7253 | 132183.6933 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-04-24 | 9:22 | 100 | 366800 | 10010 | 7.58 | 83.2 | 1198.6 | 1803.37 | 18051.7337 |  | 143.2 | 99.2998 | 213.5566 | 7.761 | 320.6174 | 3209.3799 | n | 427.7556 | 0 |  |  | 20627.273 | 18729.0822 | 37490.908 | 135251.0136 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-05-01 | 9:22 | 113 | 377180 | 10380 | 7.69 | 90.4 | 1654 | 2038.2725 | 21157.2683 |  | 144.7 | 163.8952 | 143.7789 | 23.9981 | 331.6722 | 3442.757 | n | 450.5221 | 0 |  |  | 20924.1682 | 18819.0941 | 36303.3272 | 134170.8703 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-05-08 | 9:23 | 113 | 387830 | 10650 | 7.65 | 59.2 | 1461.6 | 1740.41 | 18535.3665 |  | 129.9 | 134.4012 | 256.3835 | 8.9038 | 399.6884 | 4256.6818 | n | 565.0175 | 0 |  |  | 19323.3723 | 19234.861 | 42706.5107 | 129181.6678 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-05-15 | 8:53 | 113 | 398230 | 10400 | 7.76 | 72.8 | 1462.8 | 1912.09 | 19885.736 |  | 142.6 | 187.89 | 221.73 | 19.75 | 429.37 | 4465.448 | n | 586.514 | 0 |  |  | 19407.5261 | 19237.9852 | 42369.8955 | 129144.1778 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-05-22 | 9:02 | 85 | 405690 | 7460 | 7.38 | 36.8 | 1190.6 | 1811.63 | 13514.7598 |  | 33.68 | 61.7402 | 289.8848 | 16.5518 | 368.1768 | 2746.5992 | n | 374.7403 | 0 |  |  | 18273.2826 | 18987.1866 | 46906.8694 | 132153.7606 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-05-29 | 9:24 | 89 | 413590 | 7900 | 7.54 | 60.4 | 1323.4 | 1847.84 | 14597.936 |  | 28.12 | 58.3211 | 290.2928 | 91.4911 | 440.1049 | 3476.8289 | n | 489.3252 | 0 |  |  | 16633.4496 | 18701.7145 | 53466.2017 | 135579.4262 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-06-05 | 9:38 | 96 | 422020 | 8430 | 7.61 | 59.2 | 1361 | 1765.26 | 14881.1418 |  | 70.25 | 40.5667 | 303.5299 | 71.8044 | 415.901 | 3506.0458 | n | 493.006 | 0 |  |  | 15719.8934 | 18413.4514 | 57120.4264 | 139038.5832 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-06-12 | 9:27 | 111 | 432050 | 10030 | 7.96 | 99.2 | 1487.8 | 2089.66 | 20959.2898 |  | 161 | 238.5593 | 281.8449 | 18.2189 | 538.6231 | 5402.3899 | n | 707.5658 | 0 |  |  | 15988.2818 | 18750.2089 | 56046.8726 | 134997.4934 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-06-19 | 9:07 | 96 | 440700 | 8650 | 7.54 | 39.2 | 1239.6 | 1652.68 | 14295.682 |  | 75.66 | 46.514 | 255.7411 | 25.151 | 327.4061 | 2832.0627 | n | 389.7891 | 0 |  |  | 16183.5124 | 18361.356 | 55265.9504 | 139663.7278 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-06-26 | 9:27 | 118 | 451500 | 10800 | 7.76 | 80 | 1403.8 | 1872.96 | 20227.968 |  | 157.8 | 105.2934 | 213.6572 | 15.6018 | 334.5525 | 3613.167 | n | 483.0376 | 0 |  |  | 17591.0204 | 18382.8794 | 49635.9184 | 139405.4473 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-07-03 | 9:03 | 108 | 461350 | 9850 | 7.46 | 88 | 1183 | 1706.68 | 16810.798 |  | 104.2 | 17.6139 | 331.633 | 27.9165 | 377.1634 | 3715.0596 | n | 517.8035 | 0 |  |  | 18073.4345 | 17705.5667 | 47706.2622 | 147533.1993 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-07-10 | 9:48 | 113 | 471480 | 10130 | 7.66 | 61.6 | 1302.2 | 1662.69 | 16843.0497 |  | 84.96 | 154.4623 | 165.7743 | 20.9985 | 341.2352 | 3456.7122 | n | 454.2329 | 0 |  |  | 17044.3744 | 17480.0608 | 51822.5023 | 150239.2704 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-07-17 | 9:25 | 93 | 479750 | 8270 | 7.68 | 68.8 | 1582.8 | 1831.95 | 15150.2265 |  | 110 | 14.8747 | 332.091 | 5.5753 | 352.541 | 2915.5142 | n | 402.8273 | 0 |  |  | 17258.0105 | 17238.2685 | 50967.9578 | 153140.7776 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-07-24 | 9:03 | 90 | 487680 | 7930 | 7.7 | 99.2 | 1522.2 | 1716.03 | 13608.1179 |  | 77.03 | 13.2863 | 288.8314 | 26.31 | 328.4277 | 2604.4314 | n | 363.6669 | 0 |  |  | 15603.048 | 16609.1727 | 57587.8079 | 160689.928 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-07-31 | 9:25 | 118 | 498410 | 10730 | 7.55 | 92.4 | 1493.2 | 1873.47 | 20102.3331 |  | 141.3 | 194 | 201.6682 | 7 | 402.6682 | 4320.6297 | n | 561.1159 | 0 |  |  | 16425.9318 | 16739.7532 | 54296.2728 | 159122.9614 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-08-07 | 9:33 | 116 | 9080 | 10639 | 7.9 | 93.6 | 1546.4 | 2036.28 | 21663.9829 |  | 127.2 | 147.7469 | 374.5922 | 8.6874 | 531.0265 | 5649.591 | n | 755.3771 | 0 |  |  | 17631.1651 | 16887.9405 | 49475.3396 | 157344.7145 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-08-14 | 9:25 | 92 | 16880 | 7800 | 7.63 | 56 | 1133.2 | 1566.12 | 12215.736 |  | 28.31 | 24.1064 | 274.1434 | 23.6453 | 321.8951 | 2510.7819 | n | 348.5788 | 2.6 |  |  | 16897.5425 | 16779.6885 | 52409.8301 | 158643.7383 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-08-21 | 9:35 | 87 | 25520 | 8640 | 7.57 | 51.6 | 1034.4 | 1431.17 | 12365.3088 |  | 22.94 | 31.7484 | 228.7905 | 30.6915 | 291.2304 | 2516.231 | n | 349.4997 | 0 |  |  | 16586.8402 | 16593.6362 | 53652.6392 | 160876.3655 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-08-28 | 9:00 | 116 | 35140 | 9620 | 7.7 | 76.4 | 1073.4 | 1715.74 | 16505.4188 |  | 90.21 | 6.4338 | 286.1524 | 20.4309 | 313.0171 | 3011.2249 | n | 420.6083 | 0 |  |  | 15687.6116 | 16728.9926 | 57249.5535 | 159252.0885 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-09-04 | 9:31 | 108 | 45930 | 10790 | 7.66 | 71.6 | 1197 | 1853.06 | 19994.5174 |  | 128.3 | 30.3466 | 252.6026 | 12.6735 | 295.6227 | 3189.7685 | n | 438.9895 | 0 |  |  | 15270.2452 | 16648.5949 | 58919.019 | 160216.8609 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-09-11 | 7:56 | 132 | 57670 | 11740 | 7.94 | 70.4 | 1211 | 1869.28 | 21945.3472 |  | 132.4 | 142.0102 | 210.1047 | 3.332 | 355.4468 | 4172.946 | n | 547.6977 | 0 |  |  | 17702.648 | 17286.067 | 49189.4078 | 152567.1957 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-09-18 | 9:22 | 82 | 65850 | 8180 | 7.95 | 55.2 | 1101 | 1776.89 | 14534.9602 |  | 50.19 | 99.9946 | 205.1387 | 20.4208 | 325.5541 | 2663.0328 | n | 357.3543 | 0 |  |  | 18245.0609 | 16811.6497 | 47019.7564 | 158260.2035 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-09-25 | 9:22 | 120 | 76880 | 11030 | 7.68 | 51.6 | 1060 | 1545.39 | 17045.6517 |  | 65.2 | 71.6716 | 209.1631 | 20.458 | 301.2927 | 3323.2587 | n | 450.6978 | n/a |  |  | 18380.1191 | 16831.2209 | 46479.5235 | 158025.3498 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-10-02 | 9:27 | 101 | 86970 | 10090 | 7.62 | 30.4 | 1036.4 | 1067.55 | 10771.5795 |  | 18.32 | 39.3079 | 190.6842 | 14.6218 | 244.6139 | 2468.1543 | n | 337.8931 | n/a |  |  | 16074.3846 | 16325.265 | 55702.4614 | 164096.82 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-10-09 | 9:27 | 136 | 99620 | 12650 | 7.6 | 44.4 | 1089.6 | 1256.2 | 15890.93 |  | 38.15 | 117.2012 | 156.7612 | 14.1143 | 288.0767 | 3644.1697 | n | 481.0113 | 2.0726 |  |  | 14560.7804 | 16386.9903 | 61756.8786 | 163356.1165 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-10-16 | 8:59 | 116 | 109960 | 10340 | 7.94 | 79.6 | 1498 | 1937.15 | 20030.131 |  | 145.6 | 181.8659 | 183.6923 | 6.1007 | 371.6589 | 3842.9532 | n | 498.4475 | n/a |  |  | 15934.5731 | 16922.1581 | 56261.7078 | 156934.1034 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-10-23 | 9:30 | 100 | 119990 | 10030 | 8.23 | 76 | 1692.4 | 2151.42 | 21578.7426 |  | 147 | 223.9559 | 228.3909 | 7.3366 | 459.6834 | 4610.6245 | n | 598.158 | n/a |  |  | 17067.8458 | 17045.1922 | 51728.6169 | 155457.6939 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-10-30 | 9:24 | 98 | 128810 | 8820 | 7.82 | 72.4 | 1740.2 | 1802.7046 | 15899.8544 |  | 59.33 | 79.5534 | 282.0366 | 21.269 | 382.859 | 3376.8163 | n | 458.9574 | 0 |  |  | 18349.9145 | 16564.8481 | 46600.342 | 161221.8224 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-11-06 | 9:30 | 121 | 140880 | 12070 | 7.78 | 86 | 1592.4 | 1859.88 | 22448.7516 |  | 133.4 | 183.5127 | 257.9313 | 7.9109 | 449.3549 | 5423.7133 | n | 711.9448 | 0 |  |  | 19989.3699 | 17417.5994 | 40042.5204 | 150988.8068 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-11-13 | 9:32 | 124 | 152190 | 11310 | 8.05 | 88 | 1476.8 | 1785.12 | 20189.7072 |  | 125.7 | 92.2494 | 144.4173 | 13.617 | 250.2837 | 2830.7092 | n | 376.0335 | 0 |  |  | 20029.2639 | 18069.6326 | 39882.9442 | 143164.4084 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-11-20 | 9:24 | 108 | 162990 | 10800 | 7.86 | 76 | 1175 | 1833 | 19796.4 |  | 147.1 | 67.7416 | 198.779 | 5.0809 | 271.6016 | 2933.297 | n | 393.9514 | 0 |  |  | 19583.6783 | 18343.8811 | 41665.2868 | 139873.4272 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-11-27 | 9:26 | 83 | 171360 | 8370 | 7.76 | 56 | 1172.6 | 1688.55 | 14133.1635 |  | 68.14 | 73.616 | 197.4947 | 26.029 | 297.1397 | 2487.0594 | n | 337.9206 | 2.3884 |  |  | 19142.0056 | 17855.4349 | 43431.9777 | 145734.7811 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-12-04 | 9:24 | 102 | 181550 | 10190 | 7.73 | 59 | 1071 | 1558.24 | 15878.4656 |  | 77.14 | 43.0349 | 217.9631 | 15.6434 | 276.6414 | 2818.9756 | n | 385.9922 | 0 |  |  | 17499.4341 | 17349.8614 | 50002.2637 | 151801.6627 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-12-11 | 9:28 | 95 | 190080 | 8530 | 7.77 | 84.4 | 1045.2 | 1576.53 | 13447.8009 |  | 69.83 | 3.7879 | 238.2099 | 11.6404 | 253.6382 | 2163.5339 | n | 301.4981 | 0 |  |  | 15813.9575 | 17259.2648 | 56744.17 | 152888.822 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-12-18 | 9:25 | 95 | 199640 | 9560 | 7.65 | 60.4 | 1031.4 | 1564.79 | 14959.3924 |  | 25.77 | 40.3607 | 225.5119 | 56.2703 | 322.1429 | 3079.6858 | n | 431.5723 | 0 |  |  | 14604.7056 | 17085.4099 | 61581.1776 | 154975.0813 | 8000 | 30000 | 100 | 6 | 10 | 35000
2015-12-24 | 8:15 | 79 | 207550 | 7910 | 7.84 | 91.2 | 1080.6 | 1617.81 | 12796.8771 |  | 89.51 | 55.3643 | 203.2497 | 17.7408 | 276.3548 | 2185.9665 | n | 297.8341 | 0 |  |  | 14270.634 | 17254.1847 | 62917.464 | 152949.7837 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-01-01 | 10:02 | 120 | 219060 | 11510 | 7.63 | 67.6 | 1034 | 1674.97 | 19278.9047 |  | 135.4 | 89.9606 | 137.7196 | 33.5598 | 261.24 | 3006.8724 | n | 405.7826 | 0 |  |  | 15120.7438 | 17536.5159 | 59517.0249 | 149561.809 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-01-08 | 9:24 | 99 | 227980 | 8920 | 8.03 | 60 | 1229.4 | 1625.68 | 14501.0656 |  | 148.6 | 57.6908 | 173.6388 | 13.8481 | 245.1777 | 2186.9854 | n | 296.1471 | 0 |  |  | 15384.06 | 17075.7605 | 58463.7602 | 155090.8744 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-01-15 | 9:31 | 88 | 236750 | 8770 | 7.84 | 59.2 | 1063 | 1519.68 | 13327.5936 |  | 72.73 | 72.5755 | 199.5895 | 160.6879 | 432.8529 | 3796.1199 | n | 545.5637 | 0 |  |  | 14976.1102 | 16388.1647 | 60095.559 | 163342.0234 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-01-22 | 9:23 | 115 | 248300 | 11550 | 7.89 | 43.2 | 1380.4 | 1736.51 | 20056.6905 |  | 124.1 | 188.7245 | 168.7341 | 26.1607 | 383.6194 | 4430.8038 | n | 579.5915 | 0 |  |  | 16791.0636 | 16734.5677 | 52835.7456 | 159185.1873 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-01-29 | 9:34 | 105 | 258760 | 10460 | 8.04 | 70.8 | 1161.6 | 1788.31 | 18705.7226 |  | 89.6 | 107.5747 | 175.357 | 21.1911 | 304.1228 | 3181.1244 | n | 424.5626 | 0 |  |  | 16647.7681 | 16422.6486 | 53408.9277 | 162928.2163 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-02-05 | 8:48 | 117 | 269460 | 10700 | 7.85 | 81.6 | 1087.4 | 1701.8 | 18209.26 |  | 90.73 | 140.7403 | 205.8074 | 27.1641 | 373.7117 | 3998.7155 | n | 532.2148 | 0 |  |  | 17574.8167 | 16257.6114 | 49700.7333 | 164908.6635 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-02-12 | 8:51 | 116 | 281030 | 11570 | 8.12 | 64.4 | 1063 | 1722.69 | 19931.5233 |  | 137.2 | 118.6961 | 165.4286 | 29.601 | 313.7257 | 3629.8059 | n | 484.7486 | 0 |  |  | 19225.7991 | 16268.8716 | 43096.8036 | 164773.5402 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-02-19 | 9:12 | 107 | 290770 | 9740 | 7.88 | 77.6 | 1134.2 | 1697.64 | 16535.0136 |  | 71.7 | 124.1318 | 141.7458 | 48.5277 | 314.4052 | 3062.3069 | n | 412.1029 | 0 |  |  | 18345.3799 | 16469.0258 | 46618.4805 | 162371.6901 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-02-26 | 8:20 | 124 | 303220 | 12450 | 8.26 | 87.6 | 1112.4 | 1898.34 | 23634.333 |  | 126.4 | 196.2787 | 257.9288 | 28.2039 | 482.4114 | 6006.0214 | n | 794.0286 | 0 |  |  | 19577.5325 | 17115.3481 | 41689.8701 | 154615.8227 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-03-04 | 9:26 | 126 | 315770 | 12550 | 7.82 | 60.8 | 982 | 1677.22 | 21049.111 |  | 124 | 118.4484 | 162.023 | 19.4617 | 299.9332 | 3764.1614 | n | 499.0348 |  |  |  | 20287.4952 | 17748.7906 | 38850.0191 | 147014.5126 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-03-11 | 9:24 | 90 | 324780 | 9010 | 7.35 | 68.4 | 872.4 | 1408.29 | 12688.6929 |  | 60.45 | 107.8048 | 112.9583 | 95.8819 | 316.645 | 2852.9711 | n | 396.319 | 0 |  |  | 18476.7876 | 17559.5657 | 46092.8495 | 149285.2121 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-03-18 | 9:35 | 104 | 334950 | 10170 | 7.47 | 44.4 | 924.6 | 1588.36 | 16153.6212 |  | 70.48 | 56.1701 | 199.8506 | 64.6568 | 320.6775 | 3261.2901 | n | 455.8989 | 0 |  |  | 18381.4395 | 17839.2943 | 46474.2419 | 145928.468 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-03-23 | 9:00 | 105 | 345570 | 10620 | 8.04 | 95.6 | 1004.8 | 1751.39 | 18599.7618 |  | 124.3 | 98.2702 | 147.3789 | 37.6369 | 283.286 | 3008.4971 | n | 406.1523 | 0 |  |  | 17122.7967 | 17782.6991 | 51508.8131 | 146607.6109 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-04-01 | 8:27 | 136 | 359220 | 13650 | 7.65 | 66 | 926.2 | 1603.48 | 21887.502 |  | 133 | 40.8386 | 197.2322 | 44.5002 | 282.571 | 3857.0943 | n | 537.629 | 0 |  |  | 17332.3945 | 18398.2355 | 50670.4221 | 139221.1745 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-04-08 | 8:34 | 112 | 370420 | 11200 | 7.68 | 90.8 | 943.2 | 1553.72 | 17401.664 |  | 77.79 | 75.3924 | 253.2879 | 0 | 328.6803 | 3681.2192 | n | 494.2619 | 0 |  |  | 18510.6372 | 18737.7413 | 45957.451 | 135147.1041 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-04-15 | 8:28 | 115 | 381960 | 11540 | 7.87 | 76.8 | 1074.2 | 1678.04 | 19364.5816 |  | 134.7 | 66.9942 | 227.2995 | 42.9068 | 337.2004 | 3891.2932 | n | 535.7768 | 0 |  |  | 19313.3773 | 18680.0656 | 42746.4906 | 135839.213 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-04-22 | 8:25 | 142 | 394610 | 12650 | 8.56 | 72 | 1022.2 | 1756.7658 | 22223.0874 |  | 129.3 | 141.6353 | 139.3198 | 35.3284 | 316.2835 | 4000.9858 | n | 530.5979 |  |  |  | 20219.2087 | 18973.1793 | 39123.165 | 132321.8482 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-04-29 | 8:30 | 117 | 406360 | 11750 | 7.87 | 65.6 | 1105.8 | 1728.44 | 20309.17 |  | 131.1 | 156.5311 | 139.34 | 30.5769 | 326.4479 | 3835.7634 | n | 504.8398 | 0 |  |  | 19824.6257 | 19148.1718 | 40701.497 | 130221.9382 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-05-06 | 8:30 | 108 | 417100 | 10740 | 7.77 | 73.2 | 1124.2 | 1754.83 | 18846.8742 |  | 83.25 | 110.4414 | 302.9394 | 51.5367 | 464.9175 | 4993.2142 | n | 681.9908 | 0 |  |  | 20185.9283 | 19057.7844 | 39256.2868 | 131306.5873 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-05-13 | 8:38 | 112 | 428300 | 11200 | 7.69 | 65.6 | 1130.8 | 1710.97 | 19162.864 |  | 140.6 | 75.0365 | 218.5823 | 32.3252 | 325.944 | 3650.573 | n | 498.1651 | 0 |  |  | 20135.4989 | 19276.7719 | 39458.0044 | 128678.7369 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-05-20 | 8:28 | 120 | 440360 | 12060 | 7.65 | 73.6 | 1191.6 | 1593.49 | 19217.4894 |  | 132.1 | 65.049 | 254.1072 | 40.8754 | 360.0316 | 4341.981 | n | 597.9839 | 0 |  |  | 19384.0994 | 18908.7016 | 42463.6024 | 133095.5805 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-05-27 | 8:37 | 117 | 451980 | 11620 | 7.75 | 79.2 | 1080.8 | 1656.42 | 19247.6004 |  | 136.3 | 16.9765 | 235.4541 | 36.5315 | 288.9621 | 3357.7401 | n | 471.1586 | 0 |  |  | 19118.707 | 18758.5757 | 43525.172 | 134897.0911 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-06-03 | 8:33 | 121 | 464030 | 12050 | 7.62 | 63.6 | 931 | 1515.54 | 18262.257 |  | 111.1 | 30.2745 | 249.9164 | 47.5383 | 327.7291 | 3949.1359 | n | 553.2673 | 0 |  |  | 18972.5527 | 19223.0394 | 44109.7892 | 129323.527 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-06-10 | 8:28 | 113 | 475380 | 11350 | 7.46 | 74.4 | 900.6 | 1486.26 | 16869.051 |  | 112.6 | 44.934 | 213.0359 | 44.6843 | 302.6542 | 3435.1249 | n | 477.8012 | 0 |  |  | 18399.0995 | 19282.6586 | 46403.6022 | 128608.0972 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-06-17 | 8:47 | 134 | 488780 | 13400 | 7.86 | 66 | 924.4 | 1569.5 | 21031.3 |  | 147.7 | 67.5586 | 183.5727 | 22.2955 | 273.4269 | 3663.9199 | n | 497.3738 | 0 |  |  | 18852.5521 | 19485.2867 | 44589.7916 | 126176.559 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-06-24 | 8:31 | 136 | 2330 | 13548 | 7.81 | 75.6 | 913.6 | 1632.23 | 22113.452 |  | 156.3 | 43.7075 | 197.4673 | 28.8402 | 270.015 | 3658.1629 | n | 504.5629 | 0 |  |  | 19569.015 | 19504.1159 | 41723.94 | 125950.609 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-07-01 | 8:36 | 101 | 12500 | 10170 | 7.65 | 65.2 | 890 | 1635.98 | 16637.9166 |  | 96.11 | 116.2406 | 227.1657 | 49.0449 | 392.4512 | 3991.2285 | n | 541.9565 | 0 |  |  | 19162.9299 | 19440.4703 | 43348.2804 | 126714.3564 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-07-08 | 8:33 | 125 | 24800 | 12300 | 7.31 | 74.4 | 804.4 | 1503.09 | 18488.007 |  | 122.8 | 26.5665 | 201.7413 | 40.5519 | 268.8597 | 3306.9741 | n | 463.3241 | 0 |  |  | 19567.6689 | 19367.4224 | 41729.3244 | 127590.931 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-07-15 | 8:41 | 129 | 37700 | 12900 | 7.59 | 91.6 | 1028.8 | 1782 | 22987.8 |  | 100 | 221.0236 | 239.2952 | 42.0247 | 502.3435 | 6480.2308 | n | 856.2955 | 0 |  |  | 20056.7939 | 19431.1485 | 39772.8244 | 126826.2184 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-07-22 | 8:39 | 115 | 49650 | 11950 | 7.31 | 97 | 892.6 | 1761.58 | 21050.881 |  | 133.5 | 5.6732 | 323.7997 | 42.5779 | 372.0508 | 4446.0066 | n | 626.3423 | 0 |  |  | 19791.1512 | 19492.9577 | 40835.3954 | 126084.5074 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-07-29 | 9:02 | 147 | 63000 | 13350 | 7.75 | 95.2 | 935.2 | 1659.62 | 22155.927 |  | 112.9 | 65.0838 | 314.2463 | 35.1943 | 414.5243 | 5533.8994 | n | 761.0853 | unit shutdown |  |  | 21170.6538 | 19768.7121 | 35317.385 | 122775.4546 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-08-05 | 8:58 | 35 | 66460 | 3460 | 7.46 | 150 | 1181.8 | 1894.74 | 6555.8004 |  | 25.2 | 700.6938 | 306.0966 | 142.3834 | 1149.1738 | 3976.1413 | n | 516.1808 | unit shutdown |  |  | 18187.6021 | 18718.1235 | 47249.5916 | 135382.5182 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-08-12 | 9:10 | 47 | 71210 | 4750 | 7.75 | 76.4 | 802.2 | 1377.93 | 6545.1675 |  | 13.8 | 541.2915 | 228.463 | 88.4133 | 858.1678 | 4076.2971 | n | 525.6611 | unit shutdown |  |  | 14076.944 | 17662.0967 | 63692.2241 | 148054.8401 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-08-19 | 8:47 | 107 | 81660 | 10450 | 7.6 | 56.4 | 898.2 | 1542.11 | 16115.0495 |  | 53.07 | 71.799 | 288.3684 | 20.7784 | 380.9458 | 3980.884 | n | 542.4266 | unit shutdown |  |  | 12842.9861 | 17401.0508 | 68628.0556 | 151187.391 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-08-26 | 8:27 | 144 | 95980 | 14320 | 7.75 | 56 | 878.4 | 1462.14 | 20937.8448 |  | 94.36 | 3.7788 | 388.7147 | 45.9435 | 438.437 | 6278.4176 | n | 883.9251 | 0 |  |  | 12538.4656 | 17624.0164 | 69846.1378 | 148511.8032 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-09-02 | 8:28 | 98 | 107120 | 11140 | 7.22 | 57.6 |  | 1575.81 | 17554.5234 |  | 102.6 | 174.9753 | 284.3768 | 23.7163 | 483.0683 | 5381.381 | n | 714.8782 | 0 |  |  | 15288.1463 | 17681.1391 | 58847.4148 | 147826.3308 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-09-09 | 8:30 | 156 | 121220 | 14100 | 7.42 | 57.6 |  | 1702.12 | 23999.892 |  | 128.1 | 93.0593 | 330.2598 | 55.6107 | 478.9298 | 6752.9096 | n | 928.6645 | 0 |  |  | 19651.8274 | 17928.5218 | 41392.6903 | 144857.7388 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-09-16 | 8:38 | 118 | 133000 | 11780 | 7.87 | 59.6 |  | 1922.2 | 22643.516 |  | 92.88 | 141.9643 | 416.5269 | 25.0289 | 583.5201 | 6873.8671 | n | 927.6895 | 0 |  |  | 21283.944 | 17972.6938 | 34864.2238 | 144327.6748 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-09-24 | 8:31 | 127 | 145640 | 12640 | 7.59 | 66.4 |  | 1764.58 | 22304.2912 |  | 132 | 72.0778 | 335.1191 | 45.2341 | 452.431 | 5718.7277 | n | 788.1785 | 0 |  |  | 21625.5556 | 18444.8917 | 33497.7774 | 138661.3002 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-09-30 | 9:03 | 141 | 159770 | 14130 | 7.76 | 65.6 |  | 1695.22 | 23953.4586 |  | 164.7 | 92.8882 | 221.3699 | 33.7222 | 347.9802 | 4916.9605 | n | 667.3078 | 0 |  |  | 23225.2895 | 18900.3459 | 27098.8422 | 133195.8486 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-10-07 | 8:44 | 116 | 171430 | 11660 | 7.86 | 72.8 |  | 1764.94 | 20579.2004 |  | 126 | 72.8694 | 251.7297 | 32.5258 | 357.1248 | 4164.0748 | n | 569.5521 | 0 |  |  | 22370.1165 | 18699.6293 | 30519.5338 | 135604.4482 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-10-14 | 8:26 | 128 | 184170 | 12740 | 7.7 | 87.2 |  | 1964 | 25021.36 |  | 108.3 | 322.1305 | 277.9422 | 21.9798 | 622.0525 | 7924.9487 | n | 1026.9606 | 0 |  |  | 22964.5776 | 19030.5026 | 28141.6898 | 131633.9692 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-10-21 | 8:32 | 124 | 196550 | 12380 | 7.61 | 89.2 |  | 1673.55 | 20718.549 |  | 107 | 85.1978 | 236.0191 | 38.5142 | 359.7311 | 4453.4711 | n | 607.9548 | 0 |  |  | 22568.142 | 18910.7211 | 29727.432 | 133071.3472 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-10-28 | 8:37 | 142 | 210760 | 14210 | 7.53 | 76.8 |  | 1379.96 | 19609.2316 |  | 96.8 | 76.0576 | 193.6991 | 11.4626 | 281.2194 | 3996.127 | n | 537.0649 | 0 |  |  | 21482.0853 | 19998.507 | 34071.659 | 120017.916 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-11-04 | 9:33 | 136 | 222910 | 12150 | 7.86 | 77.2 |  | 1780.21 | 21629.5515 |  | 125.2 | 164.5513 | 159.4046 | 27.7651 | 351.721 | 4273.41 | n | 561.9804 | 0 |  |  | 21744.673 | 21255.539 | 33021.3079 | 104933.532 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-11-11 | 9:44 | 119 | 234820 | 11910 | 7.72 | 34.8 |  | 1462.91 | 17423.2581 |  | 62.97 | 227.3299 | 128.2252 | 36.2257 | 391.7807 | 4666.108 | n | 605.0883 | 0 |  |  | 19845.1476 | 21364.5564 | 40619.4098 | 103625.3234 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-11-18 | 9:28 | 113 | 246110 | 11290 | 7.49 | 60 |  | 1628.22 | 18382.6038 |  | 75.51 | 153.8117 | 114.0981 | 31.3241 | 299.2339 | 3378.3512 | n | 443.2574 | 0 |  |  | 19261.1613 | 21151.6196 | 42955.355 | 106180.5644 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-11-25 | 9:27 | 151 | 261200 | 15090 | 7.73 | 61.6 | 1268.8 | 1700.6757 | 25663.196 |  | 158.7 | 193.8589 | 152.0357 | 26.0985 | 371.9931 | 5613.3756 | n | 731.4244 | 0 |  |  | 20774.6523 | 21827.3423 | 36901.3906 | 98071.8918 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-12-02 | 9:38 | 119 | 273160 | 11960 | 7.53 | 72.8 | 1252.8 | 1743.1 | 20847.476 |  | 116.3 | 188.734 | 152.2191 | 36.1859 | 377.139 | 4510.5818 | n | 592.0947 | 0 |  |  | 20579.1335 | 21564.641 | 37683.4661 | 101224.3078 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-12-09 | 9:25 | 128 | 285960 | 12800 | 7.75 | 73.6 | 1283.6 | 1618.11 | 20711.808 |  | 67.68 | 261.8162 | 144.3977 | 12.0466 | 418.2605 | 5353.7339 | n | 682.0158 | 0 |  |  | 21401.2709 | 21403.6653 | 34394.9162 | 103156.0158 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-12-16 | 9:25 | 122 | 298120 | 12160 | 7.78 | 80.8 | 1208 | 1531.76 | 18626.2016 |  | 102.1 | 234.7332 | 159.369 | 11.367 | 405.4691 | 4930.5046 | n | 632.413 | 0 |  |  | 21462.1704 | 21097.1579 | 34151.3184 | 106834.1054 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-12-23 | 9:27 | 129 | 311000 | 12880 | 7.67 | 58 | 1236.2 | 1644.43 | 21180.2584 |  | 128.4 | 219.3908 | 131.2818 | 77.7865 | 428.4591 | 5518.5533 | n | 733.7316 | 0 |  |  | 20341.436 | 20866.0579 | 38634.256 | 109607.3056 | 8000 | 30000 | 100 | 6 | 10 | 35000
2016-12-30 | 9:43 | 70 | 318040 | 7040 | 7.52 | 70 | 973.8 | 1390.37 | 9788.2048 |  | 38.56 | 101.8454 | 140.525 | 17.559 | 259.9294 | 1829.9033 | n | 242.8162 | 0 |  |  | 17576.6182 | 19966.8082 | 49693.5272 | 120398.3012 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-01-06 | 9:32 | 108 | 328840 | 10800 | 7.8 | 67.6 | 1086.6 | 1516.48 | 16377.984 |  | 99.29 | 141.6165 | 128.1319 | 8.9843 | 278.7326 | 3010.3126 | n | 390.4434 | 0 |  |  | 16493.1622 | 19246.5269 | 54027.3512 | 129041.6772 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-01-13 | 9:33 | 63 | 335140 | 6300 | 6.95 | 62.4 | 850.4 | 1120.82 | 7061.166 |  | 27.34 | 130.55 | 147.645 | 12.6683 | 290.8633 | 1832.4389 | n | 240.1912 | 0 |  |  | 13601.9033 | 18108.4116 | 65592.3868 | 142699.0602 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-01-20 | 8:50 | 106 | 345730 | 10590 | 7.69 | 84.4 | 1112.6 | 1556.09 | 16478.9931 |  | 130.9 | 259.9066 | 152.8662 | 10.2961 | 423.0689 | 4480.3 | n | 571.2898 | 0 |  |  | 12426.587 | 17847.5584 | 70293.6521 | 145829.2987 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-01-27 | 8:55 | 126 | 358390 | 12660 | 7.87 | 81.2 | 997.4 | 1686.19 | 21347.1654 |  | 108.9 | 240.0756 | 163.9247 | 16.2599 | 420.2602 | 5320.4945 | n | 684.4727 | 0 |  |  | 15316.3271 | 17824.0263 | 58734.6915 | 146111.6848 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-02-03 | 9:32 | 126 | 371040 | 12650 | 7.78 | 57.6 |  | 1718.28 | 21736.242 |  | 104.7 | 286.5326 | 183.0149 | 19.5294 | 489.077 | 6186.8238 | n | 794.3824 | 0 |  |  | 16655.8916 | 18183.4416 | 53376.4335 | 141798.7009 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-02-10 | 10:00 | 121 | 383100 | 12060 | 7.72 | 66 |  | 1475.39 | 17793.2034 |  | 90.3 | 174.4147 | 123.9873 | 35.7217 | 334.1237 | 4029.5313 | n | 528.286 | 0 |  |  | 19338.901 | 18134.3249 | 42644.3961 | 142388.1013 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-02-17 | 9:29 | 130 | 396080 | 12980 | 7.58 | 53.2 |  | 1595.5678 | 20710.47 |  | 104.1 | 162.0233 | 151.7031 | 13.2997 | 327.0261 | 4244.799 | n | 552.3735 | 0 |  |  | 20396.7702 | 17721.5977 | 38412.9192 | 147340.8273 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-02-24 | 9:32 | 122 | 408270 | 12190 | 7.31 | 66.8 |  | 1373.09 | 16737.9671 |  | 110.9 | 63.1169 | 171.59 | 37.8969 | 272.6037 | 3323.0396 | n | 456.3393 | 0 |  |  | 19244.4706 | 17379.1387 | 43022.1175 | 151450.3362 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-03-03 | 9:32 | 111 | 419400 | 11130 | 7.48 | 56 |  | 1361.58 | 15154.3854 |  | 53.16 | 179.4703 | 215.2337 | 14.1858 | 408.8897 | 4550.9429 | n | 596.4814 | 0 |  |  | 17599.0065 | 16916.0201 | 49603.9741 | 157007.7588 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-03-10 | 9:23 | 105 | 429860 | 10460 | 7.61 | 61.2 |  | 1427.88 | 14935.6248 |  | 87.53 | 153.727 | 155.3622 | 25.5222 | 334.6114 | 3500.0351 | n | 460.6276 | 0 |  |  | 16884.6118 | 16608.472 | 52461.5527 | 160698.3356 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-03-17 | 9:37 | 129 | 442850 | 12990 | 7.6 | 97.2 |  | 1556.82 | 20223.0918 |  | 136 | 122.8905 | 227.7233 | 34.7857 | 385.3995 | 5006.3391 | n | 673.7672 |  |  |  | 16762.7673 | 16528.7082 | 52948.9309 | 161655.5022 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-03-24 | 9:31 | 146 | 457430 | 14580 | 7.66 | 62 |  | 1536.78 | 22406.2524 |  | 167.8 | 102.7067 | 153.1763 | 6.4768 | 262.3598 | 3825.206 | n | 503.9474 | 0 |  |  | 18179.8386 | 17580.2121 | 47280.6456 | 149037.4546 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-03-31 | 8:55 | 125 | 469940 | 12510 | 7.97 | 81.2 |  | 1693.01 | 21179.5551 |  | 168.9 | 132 | 179 | 0 | 311 | 3890.61 | n | 507.9905 | 0 |  |  | 19686.131 | 17980.343 | 41255.4759 | 144235.8835 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-04-07 | 9:33 | 122 | 482150 | 12210 | 7.57 | 70.4 |  | 1583.91 | 19339.5411 |  | 105.4 | 133.5221 | 148.3959 | 25.9849 | 307.9029 | 3759.4942 | n | 497.2914 | 0 |  |  | 20787.1101 | 19003.541 | 36851.5596 | 131957.5084 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-04-13 | 7:33 | 105 | 492600 | 10450 | 7.75 | 58.8 |  | 1579.94 | 16510.373 |  | 107.1 | 120.5622 | 126.7384 | 19.031 | 266.3316 | 2783.1655 | n | 366.3395 | 0 |  |  | 19858.9304 | 19006.156 | 40564.2784 | 131926.1285 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-04-21 | 8:31 | 136 | 6220 | 13619 | 7.68 | 54.8 |  | 1598.0528 | 21763.8811 |  | 110 | 102.5793 | 149.9636 | 6.1409 | 258.6838 | 3523.0151 | n | 463.7225 | 0 |  |  | 19698.3376 | 19040.8823 | 41206.6497 | 131509.4128 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-04-28 | 8:42 | 111 | 17360 | 11140 | 7.72 | 58 |  | 1578.34 | 17582.7076 |  | 103.3 | 137.7287 | 145.1662 | 13.0973 | 295.9922 | 3297.3534 | n | 431.2296 | 0 |  |  | 18799.1257 | 18694.7544 | 44803.4972 | 135662.9472 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-05-05 | 8:31 | 142 | 31510 | 14150 | 7.63 | 56 |  | 1508.43 | 21344.2845 |  | 97.92 | 156.987 | 143.6931 | 5.5275 | 306.2077 | 4332.8385 | n | 560.2285 |  |  |  | 19300.3115 | 18990.6778 | 42798.7538 | 132111.8661 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-05-12 | 8:35 | 116 | 43150 | 11640 | 7.49 | 72 |  | 1624.12 | 18904.7568 |  | 122.7 | 186.7751 | 135.5539 | 4.9645 | 327.2935 | 3809.6963 | n | 488.1547 | 0 |  |  | 19898.9075 | 18840.2017 | 40404.37 | 133917.5793 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-05-19 | 8:33 | 119 | 55020 | 11870 | 7.47 | 93.6 |  | 1606.26 | 19066.3062 |  | 114.3 | 170.3467 | 168.8801 | 5.6483 | 344.8751 | 4093.667 | n | 530.6057 | 0 |  |  | 19224.5138 | 19034.23 | 43101.9449 | 131589.2402 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-05-26 | 9:03 | 119 | 66840 | 11820 | 7.54 | 119.2 |  | 1596.05 | 18865.311 |  | 97.33 | 158.9349 | 134.0943 | 8.3504 | 301.3796 | 3562.3064 | n | 460.3762 | 0 |  |  | 19545.1646 | 19343.4738 | 41819.3415 | 127878.3146 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-06-02 | 8:30 | 139 | 78200 | 11360 | 8.1 | 130.4 |  | 1745.87 | 19833.0832 |  | 131.8 | 140.0447 | 156.5365 | 7.958 | 304.5392 | 3459.5658 | n | 451.4034 | 0 |  |  | 19167.3643 | 19751.5953 | 43330.5428 | 122980.8562 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-06-09 | 8:34 | 181 | 93210 | 15010 | 7.88 | 74.81 |  | 1397.68 | 20979.1768 |  | 87.33 | 128.6544 | 209.2836 | 5.6974 | 343.6353 | 5157.966 | n | 680.2676 |  |  |  | 19685.9693 | 19814.6024 | 41256.1228 | 122224.7712 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-06-16 | 8:36 | 128 | 106050 | 12840 | 7.88 | 56.8 |  | 1366.11 | 17540.8524 |  | 84.67 | 182.3349 | 126.3164 | 12.9637 | 321.615 | 4129.537 | n | 531.7451 | 0 |  |  | 19304.6058 | 19409.1524 | 42781.5766 | 127090.1712 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-06-23 | 8:32 | 131 | 119200 | 13150 | 7.69 | 70 |  | 1759.73 | 23140.4495 |  | 134.4 | 93.9806 | 227.1892 | 15.2351 | 336.4049 | 4423.7251 | n | 594.232 |  |  |  | 20373.3905 | 19572.5603 | 38506.4381 | 125129.2768 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-06-30 | 8:34 | 126 | 131610 | 12410 | 7.55 | 48.8 |  | 1402.96 | 17410.7336 |  | 92.49 | 89.82 | 137.9255 | 0 | 227.7455 | 2826.3214 | n | 370.638 | 0 |  |  | 19767.8031 | 19411.8263 | 40928.7877 | 127058.0843 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-07-07 | 6:35 | 80 | 139680 | 8070 | 7.56 | 45.6 |  | 1455.2845 | 11744.1459 |  | 18.97 | 132.1915 | 270.6459 | 85.4721 | 488.3095 | 3940.6579 | n | 541.3937 |  |  |  | 17459.0454 | 19014.6407 | 50163.8186 | 131824.3114 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-07-14 | 8:41 | 79 | 147550 | 7870 | 7.24 | 56.4 |  | 1015 | 7988.05 |  | 17.25 | 28.9233 | 236.8176 | 42.3223 | 308.0632 | 2424.4574 | n | 339.1781 |  |  |  | 15070.8448 | 17866.6548 | 59716.621 | 145600.1425 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-07-21 | 8:30 | 96 | 157070 | 9520 | 7.05 | 39.6 |  | 1217.13 | 11587.0776 |  | 60.74 | 213.5356 | 199.0989 | 6.7895 | 419.424 | 3992.9161 | n | 516.3809 | 0 |  |  | 12182.5018 | 17367.019 | 71269.9929 | 151595.7725 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-07-28 | 8:48 | 173 | 172400 | 15330 | 7.87 | 80.4 |  | 1759.81 | 26977.8873 |  | 136.4 | 296.6565 | 140.2204 | 17.073 | 453.9499 | 6959.0526 | n | 884.2533 | 0 |  |  | 14574.2902 | 17836.4859 | 61702.8392 | 145962.1697 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-08-04 | 8:17 | 117 | 184210 | 11810 | 7.71 | 53.2 |  | 1794.5 | 21193.045 |  | 132.2 | 186.3289 | 223.0732 | 25.1876 | 434.5897 | 5132.5046 | n | 676.3585 | 0 |  |  | 16936.515 | 18027.1765 | 52253.9401 | 143673.8815 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-08-11 | 8:34 | 127 | 196890 | 12680 | 7.68 | 58.8 |  | 1694.9384 | 21491.8194 |  | 104.9 | 232.0662 | 199.9948 | 13.7006 | 445.7617 | 5652.2578 | n | 731.5772 | 0 |  |  | 20312.4573 | 18229.3026 | 38750.1707 | 141248.3683 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-08-17 | 8:20 | 103 | 207180 | 10290 | 7.65 | 96.8 | 1540.8 | 1763 | 18141.27 |  | 93.94 | 188.371 | 266.2911 | 83.404 | 538.0661 | 5536.7004 | n | 749.8641 | 0 |  |  | 21951.0054 | 18168.9659 | 32195.9783 | 141972.4093 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-08-25 | 8:17 | 140 | 219100 | 11920 | 7.69 | 150.4 |  | 1633.1 | 19466.552 |  | 124.1 | 146.0837 | 220.1781 | 43.2523 | 409.5141 | 4881.4084 | n | 655.123 | 0 |  |  | 20073.1716 | 18138.4216 | 39707.3136 | 142338.9405 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-09-01 | 8:38 | 108 | 230010 | 10910 | 7.84 | 51.6 |  | 1700.8 | 18555.728 |  | 77.88 | 136 | 283 | 26.1641 | 445.1642 | 4856.7409 | n | 651.453 | 0 |  |  | 19413.8424 | 17936.4676 | 42344.6306 | 144762.3893 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-09-08 | 8:32 | 112 | 241180 | 11170 | 7.89 | 39.2 |  | 1754.05 | 19592.7385 |  | 122.8 | 107.7569 | 152.5161 | 13.8719 | 274.1449 | 3062.1988 | n | 405.1035 | 0 |  |  | 18939.0721 | 18107.4581 | 44243.7115 | 142710.5032 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-09-15 | 8:45 | 94 | 250540 | 9360 | 7.66 | 58.8 |  | 1664.63 | 15580.9368 |  | 66.88 | 165.5358 | 199.2924 | 12.5968 | 377.4251 | 3532.6987 | n | 462.9407 | 0 |  |  | 18298.9888 | 17477.4987 | 46804.0447 | 150270.0159 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-09-22 | 8:40 | 148 | 265400 | 14860 | 7.96 | 66.8 |  | 1903.15 | 28280.809 |  | 180.7 | 182.8701 | 171.9144 | 0 | 354.7845 | 5272.0977 | n | 679.2745 | 0 |  |  | 20502.5531 | 18383.3383 | 37989.7877 | 139399.9405 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-09-29 | 8:33 | 131 | 276310 | 10910 | 7.91 | 60 |  | 1808.76 | 19733.5716 |  | 99.07 | 116.0029 | 210.0055 | 3.8674 | 329.8758 | 3598.9445 | n | 475.8145 | 0 |  |  | 20797.014 | 19049.1238 | 36811.9441 | 131410.5148 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-10-06 | 8:33 | 114 | 287690 | 11380 | 7.74 | 58.4 |  | 2030.61 | 23108.3418 |  | 102.3 | 196.3387 | 194.0539 | 0 | 390.3926 | 4442.6676 | n | 573.4618 | 0 |  |  | 21675.9148 | 20309.1481 | 33296.3408 | 116290.223 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-10-13 | 8:31 | 123 | 300030 | 12340 | 7.83 | 68.8 |  | 1847 | 22791.98 |  | 99.83 | 226.54 | 239.17 | 5.33 | 471.04 | 5812.6336 | n | 754.1878 | 4.1 |  |  | 23478.6756 | 21242.89 | 26085.2976 | 105085.3206 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-10-20 | 8:41 | 169 | 314030 | 14000 | 8.12 | 64 |  | 1800 | 25200 |  | 139.1 | 200.95 | 160.2 | 0 | 361.15 | 5056.1 | n | 647.5174 | 0 |  |  | 22708.4734 | 21094.7327 | 29166.1066 | 106863.2079 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-10-27 | 7:51 | 145 | 327980 | 13950 | 7.82 | 85.6 |  | 1752 | 24440.4 |  | 172.9 | 208 | 163 | 4.04 | 375.04 | 5231.808 | n | 671.4562 | 5.24 |  |  | 23885.1804 | 21365.3456 | 24459.2782 | 103615.8529 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-11-03 | 8:40 | 131 | 340070 | 12090 | 8.06 | 81.6 |  | 1896.6 | 22929.894 |  | 133.5 | 172.459 | 179.73 | 6.13 | 358.319 | 4332.0767 | n | 562.6157 |  |  |  | 23840.5685 | 21485.1851 | 24637.726 | 102177.7783 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-11-10 | 8:45 | 108 | 350930 | 10860 | 8.29 | 84 |  | 1917 | 20818.62 |  | 119.6 | 204.9757 | 156.3613 | 4.8655 | 366.2025 | 3976.9587 | n | 510.2441 | 0 |  |  | 23347.2285 | 21708.2976 | 26611.086 | 99500.4283 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-11-17 | 9:33 | 119 | 362820 | 11890 | 7.97 | 72 |  | 1822.15 | 21665.3635 |  | 125.7 | 198.9939 | 165.6847 | 0 | 364.6786 | 4336.029 | n | 556.1837 | 0 |  |  | 22463.5694 | 21891.5319 | 30145.7225 | 97301.6168 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-11-24 | 8:30 | 132 | 374000 | 11180 | 8 | 72.4 |  | 1838 | 20548.84 |  | 132.6 | 229.505 | 160.55 | 0 | 390.055 | 4360.8149 | n | 555.8315 | 0 |  |  | 21490.6794 | 22057.6246 | 34037.2825 | 95308.5048 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-12-01 | 8:49 | 106 | 384630 | 10630 | 7.88 | 104.8 |  | 1783.51 |  |  | 112.5 | 150.3935 | 154.8463 | 4.6134 | 309.8532 | 3293.739 | n | 427.3475 | 0 |  |  | 21010.9412 | 22281.7052 | 56967.1765 | 114901.2433 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-12-08 | 8:46 | 113 | 395950 | 11320 | 7.81 | 58 |  | 1852.58 | 20971.2056 |  | 116.1 | 177.2538 | 155.5201 | 5.5942 | 338.3681 | 3830.3273 | n | 494.3141 | 1.9698 |  |  | 21061.803 | 22771.7296 | 56814.5909 | 109510.9745 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-12-15 | 9:22 | 120 | 407890 | 11940 | 8.01 | 51.6 |  | 1728.61 | 20639.6034 |  | 118.7 | 226.6881 | 111.3581 | 0 | 338.0461 | 4036.2707 | n | 508.1764 | 0 |  |  | 20719.883 | 22077.0745 | 57840.351 | 117152.1801 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-12-22 | 8:42 | 119 | 417800 | 9910 | 7.49 | 44.4 |  | 1758.45 | 17426.2395 |  | 85.01 | 253.9451 | 141.1773 | 3.6538 | 398.7761 | 3951.8715 | n | 500.8879 | 0 |  |  | 19679.0162 | 21867.3171 | 60962.9515 | 119459.5122 | 8000 | 30000 | 100 | 6 | 10 | 35000
2017-12-29 | 8:48 | 158 | 432630 | 14830 | 7.71 | 71.6 |  | 1901.07 | 28192.8681 |  | 186.4 | 294.8752 | 230.2851 | 8.8521 | 534.0124 | 7919.4036 | n | 1017.7739 | 0 |  |  | 21807.4791 | 22329.5467 | 32770.0834 | 114374.9859 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-01-05 | 9:20 | 136 | 446260 | 13630 | 7.65 | 79.2 |  | 1320 | 17991.6 |  | 76.65 | 287.39 | 164 | 7.3 | 458.69 | 6251.9447 | n | 794.5736 | 0 |  |  | 21062.5778 | 21893.1486 | 35749.689 | 119175.3659 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-01-12 | 8:30 | 115 | 457851 | 11591 | 8.02 | 79.2 |  | 1988 | 23042.908 |  | 76 | 192 | 159 | 30 | 381 | 4416.171 | n | 577.7134 | 0 |  |  | 21663.4039 | 21697.0493 | 33346.3844 | 121332.4579 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-01-19 | 8:35 | 136 | 469400 | 11549 | 7.88 | 70.4 |  | 1898.19 | 21922.1963 |  | 106.4 | 308.2094 | 143.8139 | 67.5277 | 519.5509 | 6000.2938 | n | 781.6464 | 0 |  |  | 22787.3931 | 21468.1217 | 28850.4276 | 123850.6616 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-01-26 | 9:15 | 138 | 483250 | 13850 | 8.01 | 77.6 |  | 1893 | 26218.05 |  | 158.8 | 226.3001 | 115.7908 | 4.8416 | 346.9325 | 4805.0144 | n | 608.1252 | 0 |  |  | 22293.6886 | 21767.0449 | 30825.2457 | 120562.5056 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-02-02 | 8:59 | 125 | 495680 | 12430 | 7.85 | 70 |  | 1909.92 | 23740.3056 |  | 137.1 | 218.8826 | 158.892 | 3.9516 | 381.7262 | 4744.8565 | n | 607.2254 | 0 |  |  | 23730.865 | 22032.6527 | 25076.5401 | 117640.82 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-02-09 | 8:34 | 115 | 7200 | 11520 | 7.95 | 50.8 |  | 1749 | 20148.48 |  | 87.21 | 158.75 | 157.0598 | 0 | 315.8097 | 3638.1281 | n | 469.6287 | 0 |  |  | 23007.258 | 21894.7542 | 27970.9681 | 119157.7035 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-02-16 | 9:27 | 137 | 20910 | 13710 | 7.76 | 42.4 |  | 1800.6 | 24686.226 |  | 112 | 224.9778 | 159.1104 | 5.5842 | 389.6724 | 5342.4083 | n | 683.7716 | 0 |  |  | 23698.2654 | 22270.8802 | 25206.9384 | 115020.3175 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-02-23 | 8:52 | 127 | 33640 | 12730 | 7.7 | 60 |  | 2078.63 | 26460.9599 |  | 145.8 | 306.402 | 172.5521 | 0 | 478.9541 | 6097.0852 | n | 771.2037 | 0 |  |  | 23758.9929 | 22620.0535 | 24964.0285 | 88559.3576 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-03-02 | 8:41 | 118 | 45450 | 11810 | 7.95 | 65.2 |  | 2132 | 18958.7113 |  | 153.2 | 245 | 217 | 0 | 462 | 5456.22 | n | 701.4602 | 0 |  |  | 22563.5943 | 22452.3457 | 29745.6228 | 90571.8519 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-03-09 | 8:23 | 101 | 55540 | 10090 | 7.7 | 54.8 |  | 1247 | 12582.23 |  | 24.5 | 188 | 151 | 14.6 | 353.6 | 3567.824 | n | 461.8783 | trace |  |  | 20672.0318 | 21780.8979 | 37311.8728 | 98629.2253 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-03-16 | 8:30 | 139 | 69470 | 13930 | 7.75 | 12 |  | 1852.35 | 25803.2355 |  | 113 | 176.0442 | 300.7252 | 3.8883 | 480.6577 | 6695.5622 | n | 882.8208 | 0 |  |  | 20951.2842 | 22478.9809 | 36194.8633 | 90252.2293 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-03-23 | 8:10 | 94 | 78800 | 9330 | 7.68 | 45.6 |  | 1534 | 14312.22 |  | 85 | 134 | 180 | 10 | 324 | 3022.92 | n | 397.4009 | 0 |  |  | 17914.0992 | 21322.2602 | 48343.6032 | 104132.8774 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-03-30 | 9:25 | 136 | 91440 | 12640 | 7.67 | 54.8 |  | 1578 | 19945.92 |  | 108.8 | 104.775 | 200.6213 | 13.4573 | 318.8537 | 4030.3109 | n | 537.347 | 0 |  |  | 18160.9014 | 21485.1202 | 47356.3945 | 102178.5574 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-04-06 | 8:00 | 151 | 106530 | 15090 | 8.05 | 69.6 |  | 1876 | 28308.84 |  | 143.8 | 234.43 | 132.15 | 19.9 | 386.48 | 5831.9832 | n | 748.035 | 0 |  |  | 22092.5539 | 21923.9479 | 31629.7845 | 96912.6254 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-04-13 | 9:22 | 133 | 119870 | 13340 | 7.8 | 42 |  | 1738.22 | 23187.8548 |  | 115 | 173.4901 | 133.5784 | 13.962 | 321.0305 | 4282.5474 | n | 553.9046 | 0 |  |  | 21438.7087 | 22029.4194 | 34245.1652 | 95646.9669 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-04-20 | 8:00 | 110 | 130880 | 11010 | 7.62 | 70.4 |  | 1971 | 21700.71 |  | 82.17 | 247.77 | 41.225 | 0 | 288.995 | 3181.8349 | n | 389.3362 | 0 |  |  | 23285.8312 | 21652.9744 | 26856.6752 | 100164.3069 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-04-27 | 9:21 | 117 | 142560 | 11680 | 7.67 | 60 |  | 1667 | 19470.56 |  | 91.28 | 7.3259 | 240.1974 | 0 | 247.5232 | 2891.0713 | n | 399.1206 | 0 |  |  | 23166.9912 | 21297.1623 | 27332.0352 | 104434.0525 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-05-04 | 8:05 | 131 | 154690 | 12130 | 7.71 | 79.6 |  | 1750 | 21227.5 |  | 93.6 | 125.57 | 153.64 | 0 | 279.21 | 3386.8173 | n | 440.5871 | 0 |  |  | 21396.6562 | 21387.0806 | 34413.3752 | 103355.0325 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-05-11 | 8:05 | 123 | 166920 | 12230 | 7.64 | 42.8 |  | 1717 | 20998.91 |  | 93.65 | 156.8872 | 147.1312 | 0 | 304.0183 | 3718.1442 | n | 479.0154 | 0 |  |  | 20849.42 | 21079.8043 | 36602.32 | 107042.3485 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-05-18 | 9:18 | 116 | 178550 | 11630 | 7.69 | 59.6 |  | 1783.76 | 20745.1288 |  | 97.36 | 132.2993 | 176.7527 | 5.07 | 314.1219 | 3653.238 | n | 478.5386 | 0 |  |  | 20610.5247 | 20603.485 | 37557.9012 | 112758.1796 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-05-25 | 7:31 | 140 | 192590 | 14040 | 7.5 | 68 |  | 1829.5918 | 25687.4694 |  | 116.9 | 164.2431 | 174.4372 | 3.819 | 342.4993 | 4808.6903 | n | 624.0357 | 0 |  |  | 22164.752 | 21164.2149 | 31340.9918 | 106029.4215 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-06-01 | 7:14 | 123 | 204900 | 12310 | 7.57 | 73.6 |  | 1627.72 | 20037.2332 |  | 126.5 | 85.3557 | 147.4508 | 0 | 232.8065 | 2865.848 | n | 377.3289 | 0 |  |  | 21867.1853 | 21785.4651 | 32531.2586 | 98574.4183 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-06-08 | 9:20 | 116 | 216430 | 11530 | 7.43 | 80.4 |  | 1757 | 20258.21 |  | 73.68 | 227.2394 | 179.5435 | 7.1869 | 413.9697 | 4773.0712 | N | 613.7968 | 0 |  |  | 21682.0103 | 21323.3797 | 33271.9586 | 104119.4438 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-06-15 | 7:21 | 116 | 228030 | 11600 | 7.5 | 49.2 |  | 1795.56 | 20828.496 |  | 91.1 | 184.84 | 192.5 | 7.8 | 385.14 | 4467.624 | N | 580.649 | 0 |  |  | 21702.8521 | 21866.4027 | 33188.5914 | 97603.1678 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-06-22 | 7:25 | 136 | 241690 | 13660 | 7.52 | 68 |  | 2169 | 29628.54 |  | 123.6 | 224.8431 | 298.3091 | 0 | 523.1521 | 7146.2582 | N | 932.3506 | 0 |  |  | 22688.1198 | 22673.2877 | 29247.5208 | 87920.5478 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-06-29 | 7:56 | 146 | 256320 | 14630 | 7.51 | 68 |  | 1959 | 28660.17 |  | 156.8 | 256.4945 | 157.9273 | 0 | 414.4218 | 6062.9908 | N | 769.2829 | 0 |  |  | 24843.854 | 22702.5652 | 20624.584 | 87569.2178 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-07-06 | 8:15 | 149 | 271220 | 14900 | 7.81 | 75.2 |  | 1824 | 27177.6 |  | 136 | 130.4094 | 206.7722 | 0 | 337.1816 | 5024.006 | N | 659.564 | 0 |  |  | 26573.7015 | 23035.0439 | 13705.194 | 83579.4726 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-07-13 | 7:22 | 129 | 284040 | 12820 | 7.64 | 36.8 |  | 1796 | 23024.72 |  | 113.3 | 169.9082 | 208.0177 | 7.6781 | 385.604 | 4943.4434 | N | 646.1356 | 0 |  |  | 27122.7575 | 23145.3781 | 11508.97 | 82255.4626 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-07-20 | 6:53 | 98 | 293930 | 9890 | 7.46 | 51.2 |  | 1465 | 14488.85 |  | 83.6 | 43.084 | 172.8827 | 0 | 215.9667 | 2135.9109 | N | 287.9898 | 0 |  |  | 23337.835 | 22730.2356 | 26648.66 | 87237.1726 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-07-27 | 9:20 | 121 | 305970 | 12040 | 7.62 | 97.6 |  | 1595 | 19203.8 |  | 130.6 | 58.9843 | 262.8655 | 0 | 321.8498 | 3875.0717 | N | 523.6768 | 0 |  |  | 20973.7425 | 22561.5939 | 36105.03 | 89260.8726 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-08-03 | 7:30 | 161 | 320100 | 14130 | 7.71 | 49.2 |  | 1721 | 24317.73 |  | 110.6 | 184.3171 | 205.2019 | 0 | 389.5191 | 5503.9046 | n | 713.5491 | 0 |  |  | 20258.775 | 22838.1623 | 38964.9 | 85942.0526 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-08-10 | 8:03 | 119 | 330970 | 10870 | 7.54 | 44 |  | 1820 | 19783.4 |  |  | 102.8054 | 274.3784 | 7.0452 | 384.229 | 4176.569 | N | 559.4556 | 0 |  |  | 19448.445 | 22758.0182 | 42206.22 | 86903.7814 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-08-17 | 9:25 | 137 | 343620 | 12650 | 7.4 | 62 |  | 1844 | 23326.6 |  | 95.37 | 181.1471 | 172.6959 | 10.5257 | 364.3687 | 4609.2635 | N | 598.4406 | 0 |  |  | 21657.8825 | 22561.2791 | 33368.47 | 89264.6508 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-08-24 | 9:00 | 134 | 357080 | 13460 | 7.42 | 80 |  | 1796 | 24174.16 |  | 132.4 | 52.5597 | 326.9851 | 0 | 379.5448 | 5108.6734 | N | 694.7226 | 0 |  |  | 22900.4725 | 22906.023 | 28398.11 | 85127.724 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-08-31 | 9:30 | 154 | 372420 | 15340 | 7.84 | 57.2 |  | 1955 | 29989.7 |  | 145.8 | 197.1388 | 223.8106 | 18.3728 | 439.3222 | 6739.2022 | n | 883.1092 | 0 |  |  | 24318.465 | 23716.9805 | 22726.14 | 75396.234 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-09-07 | 9:15 | 120 | 384440 | 12020 | 7.59 | 59.6 |  | 1858 | 22333.16 |  | 101.9 | 134 | 189.18 | 11.4 | 334.58 | 4021.6516 | n | 529.9815 | 0 |  |  | 24955.905 | 23842.3692 | 20176.38 | 73891.57 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-09-14 | 9:18 | 141 | 396470 | 12030 | 7.47 | 56 |  | 1726.42 | 20768.8326 |  | 100.9 | 101.3704 | 193.3974 | 19.5782 | 314.346 | 3781.5821 | n | 506.317 | 0 |  |  | 24316.4631 | 23104.0602 | 22734.1474 | 82751.2774 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-09-21 | 8:45 | 151 | 411580 | 15110 | 7.37 | 43.2 |  | 1893 | 28603.23 |  | 140.8 | 123.08 | 139.25 | 0 | 262.33 | 3963.8063 | N | 514.1858 | 0 |  |  | 25423.7307 | 23099.3152 | 18305.0774 | 82808.2174 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-09-28 | 8:50 | 139 | 425460 | 13880 | 7.24 | 45.2 |  | 1886.77 | 26188.3676 |  | 115.5 | 126.9777 | 206.4488 | 12.7813 | 346.2078 | 4805.3648 | n | 636.6387 | 0 |  |  | 24473.3976 | 23016.8792 | 22106.4098 | 83797.4498 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-10-05 | 9:30 | 120 | 437460 | 12000 | 7.13 | 46.8 |  | 1864.6978 | 22376.3736 |  | 68.24 | 208.4121 | 158.9717 | 4.515 | 371.8988 | 4462.7861 | n | 572.4053 | 0 |  |  | 24484.2009 | 22962.8503 | 22063.1962 | 84445.7962 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-10-12 | 8:45 | 126 | 449700 | 12240 | 7.63 | 51.6 |  | 1747 | 21383.28 |  | 103.5 | 88.47 | 169.05 | 0 | 257.52 | 3152.0448 | n | 416.3904 | 0 |  |  | 24637.8128 | 23537.3861 | 21448.7488 | 77551.3662 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-10-19 | 9:20 | 135 | 462220 | 12520 | 7.18 | 50.4 |  | 1609.16 | 20146.6832 |  | 86.67 | 126.8874 | 170.8183 | 4.0209 | 301.7265 | 3777.616 | n | 494.6392 | 2.44 |  |  | 22523.6761 | 23615.9598 | 29905.2956 | 76608.483 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-10-26 | 9:19 | 135 | 474760 | 12540 | 7.61 | 44.4 |  | 1665.43 | 20884.4922 |  | 95.65 | 98.2159 | 217.1122 | 10.973 | 326.301 | 4091.8149 | n | 546.9052 | 0 |  |  | 21197.7072 | 23329.8566 | 35209.171 | 80041.7208 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-11-02 | 8:45 | 121 | 485790 | 11030 | 7.8 | 50.4 |  | 1656 | 18265.68 |  | 65.2 | 221.5 | 171.5 | 32.38 | 425.38 | 4691.9414 | n | 612.023 | 0 |  |  | 20170.0338 | 23203.3799 | 39319.8646 | 81559.4408 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-11-09 | 9:20 | 126 | 498440 | 12650 | 7.58 | 42.8 |  | 1969.01 | 24907.9765 |  | 88.57 | 307.76 | 240.44 | 52.59 | 600.79 | 7599.9935 | n | 994.5058 | 0 |  |  | 21051.208 | 23335.1613 | 35795.1681 | 79978.0643 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-11-16 | 8:55 | 128 | 11130 | 12688 | 7.15 | 68 |  | 1686 | 21391.968 |  | 102.5 | 107.0316 | 225.0513 | 53.8394 | 385.9222 | 4896.5813 | n | 668.2291 | 0 |  |  | 21362.5292 | 23103.312 | 34549.8833 | 82760.2563 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-11-23 | 9:18 | 134 | 24440 | 13310 | 7.46 | 56 |  | 1664.22 | 22150.7682 |  | 104.7 | 129.7337 | 156.6477 | 9.7985 | 296.1799 | 3942.155 | n | 516.6144 | 0 |  |  | 21679.0982 | 22450.0677 | 33283.6073 | 90599.1881 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-11-30 | 9:00 | 155 | 39930 | 15490 | 7.58 | 53.6 |  | 1782.89 | 27616.9661 |  | 117.9 | 134.5462 | 218.6748 | 12.0407 | 365.2616 | 5657.9028 | n | 748.9179 | 0 |  |  | 24016.9197 | 22890.3848 | 23932.3212 | 85315.382 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-12-07 | 9:21 | 115 | 51390 | 11460 | 7.48 | 103 |  | 1421.75 | 16293.255 |  | 48.3 | 96.8443 | 217.677 | 13.6274 | 328.1488 | 3760.585 | n | 503.7149 | 4.2866 |  |  | 21863.2393 | 22517.42 | 32547.0427 | 89790.9596 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-12-14 | 9:23 | 148 | 64220 | 12830 | 7.74 | 41.6 |  | 1798 | 23068.34 |  | 78.45 | 202.6934 | 211.6484 | 16.5794 | 430.9212 | 5528.719 | n | 721.8064 | 0 |  |  | 22282.3323 | 22056.1792 | 30870.6707 | 95325.8496 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-12-21 | 8:45 | 151 | 79340 | 15120 | 7.59 | 50.4 |  | 1964.67 | 29705.8104 |  | 142.4 | 299.4187 | 259.2799 | 22.1278 | 580.8263 | 8782.094 | n | 1138.9662 | 4.9851 |  |  | 24171.0929 | 22349.2994 | 23315.6285 | 91808.4068 | 8000 | 30000 | 100 | 6 | 10 | 35000
2018-12-28 | 9:00 | 147 | 94070 | 14730 | 7.76 | 64 |  | 1863.76 | 27453.1848 |  | 125.1 | 211.6306 | 262.8683 | 46.5982 | 521.0972 | 7675.7613 | n | 1020.1863 | 2.4487 |  |  | 24130.1476 | 22772.367 | 23479.4098 | 86731.5956 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-01-04 | 9:17 | 137 | 107770 | 13700 | 7.78 | 61.6 |  | 1945.92 | 26659.104 |  | 118.8 | 273.3401 | 274.7784 | 26.4018 | 574.5204 | 7870.9292 | n | 1028.1033 | 0 |  |  | 26721.6098 | 23212.019 | 13113.5608 | 81455.7716 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-01-11 | 9:04 | 149 | 121560 | 13790 | 7.61 | 44 |  | 1770 | 24408.3 |  | 90.92 | 187.29 | 227.52 | 14.31 | 429.12 | 5917.5648 | n | 775.7007 | 0 |  |  | 27056.5998 | 23567.1538 | 11773.6008 | 77194.1548 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-01-18 | 8:53 | 137 | 134070 | 12510 | 7.8 | 60.4 |  | 1828 | 22868.28 |  | 95.16 | 200.41 | 238.6 | 13.8 | 452.81 | 5664.6531 | n | 741.5258 | 0 |  |  | 25347.2172 | 23732.4694 | 18611.1312 | 75210.367 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-01-25 | 9:09 | 150 | 147830 | 13760 | 7.52 | 79.2 |  | 1869 | 25717.44 |  | 125.6 | 267.88 | 156.27 | 77.6 | 501.75 | 6904.08 | n | 910.9472 | 0 |  |  | 24913.281 | 24353.4494 | 20346.876 | 67758.607 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-02-01 | 8:30 | 130 | 160990 | 13160 | 7.69 | 42 |  | 1939 | 25517.24 |  | 134.4 | 228.37 | 220.8 | 60.11 | 509.28 | 6702.1248 | n | 889.6836 | 0 |  |  | 24627.815 | 24404.2214 | 21488.74 | 67149.3435 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-02-08 | 8:55 | 143 | 174260 | 13270 | 7.8 | 46 |  | 1815 | 24085.05 |  | 95.9 | 205.59 | 133.91 | 50.88 | 390.38 | 5180.3426 | n | 681.4129 | 0 |  |  | 24547.0025 | 24628.6449 | 21811.99 | 64456.2615 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-02-15 | 9:02 | 137 | 187850 | 13590 | 7.99 | 47.6 |  | 1842 | 25032.78 |  | 103.5 | 197.7818 | 156.2345 | 56.9537 | 410.97 | 5585.0826 | n | 740.4842 | 2.3276 |  |  | 25088.1275 | 24868.8125 | 19647.49 | 61574.2497 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-02-22 | 9:08 | 145 | 201280 | 13430 | 7.63 | 54.8 |  | 1615.8537 | 21700.9146 |  | 91.3 | 114.3961 | 159.8852 | 54.7299 | 329.0112 | 4418.621 | n | 599.7548 | 2.15 |  |  | 24083.9962 | 24375.8082 | 23664.0154 | 67490.3012 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-03-01 | 9:06 | 118 | 212130 | 10850 | 7.59 | 43.6 |  | 1410 | 15298.5 |  | 28.93 | 43.43 | 79.66 | 5.34 | 128.43 | 1393.4655 | n | 185.5138 | 0 |  |  | 21529.3112 | 24292.912 | 33882.7554 | 68485.0562 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-03-08 | 9:04 | 147 | 225870 | 13740 | 7.94 | 47.6 |  | 1883 | 25872.42 |  | 98.9 | 207.54 | 151.99 | 6.75 | 366.28 | 5032.6872 | n | 645.6148 | 0 |  |  | 21976.1537 | 24526.5853 | 32095.3854 | 65680.9762 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-03-15 | 8:58 | 114 | 239090 | 13220 | 7.96 | 57.6 |  | 1754 | 23187.88 |  | 107.6 | 177.9 | 129.57 | 0 | 307.47 | 4064.7534 | n | 518.8503 | 0 |  |  | 21514.9287 | 23983.4245 | 33940.2854 | 72198.9066 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-03-22 | 8:55 | 150 | 253130 | 14040 | 7.89 | 49.6 |  | 2017 | 28318.68 |  | 108.7 | 287.14 | 127.79 | 0 | 414.93 | 5825.6172 | n | 731.0923 | 2.26 |  |  | 23169.37 | 24055.5491 | 27322.52 | 71333.4114 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-03-29 | 8:59 | 120 | 265180 | 12050 | 7.84 | 62.4 |  | 2008 | 24196.4 |  | 128.1 | 205.33 | 192.93 | 4.77 | 403.03 | 4856.5115 | n | 627.5611 | 0 |  |  | 25393.845 | 23850.3237 | 18424.62 | 73796.1154 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-04-05 | 8:48 | 159 | 280080 | 14900 | 7.35 | 40.4 |  | 1735.8 | 25863.42 |  | 121.1 | 142.29 | 129.64 | 3.86 | 275.79 | 4109.271 | n | 530.6963 | 0 |  |  | 25391.595 | 23971.5837 | 18433.62 | 72340.9954 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-04-12 | 9:03 | 136 | 293700 | 13620 | 7.8 | 39.2 |  | 1560 | 21247.2 |  | 94.77 | 86.2843 | 126.54 | 0 | 212.8243 | 2898.667 | n | 379.5188 | 0 |  |  | 24906.425 | 23836.4937 | 20374.3 | 73962.0754 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-04-18 | 8:45 | 117 | 304350 | 10650 | 7.46 | 59.2 |  | 1504 | 18687.2 |  | 83.22 | 88.23 | 128.13 | 7.88 | 224.24 | 2786.182 | n | 315.0917 | 0 |  |  | 22498.555 | 23250.6404 | 30005.78 | 80992.3154 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-04-26 | 9:01 | 196 | 322940 | 18590 | 7.97 | 56 |  | 1823 | 29653.3737 |  | 137.1 | 140.17 | 196.54 | 0 | 336.71 | 5477.009 | n | 818.2509 | 0 |  |  | 23862.7984 | 23595.3182 | 24548.8063 | 76856.1816 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-05-03 | 8:54 | 148 | 336730 | 13790 | 7.78 | 66.4 |  | 1535 | 21167.65 |  | 76.27 | 98 | 85.8 | 6.34 | 190.14 | 2622.0306 | n | 339.7828 | 0 |  |  | 22688.8559 | 23352.2015 | 29244.5762 | 79773.5816 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-05-10 | 8:55 | 152 | 350990 | 14260 | 7.63 | 45.2 |  | 1676 | 23899.76 |  | 88.38 | 112.9 | 138.18 | 6.28 | 257.36 | 3669.9536 | n | 480.1861 | trace m. |  |  | 23351.9959 | 23257.7832 | 26592.0163 | 80906.6016 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-05-17 | 9:05 | 140 | 363730 | 12740 | 7.65 | 59.2 |  | 1691 | 21543.34 |  | 93.36 | 79.92 | 124.44 | 0 | 204.36 | 2603.5464 | n | 341.5872 | 0 |  |  | 24066.0309 | 23244.652 | 23735.8763 | 81064.1763 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-05-24 | 9:02 | 129 | 375700 | 11970 | 7.44 | 70.4 |  | 1587 | 18996.39 |  | 65.47 | 70.81 | 135.6 | 9.9 | 216.31 | 2589.2307 | n | 345.4798 | 0 |  |  | 21401.785 | 23552.8095 | 34392.86 | 77366.2863 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-05-31 | 9:05 | 152 | 389850 | 14150 | 7.5 | 74.8 |  | 1565 | 22144.75 |  | 80.59 | 143.673 | 141.0579 | 5.7969 | 290.5278 | 4110.9689 | n | 533.1304 | 0 |  |  | 21646.06 | 23242.1703 | 33415.76 | 81093.9563 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-06-07 | 9:02 | 143 | 403150 | 13300 | 7.37 | 64.8 |  | 1606 | 21359.8 |  | 86.41 | 67.92 | 167.62 | 0 | 235.54 | 3132.682 | n | 417.1097 | 0 |  |  | 21011.07 | 23089.8303 | 35955.72 | 82922.0363 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-06-14 | 9:01 | 126 | 415810 | 12660 | 7.51 | 72.4 |  | 1639 | 20749.74 |  | 67.25 | 251.2196 | 169.4075 | 4.6349 | 425.2619 | 5383.816 | n | 687.2928 | 0 |  |  | 20812.67 | 22459.0853 | 36749.32 | 90490.9763 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-06-21 | 8:44 | 131 | 429110 | 13300 | 6.83 | 54.8 |  | 1571.4 | 20899.62 |  | 94.21 | 84.4 | 165.61 | 6.79 | 256.8 | 3415.44 | n | 454.1635 | 0 |  |  | 21288.4775 | 22184.3536 | 34846.09 | 93787.7563 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-06-28 | 8:45 | 171 | 444200 | 15090 | 7.88 | 46.8 |  | 1731 | 26120.79 |  | 144.5 | 168.3 | 161.15 | 4.07 | 333.52 | 5032.8168 | n | 650.8472 | 0 |  |  | 22282.4875 | 22205.8011 | 30870.05 | 93530.3862 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-07-05 | 8:52 | 138 | 456940 | 12740 | 7.55 | 62 |  | 1672 | 21301.28 |  | 77.68 | 18.1286 | 214.9037 | 4.4641 | 237.4964 | 3025.7039 | N | 416.2951 | 0 |  |  | 22267.8575 | 22210.3078 | 30928.57 | 93476.3062 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-07-12 | 9:08 | 123 | 468280 | 11340 | 7.53 | 53.2 |  | 1596 | 18098.64 |  | 67.99 | 29.4461 | 223.155 | 10.4776 | 263.0787 | 2983.312 | n | 409.849 | 0 |  |  | 21605.0825 | 22161.2611 | 33579.67 | 94064.8663 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-07-19 | 8:59 | 145 | 480920 | 12640 | 7.57 | 80.4 |  | 1509 | 19073.76 |  | 70.73 | 28.1513 | 155.4722 | 22.9789 | 206.6024 | 2611.4546 | n | 361.7175 | 0 |  |  | 21148.6175 | 21279.6267 | 35405.53 | 104644.48 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-07-26 | 9:08 | 109 | 491760 | 10840 | 7.6 | 80.8 |  | 1556 | 16867.04 |  | 87.92 | 102.5 | 98.7 | 100.79 | 301.99 | 3273.5716 | n | 457.071 | 0 |  |  | 18835.18 | 20921.2425 | 44659.28 | 108945.09 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-08-02 | 8:56 | 131 | 3920 | 12150 | 7.58 | 55.6 |  | 1652 | 20071.8 |  | 87.62 | 35.5739 | 261.3555 | 19.7594 | 316.6888 | 3847.7687 | n | 530.5161 | 0 |  |  | 18527.81 | 20602.2458 | 45888.76 | 112773.05 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-08-09 | 8:58 | 97 | 13600 | 9680 | 7.63 | 80.8 |  | 1597 | 15458.96 |  | 13.83 | 19.2825 | 275.8971 | 19.3334 | 314.5131 | 3044.4868 | n | 422.6443 | 0 |  |  | 17867.89 | 20095.2142 | 48528.44 | 118857.43 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-08-16 | 9:05 | 116 | 23230 | 9630 | 7.47 | 66 |  | 1613 | 15533.19 |  | 40.72 | 88.5565 | 216.83 | 17.0438 | 322.4304 | 3105.005 | n | 417.8924 | 0 |  |  | 16982.7475 | 19806.6142 | 52069.01 | 122320.63 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-08-23 | 8:55 | 150 | 37010 | 13780 | 7.62 | 53.2 |  | 1945 | 26802.1 |  | 134.6 | 165.2 | 226.4 | 7.8 | 399.4 | 5503.732 | n | 722.1391 | 0 |  |  | 19466.5125 | 20194.7267 | 42133.95 | 117663.28 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-08-30 | 9:04 | 150 | 51010 | 14000 | 7.72 | 38 |  | 1524 | 21336 |  | 102.2 | 0 | 320.1147 | 9.5109 | 329.6257 | 4614.7592 | n | 642.6397 | 0 |  |  | 19782.5625 | 20192.7433 | 40869.75 | 117687.08 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-09-06 | 9:15 | 130 | 63050 | 12040 | 7.6 | 68.4 |  | 1507 | 18144.28 |  | 59.21 | 25.7871 | 218.4456 | 9.5581 | 253.7908 | 3055.6416 | n | 420.2359 | 0 |  |  | 20453.8925 | 19975.6217 | 38184.43 | 120292.54 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-09-13 | 8:59 | 158 | 77790 | 14740 | 7.76 | 55.6 |  | 1997 | 29435.78 |  | 122.9 | 152.3489 | 250.8198 | 8.5689 | 411.7375 | 6069.0115 | n | 801.499 | 0 |  |  | 23929.54 | 20686.9683 | 24281.84 | 111756.38 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-09-20 | 8:58 | 138 | 91670 | 13880 | 7.89 | 59.2 |  | 1741 | 24165.08 |  | 111.1 | 32.3098 | 227.3797 | 11.4508 | 271.1404 | 3763.4281 | N | 516.7076 | 0 |  |  | 23270.285 | 20523.9925 | 26918.86 | 113712.09 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-09-27 | 8:56 | 179 | 109430 | 17760 | 7.65 | 48.4 |  | 1516 | 26924.16 |  | 121.4 | 38.99 | 215.59 | 0 | 254.58 | 4521.3408 | n | 613.5944 | 0 |  |  | 24667.325 | 20992.5658 | 21330.7 | 108089.21 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-10-04 | 8:54 | 184 | 126170 | 16740 | 7.64 | 54 |  | 1530 | 25612.2 |  | 77.25 | 130.94 | 225.7 | 0 | 356.64 | 5970.1536 | n | 785.9963 | 0 |  |  | 26534.305 | 21618.6958 | 13862.78 | 100575.65 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-10-11 | 8:49 | 169 | 142030 | 15860 | 7.69 | 54 |  | 1373 | 21775.78 |  | 69.29 | 100.91 | 106.1 | 101.91 | 308.92 | 4899.4712 | n | 684.8497 | 0 |  |  | 24619.305 | 21843.8642 | 21522.78 | 97873.63 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-10-18 | 9:02 | 157 | 156810 | 14780 | 7.75 | 58.4 |  | 1359 | 20086.02 |  | 80.59 | 11.9374 | 181.3515 | 7.5285 | 200.8174 | 2968.0804 | n | 410.5546 | 0 |  |  | 23599.54 | 22112.1125 | 25601.84 | 94654.65 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-10-25 | 8:56 | 175 | 173270 | 16460 | 7.96 | 60 |  | 1492 | 24558.32 |  | 88.69 | 62.674 | 205.024 | 7.43 | 275.128 | 4528.6069 | n | 610.9006 | 0 |  |  | 23008.08 | 22485.9892 | 27967.68 | 90168.13 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-11-01 | 8:55 | 148 | 187040 | 13770 | 7.67 | 28.8 |  | 1606.1 | 22115.997 |  | 91.07 | 118.48 | 156.59 | 6.71 | 281.78 | 3880.1106 | n | 508.9724 | 0 |  |  | 22134.0292 | 23040.7422 | 31463.883 | 83511.093 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-11-08 | 9:00 | 160 | 201570 | 14530 | 7.84 | 42.8 |  | 1586 | 23044.58 |  | 86.08 | 37.97 | 192.91 | 16.4 | 247.28 | 3592.9784 | N | 492.8939 | 0 |  |  | 22451.2293 | 23666.6914 | 30195.083 | 75999.703 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-11-15 | 8:59 | 138 | 214270 | 12700 | 7.66 | 42.8 |  | 1351 | 17157.7 |  | 75.91 | 63.01 | 163.99 | 7.01 | 234.01 | 2971.927 | n | 398.7672 | 0 |  |  | 21719.1492 | 22862.9914 | 33123.403 | 85644.103 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-11-22 | 8:58 | 163 | 230220 | 15950 | 7.8 | 41.2 |  | 1509 | 24068.55 |  | 126.3 | 69.36 | 200.89 | 13.17 | 283.42 | 4520.549 | n | 610.3257 | 0 |  |  | 21596.7068 | 23090.7039 | 33613.173 | 82911.553 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-11-29 | 8:58 | 168 | 246030 | 15810 | 7.92 | 57.2 |  | 1670 | 26402.7 |  | 133.1 | 96.8794 | 185.6668 | 5.6524 | 288.1987 | 4556.4211 | n | 604.5427 | 0 |  |  | 22668.3825 | 23778.9056 | 29326.47 | 74653.133 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-12-06 | 8:54 | 145 | 259530 | 13500 | 7.62 | 60.8 |  | 1710 | 23085 |  | 95.56 | 122.22 | 210.84 | 5.5 | 338.56 | 4570.56 | n | 603.9228 | 5.77 |  |  | 22678.4875 | 23249.6739 | 29286.05 | 81003.913 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-12-13 | 9:03 | 152 | 273360 | 13830 | 7.89 | 42.4 |  | 1423 | 19680.09 |  | 81.38 | 83.6 | 189.4 | 10.58 | 283.58 | 3921.9114 | 2 | 524.9787 | 2.14 |  |  | 23309.085 | 22875.9247 | 26763.66 | 85488.903 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-12-20 | 9:06 | 176 | 290290 | 16930 | 7.9 | 66.4 |  | 1508 | 25530.44 |  | 127.2 | 100.16 | 165.3 | 19.07 | 284.53 | 4817.0929 | N | 642.7739 | 0 |  |  | 23674.5575 | 22759.7814 | 25301.77 | 86882.623 | 8000 | 30000 | 100 | 6 | 10 | 35000
2019-12-27 | 8:45 | 185 | 307820 | 17530 | 7.72 | 36.4 |  | 1490 | 26119.7 |  | 120.3 | 91.33 | 183.43 | 6.77 | 281.53 | 4935.2209 | n | 656.3888 | 0 |  |  | 23603.8075 | 22802.0731 | 25584.77 | 86375.123 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-01-03 | 8:57 | 193 | 326090 | 18270 | 7.77 | 26.4 |  | 1539 | 28117.53 |  | 133.1 | 108.99 | 155.97 | 7.85 | 272.81 | 4984.2387 | N | 656.3381 | 0 |  |  | 24861.94 | 23330.5523 | 20552.24 | 80033.373 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-01-10 | 9:04 | 164 | 341300 | 15210 | 7.62 | 46 |  | 1547 | 23529.87 |  | 82.41 | 93.36 | 164.71 | 9.65 | 267.72 | 4072.0212 | N | 540.7953 | 0 |  |  | 25824.385 | 23617.5397 | 16702.46 | 76589.523 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-01-17 | 8:55 | 162 | 356370 | 15070 | 7.63 | 36.8 |  | 1160 | 17481.2 |  | 78.9 | 42.15 | 170.97 | 14.84 | 227.96 | 3435.3572 | n | 469.1358 | 0 |  |  | 23812.075 | 23027.7798 | 24751.7 | 83666.643 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-01-24 | 8:50 | 175 | 373070 | 16700 | 7.79 | 20 |  | 1526 | 25484.2 |  | 133.5 | 90.04 | 175.66 | 24 | 289.7 | 4837.99 | n | 651.0494 | 0 |  |  | 23653.2 | 23308.4633 | 25387.2 | 80298.44 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-01-31 | 9:00 | 176 | 389660 | 16590 | 7.67 | 36.4 |  | 1642 | 27240.78 |  | 112.3 | 106.34 | 252.75 | 14.36 | 373.45 | 6195.5355 | N | 830.6597 | 0 |  |  | 23434.0125 | 23658.1467 | 26263.95 | 76102.24 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-02-07 | 8:55 | 161 | 405740 | 16080 | 7.71 | 50 |  | 1486 | 23894.88 |  | 75.81 | 19.49 | 255.74 | 8.9 | 284.13 | 4568.8104 | N | 630.5519 | 0 |  |  | 23525.265 | 24219.5783 | 25898.94 | 69365.06 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-02-14 | 9:07 | 196 | 423340 | 17600 | 7.78 | 31.6 |  | 1310 | 23056 |  | 102.6 | 25.97 | 85.58 | 4.91 | 116.46 | 2049.696 | N | 277.3797 | 0 |  |  | 24918.965 | 24135.1992 | 20324.14 | 70377.61 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-02-21 | 8:55 | 186 | 441980 | 18640 | 7.94 | 34.4 |  | 1353 | 25219.92 |  | 130.8 | 61.13 | 183.21 | 7.6 | 251.94 | 4696.1616 | n | 632.5136 | 0 |  |  | 24852.895 | 24036.6342 | 20588.42 | 71560.39 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-02-28 | 9:00 | 185 | 460430 | 18450 | 7.73 | 41.2 |  | 1312 | 24206.4 |  | 129.16 | 16.75 | 179.9 | 106.7 | 303.35 | 5596.8075 | n | 813.8484 | 0 |  |  | 24094.3 | 24130.0842 | 23622.8 | 70438.99 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-03-06 | 9:00 | 157 | 476120 | 15690 | 7.37 | 51.6 |  | 1250 | 19612.5 |  | 47.88 | 69.73 | 151.64 | 69.48 | 290.85 | 4563.4365 | n | 636.1331 | 0 |  |  | 23023.705 | 24124.4517 | 27905.18 | 70506.58 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-03-13 | 8:55 | 43 | 493490 | 17370 | 7.3 | 48.8 |  | 1201.5 | 20870.055 |  | 78.15 | 0 | 130.58 | 65.414 | 195.994 | 3404.4158 | n | 497.2438 | 0 |  |  | 22477.2188 | 23736.0863 | 30091.125 | 75166.965 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-03-20 | 9:00 | 197 | 12130 | 18640 | 7.55 | 40.4 |  | 1450 | 27028 |  | 124.9 | 11.82 | 204.32 | 91.65 | 307.79 | 5737.2056 | n | 829.1858 | 0 |  |  | 22929.2388 | 23811.7779 | 28283.045 | 74258.665 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-03-27 | 9:00 | 177 | 28790 | 16660 | 7.74 | 33.2 |  | 1349 | 22474.34 |  | 98.17 | 76.42 | 169.43 | 81.96 | 327.81 | 5461.3146 | n | 763.3376 |  |  |  | 22496.2238 | 23341.5121 | 30015.105 | 79901.855 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-04-03 | 8:55 | 183 | 46130 | 18830 | 7.45 | 21.6 |  | 1194 | 22483.02 |  | 68.09 | 30.36 | 123.7 | 21.58 | 175.64 | 3307.3012 | n | 456.6651 | 0 |  |  | 23213.8537 | 23254.2746 | 27144.585 | 80948.705 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-04-09 | 9:00 | 163 | 61360 | 15230 | 7.34 | 48.4 |  | 1183.4 | 21027.0457 |  | 74.68 | 17.17 | 146.94 | 11.7 | 175.81 | 3123.8507 | N | 370.1683 | 0 |  |  | 23253.1014 | 23549.7617 | 26987.5943 | 77402.8593 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-04-17 | 9:03 | 194 | 80770 | 19410 | 7.43 | 26.4 |  | 1043.23 | 17717.9575 |  | 68.86 | 0 | 129.2 | 31.44 | 160.64 | 2728.2696 | n | 445.8132 | 0 |  |  | 20925.5908 | 22902.5748 | 36297.6368 | 85169.1018 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-04-24 | 9:00 | 170 | 96880 | 16110 | 7.41 | 44.16 |  | 892.95 | 14385.4245 |  | 41 | 27.98 | 137.18 | 41.6 | 206.76 | 3330.9036 | n | 468.1137 | 0 |  |  | 18903.3619 | 21831.2952 | 44386.5523 | 98024.4573 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-05-01 | 9:02 | 162 | 112080 | 15200 | 7.49 | 36.8 |  | 1316 | 20003.2 |  | 75.54 | 99.74 | 190.76 | 25.98 | 316.48 | 4810.496 | n | 646.872 | 0 |  |  | 18283.4069 | 21506.9886 | 46866.3723 | 101916.1373 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-05-07 | 8:57 | 141 | 126200 | 14120 | 7.47 | 28.4 |  | 1104.44 | 18193.8083 |  | 65.29 | 32.74 | 152.4 | 29.33 | 214.47 | 3533.0358 | n | 420.2413 | 0 |  |  | 17575.0976 | 21101.8059 | 49699.6097 | 106778.3291 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-05-15 | 8:55 | 200 | 145220 | 19020 | 7.75 | 25.4 |  | 1276.148 | 21238.2924 |  | 102.1 | 53.43 | 172.74 | 34.28 | 260.45 | 4334.5391 | n | 681.9395 | 0 |  |  | 18455.1813 | 20770.0036 | 46179.2748 | 110759.9566 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-05-22 | 8:57 | 171 | 161260 | 16040 | 7.81 | 50 |  | 1372 | 22006.88 |  | 113.1 | 25.73 | 203.03 | 34.08 | 262.84 | 4215.9536 | n | 588.7596 | 0 |  |  | 20360.5452 | 20586.7103 | 38557.8193 | 112959.4766 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-05-29 | 8:47 | 169 | 177210 | 15950 | 7.82 | 44.8 |  | 1194.88 | 19058.336 |  | 73.51 | 65.1 | 83.46 | 31.25 | 179.81 | 2867.9695 | n | 388.9757 | 0 |  |  | 20124.3292 | 20540.5299 | 39502.6833 | 113513.6406 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-06-05 | 8:57 | 176 | 193800 | 16590 | 7.8 | 40.8 |  | 1208.6 | 20050.674 |  | 90.49 | 36.04 | 148.75 | 32.44 | 217.23 | 3603.8457 | n | 500.2137 | 0 |  |  | 20588.5456 | 20472.2482 | 37645.8176 | 114333.0216 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-06-12 | 8:48 | 63 | 212610 | 18810 | 7.81 | 45.6 |  | 1364.82 | 25672.2642 |  | 113.7 | 89.98 | 180.02 | 26.98 | 296.98 | 5586.1938 | n | 753.5608 | 0 |  |  | 21697.0386 | 20359.2702 | 33211.8458 | 115688.7574 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-06-19 | 8:46 | 189 | 230480 | 17870 | 8.2 | 54.4 |  | 1409 | 25178.83 |  | 110 | 64.89 | 151.75 | 14.33 | 230.97 | 4127.4339 | n | 555.8507 | 0 |  |  | 22490.0261 | 20584.6444 | 30039.8958 | 112984.2674 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-06-26 | 8:47 | 182 | 247840 | 17360 | 7.5 | 61.6 |  | 1288 | 22359.68 |  | 89.82 | 17.76 | 215.86 | 38.36 | 271.98 | 4721.5728 | n | 663.4851 | 0 |  |  | 23315.362 | 20574.366 | 26738.5518 | 113107.6074 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-07-03 | 8:55 | 180 | 264600 | 16760 | 7.64 | 47.6 |  | 1104 | 18503.04 |  | 62 | 26.7797 | 156.799 | 35.566 | 219.1447 | 3672.8652 | n | 513.8983 | 0 |  |  | 22928.4535 | 20364.0322 | 28286.1858 | 115631.6131 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-07-10 | 8:50 | 167 | 280910 | 16310 | 7.78 | 50.8 |  | 1222 | 19930.82 |  | 81.25 | 42.6 | 152.78 | 28.91 | 224.29 | 3658.1699 | n | 504.4201 |  |  |  | 21493.0925 | 20548.4374 | 34027.63 | 113418.7506 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-07-17 | 8:50 | 186 | 298700 | 17790 | 7.53 | 55.6 |  | 1468.59 | 26126.2161 |  | 119.8 | 82.6 | 155.5 | 30.3 | 268.4 | 4774.836 | n | 646.0275 |  |  |  | 21729.939 | 21526.8367 | 33080.2439 | 101677.959 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-07-24 | 8:52 | 148 | 312500 | 13800 | 7.58 | 54.8 |  | 1160 | 16008 |  | 62 | 34.22 | 192.22 | 30.77 | 257.21 | 3549.498 | n | 492.5296 | 0 |  |  | 20142.019 | 21193.9034 | 39431.9239 | 105673.159 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-07-31 | 8:56 | 106 | 329360 | 16860 | 7.77 | 48 |  | 1160 | 19557.6 |  | 74.8 | 53.29 | 144.7 | 32.6 | 230.59 | 3887.7474 | n | 534.1245 | 0 |  |  | 20405.659 | 21307.5527 | 38377.3639 | 104309.3673 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-08-07 | 8:52 | 181 | 346470 | 17110 | 7.91 | 74.8 |  | 1310.1 | 22415.811 |  | 96.25 | 11.62 | 163.19 | 31.98 | 206.79 | 3538.1769 | n | 498.8768 |  |  |  | 21026.9068 | 21405.6793 | 35892.3729 | 103131.8487 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-08-14 | 8:55 | 185 | 363940 | 17470 | 7.66 | 59.2 |  | 1382 | 24143.54 |  | 107.5 | 240.68 | 20.74 | 30.74 | 292.16 | 5104.0352 | n | 639.766 | 2.4 |  |  | 20531.2378 | 21583.7343 | 37875.049 | 100995.1887 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-08-21 | 8:45 | 199 | 382840 | 18900 | 7.71 | 44.8 |  | 1473.08 | 27841.212 |  | 130.2 | 27.92 | 233.93 | 25.92 | 233.93 | 4421.277 | n | 754.825 |  |  |  | 23489.5408 | 22315.6406 | 26041.837 | 92212.3127 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-08-28 | 8:41 | 187 | 400330 | 17490 | 7.75 | 37.2 |  | 1223.3 | 21395.517 |  | 76.89 | 90.18 | 226.52 | 47.93 | 364.63 | 6377.3787 | n | 872.7939 |  |  |  | 23949.02 | 22427.7109 | 24203.92 | 90867.4697 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-09-04 | 9:00 | 180 | 417330 | 17000 | 7.65 | 37.6 |  | 1229 | 20893 |  | 66.1 | 75.16 | 171.43 | 138.95 | 385.54 | 6554.18 | n | 936.9694 |  |  |  | 23568.3173 | 22029.4388 | 25726.731 | 95646.7339 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-09-11 | 8:48 | 182 | 434530 | 17200 | 7.68 | 51.2 |  | 1270.9 | 21859.48 |  | 51.85 | 95.3354 | 271.49 | 74.25 | 441.0754 | 7586.4969 | N | 1048.9972 |  |  |  | 22997.3023 | 21752.8263 | 28010.791 | 98966.0839 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-09-18 | 8:45 | 183 | 452910 | 18380 | 7.66 | 34.8 |  | 1198.84 | 22034.6792 |  | 79.88 | 51.09 | 169.33 | 66.31 | 286.73 | 5270.0974 | N | 739.8941 | 5.56 |  |  | 21545.6691 | 21725.7429 | 33817.3238 | 99291.0847 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-09-25 | 8:35 | 203 | 472200 | 19290 | 7.43 | 45.6 |  | 1317.65 | 25417.4685 |  | 120.9 | 54.19 | 272.07 | 56.15 | 382.41 | 7376.6889 | n | 1026.8564 |  |  |  | 22551.1569 | 22301.9453 | 29795.3723 | 92376.6562 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-10-02 | 8:36 | 191 | 490330 | 18130 | 7.98 | 30.4 |  | 1179 | 21375.27 |  | 76.24 | 61.7 | 199.76 | 57 | 318.46 | 5773.6798 | n | 802.1587 | 0 |  |  | 22671.7244 | 22422.3161 | 29313.1023 | 90932.2062 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-10-09 | 8:50 | 183 | 507600 | 17270 | 7.99 | 23.6 |  | 1282 | 22140.14 |  | 46.2 | 73.8 | 212.6292 | 33.2732 | 319.7024 | 5521.2601 | n | 753.9811 | 2.8 |  |  | 22741.8894 | 22090.1431 | 29032.4423 | 94918.2823 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-10-16 | 8:35 | 177 | 523920 | 16320 | 8.29 | 58 |  | 1626 | 26536.32 |  | 141.2 | 88.3 | 319.76 | 30.02 | 438.08 | 7149.4656 | n | 974.6269 | 6.3 |  |  | 23867.2996 | 22967.5031 | 24530.8015 | 84389.9623 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-10-20 | 9:03 | 151 | 38020 | 14100 | 7.71 | 41.6 |  | 1361.52 | 19197.432 |  | 67.82 | 100.71 | 256.3 | 63.37 | 420.38 | 5927.358 | n | 814.6271 | 6.33 |  |  | 22312.2905 | 22937.4891 | 30750.838 | 84750.1303 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-10-30 | 8:20 | 176 | 54490 | 16470 | 7.4 | 19.2 |  | 546 | 8992.62 |  | 46.05 | 30.33 | 94.05 | 21 | 145.38 | 2394.4086 | n | 330.144 | trace M only |  |  | 19216.628 | 21818.8899 | 43133.488 | 98173.3213 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-11-06 | 8:28 | 156 | 69080 | 14590 | 7.65 | 46 |  | 1451 | 21170.09 |  | 96.71 | 73.66 | 231.8 | 59.1 | 364.56 | 5318.9304 | n | 736.1393 | trace only |  |  | 18974.1155 | 21571.1024 | 44103.538 | 101146.7713 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-11-13 | 8:47 | 153 | 83320 | 14240 | 7.66 | 38 |  | 1128 | 16062.72 |  | 60.17 | 29.7 | 167.88 | 53.15 | 250.73 | 3570.3952 | n | 503.7715 | 0 |  |  | 16355.7155 | 20589.5614 | 54577.138 | 112925.2633 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-11-20 | 8:58 | 154 | 97810 | 14490 | 7.6 | 82 |  | 1318.29 | 19102.0221 |  | 76.53 | 74.84 | 178.12 | 89.17 | 342.13 | 4957.4637 | n | 695.4376 | 4.35 |  |  | 16331.863 | 20398.4368 | 54672.5479 | 115218.7582 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-11-27 | 8:44 | 168 | 113540 | 15730 | 7.92 | 82.8 |  | 1679 | 26410.67 |  | 117.6 | 168.92 | 144.8 | 53.93 | 367.65 | 5783.1345 | n | 770.1774 | 2.28 |  |  | 20686.3755 | 20858.2427 | 37254.4979 | 109701.0882 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-12-04 | 8:40 | 121 | 127090 | 13550 | 7.48 | 37.2 |  | 1168.63 | 15834.9365 |  | 81.88 | 48.09 | 55.44 | 182.14 | 285.67 | 3870.8285 | n | 579.2489 | 0 |  |  | 19352.5871 | 20356.1974 | 42589.6514 | 115725.6317 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-12-11 | 8:40 | 167 | 142470 | 15380 | 7.78 | 42.8 |  | 1101.88 | 16946.9144 |  | 33.58 | 78.09 | 188.51 | 53.78 | 320.38 | 4927.4444 | n | 678.6956 | 0 |  |  | 19573.6358 | 19932.217 | 41705.457 | 120813.3965 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-12-18 | 8:49 | 169 | 158450 | 15980 | 7.66 | 45.6 |  | 1649.01 | 26351.1798 |  | 136.8 | 62.7 | 329.86 | 46.22 | 438.78 | 7011.7044 | n | 969.4017 | 0 |  |  | 21385.9252 | 20010.0262 | 34456.2993 | 119879.6852 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-12-24 | 8:30 | 150 | 172240 | 13790 | 8.13 | 64 |  | 1776.53 | 28581.4068 |  | 146.1 | 125.37 | 258.12 | 47.57 | 431.06 | 6935.037 | n | 805.8254 | 0 |  |  | 21928.6094 | 20610.5376 | 32285.5625 | 112673.5484 | 8000 | 30000 | 100 | 6 | 10 | 35000
2020-12-31 | 8:45 | 177 | 188890 | 16650 | 7.82 | 30.8 |  | 1657.29 | 27593.8785 |  | 157.4 | 97.65 | 222.24 | 40.06 | 359.95 | 5993.1675 | n | 814.7943 | 0 |  |  | 24868.3449 | 21065.0158 | 20526.6205 | 107219.8099 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-01-08 | 8:49 | 181 | 206080 | 17190 | 7.84 | 41.2 |  | 1528 | 26266.32 |  | 93.7 | 135 | 210.06 | 52.8 | 397.86 | 6839.2134 | n | 924.2655 | 0 |  |  | 27198.1963 | 21042.5158 | 11207.2149 | 107489.8099 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-01-15 | 8:30 | 172 | 222260 | 16180 | 7.67 | 53 |  | 1287.64 | 20834.0152 |  | 51.66 | 53.2 | 212.26 | 55.75 | 321.21 | 5197.1778 | n | 724.2047 | 4.83 |  |  | 25818.9051 | 21178.8978 | 16724.3795 | 105853.2267 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-01-22 | 8:45 | 165 | 237700 | 15440 | 7.74 | 34.8 |  | 1392.86 | 21505.7584 |  | 81.6 | 31.24 | 211.68 | 69.21 | 312.13 | 4819.2872 | n | 682.7127 | 0 |  |  | 24049.993 | 22221.6593 | 23800.0279 | 93340.0883 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-01-29 | 8:42 | 157 | 252490 | 14790 | 7.73 | 51.2 |  | 1481.81 | 21915.9699 |  | 89.54 | 45.89 | 174.2 | 108.29 | 328.38 | 4856.7402 | n | 696.071 | 0 |  |  | 22630.5159 | 22283.816 | 29477.9365 | 92594.2084 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-02-05 | 8:57 | 155 | 267970 | 15480 | 7.86 | 57.6 |  | 1455 | 22523.4 |  | 88.39 | 77.67 | 222.52 | 37.6 | 337.79 | 5228.9892 | n | 715.0023 | 5.13 |  |  | 21694.7859 | 22822.206 | 33220.8565 | 86133.5284 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-02-12 | 9:03 | 196 | 283810 | 15840 | 7.77 | 69.6 |  | 1522.9 | 24122.736 |  | 117.4 | 48.26 | 236.86 | 100.22 | 385.34 | 6103.7856 | n | 866.9887 | 0 |  |  | 22516.9661 | 23240.5988 | 29932.1357 | 81112.8145 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-02-19 | 8:45 | 174 | 301230 | 17420 | 7.74 | 46.8 |  | 1351.77 | 23547.8334 |  | 94.61 | 96.41 | 206.75 | 17.38 | 320.54 | 5583.8068 | n | 748.9108 | 0 |  |  | 23027.4848 | 23002.0291 | 27890.0607 | 83975.6511 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-02-26 | 6:00 | 126 | 317640 | 16410 | 7.6 | 59.2 |  | 1248 | 20479.68 |  | 79.3 | 42.6658 | 203.0799 | 21.3874 | 267.1331 | 4383.6548 | n | 602.1921 | n/a |  |  | 22668.4123 | 23389.091 | 29326.3506 | 79330.9076 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-03-05 | 8:55 | 230 | 330050 | 12410 | 7.75 | 64.8 |  | 1159 | 14383.19 |  | 56.15 | 33.81 | 181.99 | 15.6 | 231.4 | 2871.674 | n | 394.4186 | n/a |  |  | 20633.3599 | 23175.4473 | 37466.5606 | 81894.632 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-03-12 | 8:45 | 161 | 346130 | 16080 | 7.71 | 52.8 |  | 1312.74 | 21108.8592 |  | 79.49 | 171.44 | 117.42 | 18.74 | 307.6 | 4946.208 | n | 640.0782 | n/a |  |  | 19879.8907 | 22738.5873 | 40480.4374 | 87136.9526 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-03-19 | 9:04 | 193 | 363720 | 17590 | 7.77 | 56.4 |  | 1388 | 24414.92 |  | 113.9 | 54.22 | 179.576 | 38.744 | 272.54 | 4793.9786 | n | 661.6347 | n/a |  |  | 20096.6623 | 22391.38 | 39613.3508 | 91303.4394 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-03-26 | 8:45 | 155 | 378280 | 14560 | 7.55 | 46.4 |  | 1573.12 | 22904.6272 |  | 127.5 | 175.87 | 151.37 | 35.69 | 362.93 | 5284.2608 | n | 695.5235 | n/a |  |  | 20702.8991 | 22000.6091 | 37188.4036 | 95992.6907 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-04-01 | 8:50 | 120 | 390200 | 11920 | 7.84 | 57.6 |  | 1561.26 | 21711.9224 |  | 94.8 | 154.36 | 138.65 | 25.84 | 318.85 | 4434.1407 | n | 498.821 | n/a |  |  | 22535.0822 | 21621.076 | 29859.6712 | 100547.0883 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-04-09 | 8:40 | 190 | 407220 | 17020 | 7.71 | 49.6 |  | 1347.18 | 20062.8782 |  | 79.97 | 123.16 | 117.48 | 22.26 | 262.9 | 3915.2382 | n | 588.9519 | n/a |  |  | 22273.5869 | 21556.8146 | 30905.6522 | 101318.2253 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-04-16 | 8:50 | 155 | 421780 | 14560 | 8.08 | 45.6 |  | 1513.64 | 22038.5984 |  | 86.76 | 237.17 | 153.81 | 19.32 | 410.3 | 5973.968 | n | 768.8915 | n/a |  |  | 21679.5065 | 21601.2179 | 33281.9739 | 100785.3853 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-04-23 | 8:40 | 161 | 436840 | 15060 | 7.82 | 48.8 |  | 1332 | 20059.92 |  | 92.2 | 117.16 | 142.84 | 16.46 | 276.46 | 4163.4876 | n | 549.2003 | n/a |  |  | 20968.3297 | 21446.5471 | 36126.681 | 102641.4352 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-04-30 | 8:45 | 146 | 450420 | 13580 | 7.81 | 56.8 |  | 1588.24 | 21568.2992 |  | 82.65 | 178.33 | 128.99 | 50.04 | 357.36 | 4852.9488 | n | 641.9381 | n/a |  |  | 20932.4239 | 21366.9553 | 36270.3043 | 103596.536 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-05-07 | 8:45 | 161 | 465590 | 15170 | 7.92 | 43.6 |  | 1623 | 24620.91 |  | 96.6 | 184 | 179 | 90 | 453 | 6872.01 | n | 930.099 | n/a |  |  | 22071.9319 | 21408.4698 | 31712.2724 | 103098.362 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-05-14 | 9:19 | 163 | 480780 | 15190 | 7.42 | 57.2 |  | 1613 | 24501.47 |  | 82.94 | 64.2607 | 77.4421 | 48.2112 | 189.9141 | 2884.7949 | n | 397.7046 | n/a |  |  | 22687.6498 | 21487.9395 | 29249.4008 | 102144.7254 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-05-21 | 8:40 | 163 | 496300 | 15520 | 8.035 | 74.4 |  | 1849 | 28696.48 |  | 76 | 207.52 | 225.4 | 36.2 | 469.12 | 7280.7424 | n | 960.6927 | n/a |  |  | 24846.7898 | 22172.6729 | 20612.8408 | 93927.9254 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-05-28 | 8:50 | 154 | 10550 | 14249 | 8.29 | 87.2 |  | 1645 | 23439.605 |  | 111.5 | 161.897 | 213.921 | 26.417 | 402.235 | 5731.4465 | n | 759.1257 | n/a |  |  | 25314.6162 | 22927.3741 | 18741.535 | 84871.5105 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-06-04 | 8:37 | 163 | 25700 | 15150 | 7.8 | 58.8 |  | 1714 | 25967.1 |  | 111.4 | 109.587 | 212.851 | 18.373 | 340.811 | 5163.2867 | n | 690.4408 | n/a |  |  | 25651.1637 | 23332.2275 | 17395.345 | 80013.2697 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-06-11 | 8:38 | 145 | 39260 | 13560 | 7.71 | 45.6 |  | 1324 | 17953.44 |  | 61.13 | 10.956 | 253.577 | 42.584 | 307.117 | 4164.5065 | n | 587.3224 | n/a |  |  | 24014.1562 | 22793.7709 | 23943.375 | 86474.7496 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-06-18 | 8:42 | 142 | 52410 | 13150 | 7.79 | 59.2 |  | 1534 | 20172.1 |  | 55.77 | 18.34 | 423.6 | 27.88 | 469.82 | 6178.133 | n | 859.981 | n/a |  |  | 21883.0612 | 22566.0603 | 32467.755 | 89207.2768 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-06-25 | 8:49 | 160 | 67320 | 14910 | 7.73 | 50 |  | 1624 | 24213.84 |  | 114.5 | 43.592 | 311.811 | 12.84 | 368.243 | 5490.5031 | n | 753.0097 | n/a |  |  | 22076.62 | 22774.5534 | 31693.52 | 86705.3592 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-07-02 | 8:30 | 137 | 79620 | 12300 | 7.71 | 24.4 |  | 1177 | 14477.1 |  | 13.9 | 158.4 | 102.21 | 80.96 | 341.57 | 4201.311 | n | 567.6403 | n/a |  |  | 19204.12 | 22309.0719 | 43183.52 | 92291.1374 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-07-09 | 8:33 | 146 | 93260 | 13640 | 7.69 | 35.2 |  | 1418 | 19341.52 |  | 83.13 | 4.422 | 263.286 | 28.873 | 296.581 | 4045.3648 | n | 568.3849 | 6.862 |  |  | 19551.14 | 22084.3154 | 41795.44 | 94988.2158 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-07-16 | 8:46 | 141 | 106520 | 13260 | 7.76 | 42.4 |  | 1520.2 | 20157.852 |  | 105 | 0.1 | 293.61 | 116.8 | 410.51 | 5443.3626 | n | 789.0467 | 8.135 |  |  | 19547.578 | 22092.4764 | 41809.688 | 94890.2838 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-07-23 | 8:45 | 153 | 120770 | 14250 | 7.89 | 61.6 |  | 1561 | 22244.25 |  | 124.5 | 63.0543 | 221.68 | 115.3324 | 400.0667 | 5700.9505 | N | 809.8577 | 7.268 |  |  | 19055.1805 | 22148.8056 | 43779.278 | 94214.333 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-07-30 | 9:05 | 166 | 136310 | 15540 | 7.69 | 70.8 |  | 1634 | 25392.36 |  | 113 | 0 | 248.095 | 71.844 | 319.939 | 4971.8521 | N | 714.0709 |  |  |  | 21783.9955 | 22213.0931 | 32864.018 | 93442.883 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-08-06 | 8:35 | 19 | 138230 | 1920 | 7.49 | 65.2 |  | 444 | 852.48 |  | 6.505 | 96.04 | 211.101 | 70.023 | 377.164 | 724.1549 | n | 99.8814 | na |  |  | 17161.7355 | 20242.3439 | 51353.058 | 117091.873 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-08-13 | 8:41 | 82 | 146180 | 7950 | 7.56 | 47.6 |  | 641 | 5095.95 |  | 4.03 | 220.1554 | 162.686 | 68.9168 | 451.7582 | 3591.4777 | N | 476.8726 | na |  |  | 13396.26 | 18275.6331 | 66414.96 | 140692.403 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-08-20 | 8:52 | 175 | 162750 | 16570 | 7.62 | 52 |  | 997 | 16520.29 |  | 38.67 | 203.8075 | 157.0028 | 19.4617 | 380.272 | 6301.1074 | N | 816.5987 | N/A |  |  | 11965.27 | 17699.0235 | 72138.92 | 147611.718 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-08-27 | 9:05 | 150 | 176750 | 14000 | 7.78 | 59.6 |  | 1418 | 19852 |  | 59.77 | 4.179 | 318.214 | 21.805 | 344.198 | 4818.7719 | N | 673.6488 | N/A |  |  | 10580.18 | 17189.4318 | 77679.28 | 153726.818 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-09-03 | 8:48 | 166 | 192360 | 15610 | 7.76 | 27.6 |  | 1560 | 24351.6 |  | 125.2 | 51.2847 | 334.233 | 30.46 | 415.9777 | 6493.4119 | n | 895.5077 | NA |  |  | 16454.96 | 17722.6118 | 54180.16 | 147328.658 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-09-10 | 8:50 | 147 | 206020 | 13660 | 7.83 | 55.2 |  | 1472 | 20107.52 |  | 90.29 | 0 | 424.9 | 26.126 | 451.026 | 6161.0152 | n | 861.9626 | N/A |  |  | 20207.8525 | 17717.2302 | 39168.59 | 147393.238 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-09-17 | 8:51 | 164 | 221430 | 15410 | 7.77 | 49.2 |  | 1151 | 17736.91 |  | 52 | 4.4901 | 308.1134 | 20.7119 | 333.3154 | 5136.3895 | N | 717.7825 | N/A |  |  | 20512.0075 | 17177.486 | 37951.97 | 153870.168 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-09-24 | 8:55 | 149 | 235380 | 13950 | 7.9 | 72 |  | 1302 | 18162.9 |  | 65.72 | 24.69 | 270.22 | 14.34 | 309.25 | 4314.0375 | N | 595.9187 | N/A |  |  | 20089.7325 | 17484.636 | 39641.07 | 150184.368 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-10-01 | 8:51 | 167 | 250890 | 15510 | 8.11 | 64.4 |  | 1699 | 26351.49 |  | 146.02 | 37.1109 | 310.1616 | 21.7055 | 368.978 | 5722.8496 | N | 789.8648 | N/A |  |  | 20589.705 | 18068.8002 | 37641.18 | 143174.398 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-10-08 | 8:45 | 167 | 266630 | 15740 | 7.97 | 64.4 |  | 1533 | 24129.42 |  | 125.8 | 124.36 | 186.49 | 56.32 | 367.17 | 5779.2558 | N | 783.754 | N/A |  |  | 21595.18 | 18399.7642 | 33619.28 | 139202.83 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-10-15 | 8:46 | 163 | 281890 | 15260 | 7.94 | 19.2 |  | 1369 | 20890.94 |  | 85.1 | 89.69 | 213.75 | 38.69 | 342.13 | 5220.9038 | n | 710.915 | NA |  |  | 22383.6875 | 18286.9883 | 30465.25 | 140556.14 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-10-22 | 8:38 | 136 | 294540 | 12650 | 7.88 | 48.8 |  | 1283 | 16229.95 |  | 72.4 | 27.95 | 223.63 | 27.95 | 279.53 | 3536.0545 | n | 491.3306 | N/A |  |  | 21900.45 | 17523.4542 | 32398.2 | 149718.55 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-10-29 | 8:48 | 158 | 309340 | 14800 | 7.97 | 46.4 |  | 1310 | 19388 |  | 84.56 | 100.8765 | 235.1828 | 34.3563 | 370.4156 | 5482.1504 | N | 742.9435 | N/A |  |  | 20159.5775 | 19068.0808 | 39361.69 | 131183.03 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-11-05 | 8:50 | 168 | 325090 | 15750 | 7.72 | 8.8 |  | 1247 | 19640.25 |  | 50.91 | 182.7823 | 147.5183 | 19.2082 | 349.5088 | 5504.763 | n | 715.2144 | na |  |  | 19037.285 | 20280.1058 | 43850.86 | 116638.73 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-11-12 | 8:58 | 195 | 343660 | 18570 | 8.16 | 40 |  | 1367 | 25385.19 |  | 108.4 | 163.5354 | 177.0362 | 19.5483 | 360.1199 | 6687.4273 | N | 877.5016 | N/A |  |  | 20160.8475 | 21018.8475 | 39356.61 | 107773.83 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-11-19 | 8:45 | 160 | 358630 | 14970 | 7.77 | 85.6 |  | 1677 | 25104.69 |  | 146.9 | 121.98 | 191.27 | 26.35 | 339.6 | 5083.812 | n | 678.8715 | N/A |  |  | 22379.5325 | 21456.5717 | 30481.87 | 102521.14 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-11-26 | 8:49 | 142 | 371740 | 13110 | 7.96 | 40 |  | 1420 | 18616.2 |  | 72.74 | 116.47 | 160.43 | 26.22 | 303.12 | 3973.9032 | n | 529.5616 | N/A |  |  | 22186.5825 | 20978.6217 | 31253.67 | 108256.54 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-12-03 | 8:58 | 176 | 388610 | 16870 | 7.61 | 47.6 |  | 1474 | 24866.38 |  | 124.7 | 138 | 136 | 30 | 303 | 5111.61 | n | 678.0372 | N/A |  |  | 23493.115 | 21375.1933 | 26027.54 | 103497.68 | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-12-10 | 9:04 | 158 | 403480 | 14870 | 8.06 | 68.8 |  | 1508 | 22423.96 |  | 96.39 | 228.9 | 104.2 | 25.1 | 358.2 | 5326.434 | n | 682.1224 | n/a | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-12-17 | 8:48 | 172 | 419610 | 16130 | 7.6 | 47.2 |  | 1543 | 24888.59 |  | 143.7 | 129.749 | 156.889 | 36.7909 | 323.4289 | 5216.9086 | n | 696.7013 | N/A | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-12-24 | 8:45 | 171 | 435700 | 16090 | 8.01 | 38.8 |  | 1509 | 24279.81 |  | 111 | 115.951 | 156.524 | 25.304 | 297.779 | 4791.2641 | n | 637.8524 | n/a | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2021-12-31 | 8:48 | 152 | 449860 | 14160 | 7.7 | 31.6 |  | 1548 | 21919.68 |  | 144.9 | 100.21 | 221.75 | 31.82 | 353.78 | 5009.5248 | n | 677.5422 | n/a | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-01-07 | 8:54 | 191 | 468130 | 18270 | 8.1 | 50 |  | 1331 | 24317.37 |  | 108.3 | 130.546 | 169.516 | 28.288 | 328.35 | 5998.9545 | n | 797.8554 | n/a | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-01-14 | 8:35 | 156 | 483730 | 15600 | 8.14 | 65.6 |  | 1294.23 | 20189.988 |  | 82.56 | 85.45 | 191.23 | 18.14 | 294.82 | 4599.192 | n | 618.5555 | n/a | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-01-21 | 8:57 | 166 | 499360 | 15630 | 8.012 | 48.8 |  | 1280 | 20006.4 |  | 78.84 | 96.78 | 161.65 | 30.7 | 289.13 | 4519.1019 | n | 608.4395 | n/a | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-01-28 | 9:00 | 177 | 15870 | 15230 | 8.13 | 45.2 |  | 1510 | 22997.3 |  | 114 | 69.19 | 219.07 | 31.91 | 320.17 | 4876.1891 | n | 666.7728 | n/a | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-02-04 | 8:50 | 153 | 29550 | 13680 | 8.15 | 52.4 |  | 1455 | 19904.4 |  | 91.44 | 248.17 | 158.83 | 23.58 | 430.58 | 5890.3344 | n | 759.3231 | n/a | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-02-11 | 8:43 | 175 | 46060 | 16510 | 8 | 49.2 |  | 1347 | 22238.97 |  | 98.9 | 97 | 165 | 6 | 268 | 4424.68 | n | 585.1745 | n/a | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-02-18 | 8:42 | 180 | 61130 | 15070 | 7.98 | 37.6 |  | 1225 | 18460.75 |  | 78.08 | 129.97 | 130.31 | 21.87 | 282.15 | 4252.0005 | n | 559.6101 | n/a | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-02-25 | 8:48 | 168 | 78920 | 17790 | 7.96 | 59.6 |  | 1512 | 26898.48 |  | 104.1 | 208.115 | 142.822 | 14.086 | 365.023 | 6493.7592 | n | 835.5335 | n/a | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-03-04 | 8:57 | 167 | 94570 | 15650 | 7.087 | 42.8 |  | 1259 | 19703.35 |  | 80.21 | 69.72 | 208.97 | 29.22 | 307.91 | 4818.7915 | n | 657.4686 | n/a | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-03-11 | 8:48 | 167 | 110190 | 15620 | 8.02 | 49.6 |  | 1407 | 21977.34 |  | 105.2 | 176.55 | 195.238 | 41.93 | 413.718 | 6462.2752 | n | 858.0955 | n/a | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-03-18 | 8:54 | 166 | 125840 | 15650 | 8.08 | 48.8 |  | 1255 | 19640.75 |  | 97.29 | 100.2 | 168.46 | 35.04 | 303.7 | 4752.905 | n | 641.3253 | n/a | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-03-25 | 8:49 | 148 | 139480 | 13640 | 8.03 | 54 |  | 1252 | 17077.28 |  | 79.83 | 132.097 | 142.797 | 32.735 | 307.629 | 4196.0596 | n | 557.4371 | n/a | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-04-01 | 8:50 | 150 | 153190 | 13710 | 8.216 | 56.8 |  | 1353 | 18549.63 |  | 104.3 | 168.4438 | 122.9259 | 57.2344 | 348.604 | 4779.3615 | N | 636.213 | N/A | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-04-08 | 8:51 | 181 | 170370 | 17180 | 8.188 | 32.8 |  | 1138 | 19550.84 |  | 76.94 | 118.45 | 149.27 | 8.71 | 276.43 | 4749.0674 | n | 623.05 | N/A | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-04-14 | 8:49 | 150 | 184380 | 14010 | 7.82 | 41.2 |  | 1287 | 21036.015 |  | 91.54 | 143.98 | 129.45 | 39.12 | 312.55 | 5108.6298 | n | 580.9543 | n/a | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-04-22 | 8:50 | 190 | 202330 | 17950 | 7.66 | 58.8 |  | 1175 | 18454.8438 |  | 50.95 | 57.309 | 223.17 | 25.84 | 306.319 | 4811.1228 | n | 753.0044 | n/a | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-04-29 | 8:53 | 100 | 217650 | 15320 | 8.09 | 38 |  | 1189 | 18215.48 |  | 71.96 | 102.78 | 154.71 | 31.9 | 289.39 | 4433.4548 | n | 595.5917 | n/a | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-05-06 | 9:00 | 141 | 230810 | 13160 | 7.809 | 38.4 |  | 1111 | 14620.76 |  | 29.56 | 51.7234 | 223.125 | 16.8408 | 291.6892 | 3838.6304 | N | 524.1281 | N/A | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-05-13 | 8:50 | 165 | 246270 | 15460 | 8.107 | 58 |  | 1381 | 21350.26 |  | 104.9 | 186.45 | 129.41 | 44.37 | 360.23 | 5569.1558 | n | 732.6228 | N/A | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-05-20 | 8:47 | 156 | 260850 | 14580 | 7.8 | 71.6 |  | 1660 | 24202.8 |  | 153.9 | 38.91 | 406.63 | 74.13 | 519.67 | 7576.7886 | n | 1063.6025 | n/a | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-05-27 | 8:51 | 149 | 274800 | 13950 | 7.95 | 71.6 |  | 1507 | 21022.65 |  | 117.62 | 38.3 | 277.56 | 60.217 | 376.077 | 5246.2742 | n | 735.8159 | n/a | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-06-03 | 8:52 | 156 | 289400 | 14600 | 7.741 | 72.8 |  | 1551 | 22644.6 |  | 160.42 | 77.77 | 236.71 | 80.01 | 394.49 | 5759.554 | n | 802.8872 | n/a | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-06-10 | 8:57 | 169 | 305120 | 15720 | 8.07 | 63.2 |  | 1239 | 19477.08 |  | 92.49 | 137.78 | 164.55 | 40.16 | 342.49 | 5383.9428 | n | 719.3147 | n/a | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-06-17 | 9:01 | 141 | 319280 | 14160 | 7.86 | 45.6 |  | 1144 | 16199.04 |  | 100.4 | 9.5 | 282.85 | 46.79 | 339.14 | 4802.2224 | n | 677.8832 | n/a | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-06-24 | 9:00 | 170 | 335140 | 15860 | 7.7 | 30.8 |  | 1038 | 16462.68 |  | 35.79 | 30.954 | 245.954 | 15.924 | 292.832 | 4644.3155 | n | 640.094 | n/a | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-07-01 | 8:55 | 177 | 351670 | 16530 | 7.947 | 20.4 |  | 1220 | 20166.6 |  | 88.43 | 53.5886 | 291.595 | 43.8208 | 389.0045 | 6430.2444 | N | 890.6869 | N/A | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-07-08 | 8:43 | 172 | 367880 | 16210 | 7.88 | 42.8 |  | 1124 | 18220.04 |  | 66.39 | 27.05 | 264.86 | 37.66 | 329.57 | 5342.3297 | n | 745.8261 | n/a | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-07-15 | 9:02 | 163 | 383210 | 15330 | 8.06 | 56.4 |  | 1387 | 21262.71 |  | 121.1 | 31.758 | 299.035 | 65.077 | 395.87 | 6068.6871 | N | 854.2284 | N/A | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-07-22 | 8:56 | 130 | 395150 | 11940 | 7.742 | 114.8 |  | 901 | 10757.94 |  | 42.5 | 12.2048 | 224.79 | 5.088 | 242.0828 | 2890.4686 | n | 399.2518 | N/A | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-07-29 | 9:05 | 147 | 408900 | 13750 | 7.699 | 60.8 |  | 854 | 11742.5 |  | 5.27 | 6.5775 | 263.12 | 16.33 | 286.0275 | 3932.8781 | n | 548.4455 | N/A | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-08-05 | 8:54 | 179 | 425780 | 16880 | 7.8 | 46.8 |  | 819 | 13824.72 |  | 19.76 | 4.56 | 206.18 | 13.52 | 224.26 | 3785.5088 | n | 528.3555 | 3.55 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-08-12 | 9:02 | 184 | 443200 | 17420 | 7.87 | 44.8 |  | 1084 | 18883.28 |  | 88.08 | 2 | 220.46 | 29.7 | 252.16 | 4392.6272 | n | 619.759 | 3.3 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-08-19 | 8:57 | 171 | 459310 | 16110 | 8.11 | 77.6 |  | 1305 | 21023.55 |  | 119.3 | 23.26 | 247.69 | 45.25 | 316.2 | 5093.982 | n | 715.2538 | 4.13 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-08-26 | 8:55 | 185 | 476740 | 17430 | 7.83 | 60 |  | 1293 | 22536.99 |  | 93.68 | 20.7041 | 412.4478 | 29.7171 | 462.869 | 8067.8074 | n | 1123.023 | 3.26 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-09-02 | 8:53 | 175 | 493280 | 16540 | 8.11 | 67.6 |  | 1427 | 23602.58 |  | 115.4 | 11.04 | 274.07 | 46.17 | 331.28 | 5479.3712 | n | 773.0892 | 4.38 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-09-09 | 8:53 | 192 | 11490 | 18210 | 7.88 | 49.2 |  | 1482 | 26987.22 |  | 131.1 | 23.17 | 308.98 | 47.48 | 379.63 | 6913.0623 | n | 969.5341 | 4.48 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-09-16 | 9:01 | 156 | 26080 | 14590 | 7.98 | 58.8 |  | 1207 | 17610.13 |  | 53.97 | 8.811 | 298.266 | 15.357 | 322.434 | 4704.3121 | n | 654.6438 | 9.058 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-09-23 | 8:50 | 180 | 43200 | 17120 | 7.898 | 46.4 |  | 1168 | 19996.16 |  | 77.35 | 106.377 | 137.3726 | 21.4909 | 265.2405 | 4540.9174 | N | 603.1192 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-09-30 | 8:55 | 142 | 61720 | 18520 | 7.95 | 48.4 |  | 1243 | 23020.36 |  | 112.7 | 66.9 | 175.67 | 41.21 | 283.78 | 5255.6056 | n | 722.0377 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-10-07 | 8:52 | 190 | 79600 | 17880 | 7.903 | 26 |  | 896 | 16020.48 |  | 20.58 | 99.2551 | 130.4818 | 15.312 | 245.049 | 4381.4754 | N | 579.7997 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-10-14 | 8:53 | 167 | 95370 | 15770 | 8.025 | 37.2 |  | 1117 | 17615.09 |  | 79.34 | 124.55 | 147.47 | 27.06 | 299.08 | 4716.4916 | n | 626.0578 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-10-21 | 8:48 | 172 | 111570 | 16200 | 7.959 | 44.8 |  | 1432 | 23198.4 |  | 125.2 | 165.6613 | 148.2706 | 54.923 | 368.8549 | 5975.4494 | N | 797.2549 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-10-28 | 8:42 | 179 | 128260 | 16690 | 8.2 | 54 |  | 1432 | 23900.08 |  | 120.7 | 36.28 | 248.78 | 50.26 | 335.32 | 5596.4908 | n | 782.9841 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-11-04 | 8:53 | 158 | 143000 | 14740 | 8.14 | 50.8 |  | 1324 | 19515.76 |  | 82.8 | 115.3 | 195.2 | 32.7 | 343.2 | 5058.768 | n | 679.751 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-11-11 | 8:54 | 159 | 157880 | 14880 | 8.049 | 44.4 |  | 1223 | 18198.24 |  | 48.02 | 109.89 | 127.1 | 37.57 | 274.56 | 4085.4528 | n | 547.7745 | 159.73 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-11-18 | 8:52 | 186 | 175500 | 17620 | 8.266 | 44.4 |  | 1232.69 | 21719.9978 |  | 98.92 | 141.517 | 137.5624 | 47.2303 | 326.3097 | 5749.5767 | N | 768.2671 | N/A | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-11-25 | 9:00 | 189 | 193370 | 17870 | 8.9 | 35.6 |  | 1206.4 | 21558.368 |  | 51.27 | 94.279 | 188.529 | 13.295 | 296.103 | 5291.3606 | n | 706.8194 | N/A | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-12-02 | 8:54 | 186 | 211030 | 17660 | 8.087 | 44.8 |  | 1215.75 | 21470.145 |  | 69.86 | 81.6012 | 190.1349 | 25.7694 | 297.5055 | 5253.9473 | N | 711.1043 | N/A | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-12-09 | 8:49 | 187 | 228720 | 17690 | 8.293 | 58 |  | 1309 | 23156.21 |  | 108 | 97.1963 | 240.24 | 24.8343 | 362.2706 | 6408.5664 | n | 865.5229 | 5.86 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-12-16 | 8:49 | 131 | 241910 | 13190 | 8.003 | 34.8 |  | 937.98 | 12371.9562 |  | 66.52 | 81.27 | 147.76 | 22.69 | 251.72 | 3320.1868 | n | 446.5799 | n/a | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-12-23 | 8:56 | 188 | 260720 | 18810 | 8.02 | 24 |  | 1195 | 22477.95 |  | 81.95 | 101.11 | 155.51 | 22.92 | 279.54 | 5258.1474 | n | 702.4171 | 5.3 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2022-12-30 | 8:49 | 165 | 276210 | 15490 | 7.99 | 46 |  | 1532 | 23730.68 |  | 134.9 | 70.72 | 248.13 | 23.36 | 342.21 | 5300.8329 | n | 722.075 | 7.5 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-01-06 | 8:48 | 158 | 291940 | 15730 | 8.077 | 50.4 |  | 1373 | 21597.29 |  | 96.76 | 113.35 | 221.76 | 18.19 | 353.3 | 5557.409 | n | 742.9182 | 7.42 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-01-13 | 9:04 | 155 | 306440 | 14500 | 8.041 | 65.6 |  | 1281 | 18574.5 |  | 70.31 | 80.463 | 209.421 | 41.941 | 331.825 | 4811.4625 | n | 658.3846 | 7.39 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-01-20 | 8:50 | 154 | 320770 | 14330 | 8.11 | 43.9 |  | 1278 | 18313.74 |  | 76 | 52.84 | 183.91 | 43.27 | 280.02 | 4012.6866 | n | 555.6916 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-01-27 | 8:53 | 151 | 334880 | 14110 | 8.3 | 48.8 |  | 1240 | 17496.4 |  | 76.63 | 21.5753 | 215.58 | 50.605 | 287.7603 | 4060.2984 | n | 572.97 | 2.994 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-02-03 | 9:00 | 122 | 346091 | 11211 | 8.04 | 45.6 |  | 1314 | 14731.254 |  | 74.83 | 110.552 | 205.68 | 51.657 | 367.889 | 4124.4036 | n | 561.1236 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-02-10 | 8:54 | 169 | 363240 | 17149 | 8.08 | 41.6 |  | 1181 | 20252.969 |  | 69.77 | 34.721 | 228.26 | 29.71 | 292.691 | 5019.358 | n | 695.8304 | 3.183 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-02-17 | 8:52 | 150 | 377010 | 13770 | 8.02 | 37.2 |  | 1232 | 16964.64 |  | 75.17 | 38.76 | 193.41 | 46.99 | 279.16 | 3844.0332 | n | 537.1521 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-02-24 | 9:02 | 150 | 391050 | 14040 | 8.116 | 48 |  | 1353 | 18996.12 |  | 79.61 | 76.12 | 154.71 | 32.67 | 263.5 | 3699.54 | n | 502.7804 | 2.2 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-03-03 | 9:00 | 160 | 406170 | 15120 | 7.91 | 59.2 |  | 1750 | 26460 |  | 75.51 | 113.48 | 206.29 | 75.06 | 394.83 | 5969.8296 | n | 820.2914 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-03-10 | 8:55 | 169 | 422080 | 15910 | 8.07 | 44.8 |  | 1422 | 22624.02 |  | 85.2 | 80.59 | 216.85 | 37.9 | 335.34 | 5335.2594 | n | 728.6862 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-03-17 | 8:53 | 157 | 436680 | 14600 | 8.02 | 34.4 |  | 1384 | 20206.4 |  | 93.33 | 81.4 | 244.5 | 57.05 | 382.95 | 5591.07 | n | 771.0511 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-03-24 | 8:46 | 165 | 451910 | 15230 | 8.17 | 49.6 |  | 1514 | 23058.22 |  | 122 | 88.15 | 268.68 | 75.16 | 431.99 | 6579.2077 | n | 912.0539 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-03-31 | 8:50 | 122 | 463030 | 11120 | 7.762 | 66 |  | 904 | 10052.48 |  | 24.1 | 53.56 | 191.42 | 22.85 | 267.83 | 2978.2696 | n | 407.2073 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-04-06 | 8:49 | 149 | 476940 | 13910 | 8.05 | 90.8 |  | 1428 | 19863.48 |  | 82.59 | 76.51 | 210.18 | 45.39 | 332.08 | 5386.5 | n | 634.1992 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-04-14 | 8:54 | 194 | 495280 | 18340 | 8.358 | 48.8 |  | 1129 | 20705.86 |  | 94.14 | 83.86 | 178.53 | 47.48 | 309.87 | 4972 | n | 778.0144 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-04-21 | 8:40 | 170 | 9989 | 14709 | 8.259 | 50.8 |  | 1557 | 22901.913 |  | 119.5 | 203.7104 | 229.9568 | 32.224 | 465.8913 | 6852.7951 | N | 903.6664 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-04-28 | 8:42 | 156 | 26620 | 16631 | 7.76 | 126.8 |  | 1219 | 20273.189 |  | 35.79 | 143.9885 | 257.5334 | 27.9879 | 429.5097 | 7143.1762 | n | 955.133 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-05-05 | 8:49 | 165 | 42070 | 15450 | 8.04 | 30.4 |  | 1319 | 20378.55 |  | 73.02 | 72.1986 | 200.051 | 20.2677 | 292.5173 | 4519.3917 | N | 612.2905 | 13.5952 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-05-12 | 8:48 | 161 | 58230 | 16160 | 8.04 | 30.4 |  | 1205 | 19472.8 |  | 77.35 | 75.74 | 208.12 | 47.06 | 330.92 | 5347.6672 | n | 735.023 | 12.02 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-05-19 | 8:53 | 172 | 74390 | 16160 | 7.93 | 33.6 |  | 1350 | 21816 |  | 102.4 | 71.9927 | 251.0165 | 91.484 | 414.4932 | 6698.2098 | N | 939.3879 | 27.7315 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-05-26 | 9:10 | 141 | 87500 | 13110 | 8.124 | 46 |  | 1565 | 20517.15 |  | 109.9 | 84.0498 | 201.6346 | 107.7911 | 393.4755 | 5158.4637 | N | 725.6684 | 32.5618 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-06-02 | 8:56 | 135 | 99980 | 12480 | 8.3 | 30.4 |  | 1543 | 19256.64 |  | 96.94 | 101.94 | 229.67 | 4.25 | 335.86 | 4191.5328 | n | 558.0719 | 135.89 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-06-09 | 9:07 | 165 | 116430 | 16450 | 8.448 | 38 |  | 1593 | 26204.85 |  | 110.4 | 119.6375 | 153.3408 | 5.5119 | 278.4902 | 4581.164 | n | 599.7297 | 87.44 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-06-16 | 9:10 | 105 | 125870 | 9440 | 8.16 | 40 |  | 859 | 8108.96 |  | 48.11 | 49.06 | 157.27 | 6.07 | 212.4 | 2005.056 | n | 270.4278 | 54.88 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-06-23 | 9:15 | 87 | 138170 | 12300 | 8.41 | 34.8 |  | 1201 | 14772.3 |  | 92.15 | 28.83 | 237.96 | 4.974 | 271.764 | 3342.6972 | n | 457.987 | 35.08 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-06-30 | 9:06 | 127 | 149760 | 11590 | 7.7 | 34.4 |  | 815 | 9445.85 |  | 46.48 | 11.676 | 153.128 | 8.211 | 173.015 | 2005.2439 | n | 277.5121 | 26.255 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-07-07 | 8:46 | 121 | 164000 | 14240 | 7.748 | 42 |  | 951.55 | 13550.072 |  | 56.86 | 11.348 | 136.9903 | 10.3567 | 158.695 | 2259.8165 | N | 313.4683 | 11.4499 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-07-14 | 8:57 | 191 | 182050 | 18050 | 7.72 | 73.6 |  | 859 | 15504.95 |  | 46.75 | 7.86 | 112.74 | 7.24 | 127.84 | 2307.512 | n | 320.0788 | N/A | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-07-21 | 8:55 | 171 | 199120 | 17070 | 8.046 | 51.2 |  | 1086 | 18538.02 |  | 59.84 | 20.2122 | 125.629 | 4.155 | 149.9962 | 2560.4351 | N | 349.9537 | N/A | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-07-28 | 9:01 | 200 | 218150 | 19030 | 8.011 | 48.8 |  | 1022 | 19448.66 |  | 43.78 | 38.75 | 137.27 | 6.6 | 182.62 | 3475.2586 | n | 470.5424 | N/A | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-08-04 | 8:44 | 166 | 233640 | 15490 | 7.86 | 40 |  | 1194 | 18495.06 |  | 71.55 | 131.72 | 90.65 | 8.75 | 231.12 | 3580.0488 | n | 460.5914 | N/A | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-08-11 | 8:43 | 184 | 250990 | 17350 | 7.77 | 35.2 |  | 1054 | 18286.9 |  | 63.03 | 25.28 | 151.06 | 16.9 | 193.24 | 3352.714 | n | 462.9589 | N/A | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-08-18 | 8:52 | 161 | 266100 | 15110 | 7.34 | 59.2 |  | 996 | 15049.56 |  | 34.84 | 13.75 | 168.93 | 8.55 | 191.23 | 2889.4853 | n | 399.4661 | n/a | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-08-25 | 9:01 | 190 | 284060 | 17960 | 7.79 | 46.4 |  | 1303 | 23401.88 |  | 81.47 | 26.4667 | 110.6156 | 8.1796 | 145.2618 | 2608.9019 | n | 355.8963 | n/a | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-09-01 | 9:00 | 179 | 301000 | 16940 | 7.742 | 35.6 |  | 1251 | 21191.94 |  | 97.21 | 16.8473 | 190.0114 | 30.5628 | 237.4215 | 4021.9207 | n | 563.6325 | N/A | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-09-08 | 8:57 | 182 | 318250 | 17250 | 7.816 | 38.8 |  | 1094 | 18871.5 |  | 63.12 | 15.63 | 148.33 | 12.94 | 176.9 | 3051.525 | n | 422.8518 | N/A | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-09-15 | 9:01 | 169 | 334100 | 15850 | 7.294 | 64 |  | 1326 | 21017.1 |  | 59.75 | 119.503 | 156.351 | 28.373 | 304.227 | 4821.9979 | n | 642.5224 | N/A | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-09-22 | 8:55 | 178 | 350900 | 16800 | 7.98 | 39.6 |  | 1325 | 22260 |  | 108.9 | 19.762 | 171.27 | 21.693 | 212.725 | 3573.78 | n | 497.2112 | 5.144 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-09-29 | 9:11 | 147 | 365650 | 14750 | 7.93 | 57.6 |  | 1455 | 21461.25 |  | 109.2 | 49.355 | 202.398 | 27.381 | 279.134 | 4117.2265 | n | 565.9137 | 4.128 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-10-06 | 8:54 | 152 | 379800 | 14150 | 7.84 | 58.4 |  | 1552 | 21960.8 |  | 131.48 | 30.4666 | 185.54 | 50.6846 | 266.6912 | 3773.6809 | N | 530.91 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-10-13 | 8:55 | 168 | 395630 | 15830 | 7.9 | 43.6 |  | 1289 | 20404.87 |  | 73.42 | 5.55 | 203.715 | 25.12 | 234.385 | 3710.3144 | N | 521.5055 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-10-20 | 9:01 | 140 | 408690 | 13060 | 7.786 | 65.6 |  | 1230 | 16063.8 |  | 76.89 | 89.135 | 139.914 | 29.309 | 258.358 | 3374.1555 | n | 454.1764 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-10-27 | 8:55 | 146 | 423310 | 14620 | 7.64 | 38.4 |  | 1292 | 18889.04 |  | 77.73 | 125.8141 | 109.94 | 17.8796 | 253.6337 | 3708.125 | N | 484.961 |  | Problems with HPLC - Amines results and RO coming shortly. | [5 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-11-03 | 9:01 | 151 | 437450 | 14140 | 7.6 | 61.2 |  | 914.8 | 12935.272 |  | 37 | 101 | 105 | 30 | 236 | 3337.04 | N | 444.9506 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-11-10 | 8:55 | 166 | 452930 | 15480 | 7.9 | 26.4 |  | 1546 | 23932.08 |  | 112.7 | 165.6 | 165.3 | 43.4 | 374.3 | 5794.164 | N | 769.5443 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-11-17 | 9:00 | 160 | 467940 | 15010 | 7.727 | 30.4 |  | 1329 | 19948.29 |  | 90.65 | 94.738 | 89.354 | 97.79 | 281.882 | 4231.0488 | n | 592.2675 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-11-24 | 8:50 | 143 | 481380 | 13440 | 7.634 | 61.6 |  | 1399 | 18802.56 |  | 47.57 | 81.568 | 180.181 | 28.407 | 290.156 | 3899.6966 | n | 528.2874 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-12-01 | 8:55 | 165 | 496890 | 15510 | 8.233 | 64.8 |  | 1707 | 26475.57 |  | 167.1 | 147.0513 | 179.8249 | 60.1349 | 387.0111 | 6002.5428 | N | 809.6063 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-12-08 | 8:58 | 88 | 4520 | 7620 | 7.75 | 51.2 |  | 1348 | 10271.76 |  | 48.6 | 368.703 | 142.108 | 21.244 | 532.055 | 4054.2591 | n | 512.3309 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-12-15 | 9:00 | 103 | 13810 | 9290 | 7.7 | 20.8 |  | 872.2 | 8102.738 |  | 4.121 | 7.79 | 209.817 | 21 | 238.607 | 2216.659 | N | 310.2395 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-12-22 | 9:00 | 115 | 24310 | 10500 | 8.027 | 34 |  | 1458 | 15309 |  | 81.1 | 102.22 | 165.51 | 24.648 | 292.378 | 3069.969 | N | 410.9677 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2023-12-29 | 8:57 | 168 | 40040 | 15730 | 8.08 | 43.2 |  | 1608 | 25293.84 |  | 157.14 | 81.9128 | 172.8356 | 26.0426 | 280.791 | 4416.8423 | N | 596.9488 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2024-01-05 | 9:00 | 173 | 56360 | 16320 | 7.815 | 48.8 |  | 1425 | 23256 |  | 130.92 | 80.3458 | 233.3543 | 48.5979 | 362.298 | 5912.7032 | n | 812.4181 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2024-01-12 | 8:58 | 150 | 70340 | 13980 | 7.674 | 46.8 |  | 1358 | 18984.84 |  | 72.67 | 49.647 | 213.71 | 36.2398 | 299.5969 | 4188.364 | n | 578.7096 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2024-01-19 | 8:59 | 161 | 85520 | 15180 | 7.71 | 24.4 |  | 1749 | 26549.82 |  | 132 | 68.121 | 298.461 | 63.183 | 429.765 | 6523.8327 | n | 906.0857 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2024-01-26 | 9:07 | 155 | 100040 | 14520 | 7.75 | 44.8 |  | 1282 | 18614.64 |  | 91.96 | 30.6372 | 204.0453 | 30.9194 | 265.6019 | 3856.5392 | N | 536.1514 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2024-02-02 | 8:55 | 122 | 112240 | 12200 | 7.735 | 38.8 |  | 1605 | 19581 |  | 129.7 | 19.3751 | 251.545 | 4.8231 | 275.7432 | 3364.0675 | n | 463.1382 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2024-02-09 | 8:54 | 180 | 128670 | 16430 | 7.6 | 48.8 |  | 1120 | 18401.6 |  | 84.19 | 63.6 | 148 | 12.6 | 224.2 | 3683.606 | N | 495.4088 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2024-02-16 | 9:10 | 159 | 143560 | 14890 | 7.79 | 45.2 |  | 1391 | 20711.99 |  | 98.99 | 50.2139 | 182.379 | 20.765 | 253.3579 | 3772.4994 | N | 515.6445 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2024-02-23 | 8:51 | 147 | 157120 | 13560 | 7.931 | 53.2 |  | 1590 | 21560.4 |  | 113.6 | 66.3485 | 199.3035 | 10.9701 | 276.6221 | 3750.9959 | N | 506.2039 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2024-03-01 | 9:01 | 163 | 171310 | 14190 | 8.246 | 64 |  | 1672 | 23725.68 |  | 171.76 | 68.2315 | 224.95 | 16.997 | 310.1785 | 4401.4333 | n | 597.1265 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2024-03-08 | 9:02 | 134 | 183660 | 12350 | 7.556 | 11.2 |  | 1102 | 13609.7 |  | 76.04 | 28.1053 | 164.9311 | 12.134 | 205.1704 | 2533.8544 | n | 347.9904 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2024-03-15 | 9:04 | 151 | 197260 | 13600 | 7.71 | 49.6 |  | 1434 | 19502.4 |  | 105.5 | 17.0166 | 228.9407 | 20.5983 | 266.5556 | 3625.1556 | N | 504.3586 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2024-03-22 | 8:58 | 151 | 211450 | 14190 | 7.969 | 63.6 |  | 1533 | 21753.27 |  | 113.8 | 19.403 | 319.2054 | 30.6567 | 369.2651 | 5239.8719 | N | 730.8032 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2024-03-28 | 9:00 | 146 | 225060 | 13610 | 8.139 | 43.2 |  | 1534 | 24357.3633 |  | 152.28 | 21.441 | 252.5552 | 46.1867 | 320.183 | 5083.9716 | N | 612.5261 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2024-04-05 | 8:52 | 181 | 242230 | 17170 | 7.85 | 36.4 |  | 1405 | 21108.3688 |  | 114.4 | 16.504 | 245.665 | 39.76 | 301.929 | 4536.1058 | N | 728.4471 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2024-04-12 | 8:53 | 150 | 256480 | 14250 | 7.993 | 58.4 |  | 1455 | 20733.75 |  | 105.5 | 11.2355 | 213.8507 | 26.9445 | 252.0306 | 3591.4358 | N | 503.3523 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2024-04-19 | 8:55 | 165 | 271590 | 15110 | 7.852 | 52 |  | 1506 | 22755.66 |  | 110.9 | 10.166 | 218.012 | 39 | 267.178 | 4037.0596 | N | 569.8252 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2024-04-26 | 8:58 | 143 | 284870 | 13280 | 8.241 | 63.2 |  | 1517 | 20145.76 |  | 118.7 | 37 | 190.84 | 103.84 | 331.68 | 4404.7104 | n | 631.9992 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2024-05-03 | 8:58 | 156 | 299440 | 14570 | 8.099 | 53.6 |  | 1349 | 19654.93 |  | 73.33 | 11.303 | 187.041 | 21.324 | 219.668 | 3200.5628 | n | 447.4508 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2024-05-10 | 9:00 | 158 | 314190 | 14750 | 8.059 | 84 |  | 1441 | 21254.75 |  | 82.5 | 58.7962 | 182.2732 | 25.0363 | 266.1058 | 3925.0606 | n | 535.8657 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2024-05-17 | 8:58 | 159 | 329130 | 14940 | 7.7 | 45.2 |  | 1521 | 22723.74 |  | 109.9 | 10.398 | 221 | 21 | 252.398 | 3770.8261 | n | 526.7423 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2024-05-24 | 9:00 | 161 | 344210 | 15080 | 8.16 | 52 |  | 1353 | 20403.24 |  | 73.33 | 10.72 | 286.85 | 12.2732 | 309.8432 | 4672.4355 | n | 648.7283 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2024-05-31 | 8:56 | 132 | 356440 | 12230 | 8.01 | 78.4 |  | 1703 | 20827.69 |  | 123.42 | 0 | 316.0594 | 19.57 | 335.6294 | 4104.7472 | n | 574.3135 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2024-06-07 | 9:01 | 149 | 370330 | 13890 | 7.831 | 67.2 |  | 1355 | 18820.95 |  | 70.99 | 43.709 | 202.0648 | 14.4846 | 260.2584 | 3614.9892 | n | 494.0669 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2024-06-14 | 8:57 | 136 | 382990 | 12660 | 7.697 | 66.8 |  | 1375 | 17407.5 |  | 64.62 | 101 | 127 | 12.981 | 240.981 | 3050.8195 | n | 402.3136 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2024-06-21 | 9:00 | 150 | 397040 | 14050 | 7.98 | 79 |  | 1896 | 26638.8 |  | 161.26 | 110.3661 | 196.5135 | 30.9186 | 337.7982 | 4746.0647 | n | 638.1665 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2024-06-28 | 9:00 | 142 | 410250 | 13210 | 8.259 | 76.8 |  | 1745 | 23051.45 |  | 135.4 | 3.867 | 276.6206 | 17.4126 | 297.9003 | 3935.263 | N | 549.6444 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2024-07-05 | 8:58 | 148 | 423840 | 13590 | 8.089 | 54.8 |  | 1673 | 22736.07 |  | 82.6 | 6.799 | 264.0028 | 20.1816 | 290.9833 | 3954.4637 | n | 552.5097 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2024-07-12 | 8:56 | 164 | 439350 | 15510 | 8.073 | 32 |  | 1290 | 20007.9 |  | 75.86 | 0 | 215 | 8.1 | 223.1 | 3460.281 | n | 482.4452 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2024-07-19 | 8:58 | 157 | 453990 | 14640 | 8.149 | 84 |  | 1305 | 19105.2 |  | 72.86 | 5.1832 | 221.607 | 17.5548 | 244.3451 | 3577.2117 | n | 500.1453 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2024-07-26 | 9:03 | 111 | 466400 | 12410 | 7.839 | 33.2 |  | 1105 | 13713.05 |  | 42.14 | 4.6261 | 192.5299 | 13.9936 | 211.1496 | 2620.366 | n | 366.0044 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2024-08-02 | 8:58 | 66 | 472990 | 6590 | 7.957 | 64.8 |  | 1216 | 8013.44 |  | 86.91 | 6.4506 | 225.0982 | 16.784 | 248.3329 | 1636.5135 | n | 228.5048 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2024-08-09 | 9:06 | 108 | 482780 | 9790 | 8.154 | 52 |  | 1527 | 14949.33 |  | 120.6 | 0 | 236 | 20.169 | 256.169 | 2507.8945 | n | 352.0333 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2024-08-16 | 9:01 | 115 | 493350 | 10570 | 8.193 | 99.2 |  | 1887 | 19945.59 |  | 117.2 | 4.3424 | 400.458 | 16.965 | 421.7654 | 4458.0599 | n | 621.0787 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2024-08-23 | 8:55 | 150 | 7320 | 13970 | 8.3 | 54.8 |  | 1212 | 16931.64 |  | 77.6 | 26.07 | 136.518 | 13.6402 | 176.2282 | 2461.9081 | n | 338.6014 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2024-08-30 | 9:02 | 160 | 22250 | 14930 | 7.941 | 36.8 |  | 1629 | 24320.97 |  | 137.72 | 38.91 | 222.36 | 8.799 | 270.069 | 4032.1302 | n | 550.8275 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2024-09-06 | 9:11 | 153 | 36460 | 14210 | 7.94 | 65.6 |  | 1763.95 | 25065.7295 |  | 195.86 | 6.394 | 279.43 | 25.77 | 311.594 | 4427.7507 | n | 620.1935 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2024-09-13 | 9:00 | 158 | 50950 | 14490 | 8.032 | 50.4 |  | 1382.69 | 20035.1781 |  | 91.37 | 31.0644 | 162.7304 | 8.9 | 202.6948 | 2937.0477 | n | 401.4597 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
2024-09-20 | 9:05 | 79 | 57830 | 6880 | 7.89 | 46.4 |  | 1107.42 | 7619.0496 |  | 58.89 | 46.4594 | 117.3225 | 12.4655 | 176.2474 | 1212.582 | n | 163.9346 | 0 | [6 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
COPY THIS ROW WEEK 2 to 5 |  |  |  | -57830 |  |  |  |  | 0 | [5 empty] | 0 | 0 |  | 0 | [7 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
Add new rows above this line
COPY THIS ROW WEEK 1 |  |  |  | 0 |  |  |  |  | 0 | [5 empty] | 0 | 0 |  | 0 | [7 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
COPY THIS ROW WEEK 2 to 5 |  |  |  | 0 |  |  |  |  | 0 | [5 empty] | 0 | 0 |  | 0 | [7 empty] | 8000 | 30000 | 100 | 6 | 10 | 35000
Formulas:
SAMPLE DATE = [SAMPLE DATE, row above]+7
SAMPLE DATE = +[SAMPLE DATE, row above]+7
Note on A7: ASellars: IPC limits in force before 21/11/06
Note on A8: ASellars: PPC limits in force after 21/11/06
Note on A423: lfllab: Some ice found in collection container after sample collected and remainder disposed of.
Note on A754: Lab Sl3 - LGL: read after only 6 days
Note on A949: Lab Sl3 - LGL: Due to Christmas and New Year holidays , this represents 7 days sampling but actually refers to an 8 day period. This has now reset future sampling to the correct 7 day sequencing.
Note on B490: lfllab: time on sirco sampler
Note on B498: lfllab: time on Sirco sampler
Note on B499: lfllab: time on sirco sampler
Note on B500: lfllab: time on Sirco sampler
Note on B528: lfllab: Time on Sirco. Actual time was 9.15
Note on B530: lfllab: sirco time
Note on B531: lfllab: sirco time
Note on B535: lfllab: Sirco clock reset to correct time
Note on B544: lfllab: 08:03 on sampler time not changed to BST
Note on B548: lfllab: Sirco time 08:30
Note on B549: lfllab: sirco time 08:16
Note on B556: lfllab: sirco time 08:16
Note on B557: lfllab: 08:22 sirco time
Note on B558: lfllab: 08:14 sirco time
Note on B559: lfllab: circo time
Note on B565: lfllab: sirco time
Note on B597: Lab Sl3 - LGL: Sirco time
Note on B598: Lab Sl3 - LGL: sirco time
Note on B700: Lab Sl3 - LGL: BST
Note on B721: Lab Sl3 - LGL: sirco
Note on B722: Lab Sl3 - LGL: sirco
Note on B723: Lab Sl3 - LGL: sirco
Note on B724: Lab Sl3 - LGL: sirco
Note on B725: lfllab: sirco
Note on B727: Lab Sl3 - LGL: sirco time
Note on B728: Lab Sl3 - LGL: sirco time
Note on B729: lfllab: sirco
Note on B730: lfllab: sirco
Note on B755: lfllab: sirco time
Note on B759: lfllab: Sirco time
Note on B761: lfllab: sirco time
Note on B762: lfllab: sirco time
Note on B763: Lab Sl3 - LGL: sirco time
Note on B764: lfllab: sirco time
Note on B765: Lab Sl3 - LGL: sirco time
Note on B766: Lab Sl3 - LGL: sirco time
Note on B767: Lab Sl3 - LGL: sirco
Note on B768: lfllab: sirco time
Note on B769: lfllab: sirco
Note on B770: Lab Sl3 - LGL: sirco time
Note on B771: lfllab: sirco time
Note on B772: lfllab: sirco time
Note on B773: Lab Sl3 - LGL: Sirco time
Note on B774: lfllab: sirco time
Note on B775: lfllab: sirco
Note on B779: Lab Sl3 - LGL: sirco
Note on B780: lfllab: Sirco time
Note on B796: lfllab: sirco time
Note on B825: lfllab: collected 07:25 sirco time
Note on C358: LFLLAB: not reset from previous week reading was 331.
Note on C407: lfllab: was reset somepoint during Monday . Was expecting around 161
Note on C410: lfllab: counter reset on 07/07/10 displaying 89. A further 60 pulses recorded
Note on C430: lfllab: 275 on meter as not zeroised last week
Note on C468: lfllab: Manual samples taken for composite for 48 hr period whilst sampler position switched. Now on North side of effluent pit.
Note on C500: lfllab: counter 267 as not reset last week
Note on C577: lfllab: 272-127
Note on C956: Lab Sl3 - LGL: 91 sirco 35 bottles
Note on C957: Lab Sl3 - LGL: number of sirco samples recorded: 192 manual samples: 38
Note on C959: Lab Sl3 - LGL: Sirco 187 manual 6
Note on C1081: Lab Sl3 - LGL: PLUS 7 MANUAL SAMPLES
Note on D107: APortess: Flow totaliser reset @ 05:38 on 17/11/04 at 499, 997 m3.
Note on D135: SL3Lab: totaliser reset at 09:01 on 27.05.05 at 495253m3
Note on D168: SL3Lab: Reset at 499997
Note on D369: LFLLAB: actual reading on display 700. Display resets its self after 500,000
Note on D936: Lab Sl3 - LGL: counter reset at 500000 ,unable to reset here HF
Note on D938: Lab Sl3 - flow calculation rest.
Note on E32: APortess: Totaliser rest at 499998 m^3.
Note on E55: SL3Lab: Totaliser reset at 499997
Note on E179: ASellars: Corrected for rounding errors in the effluent flow integrator. See comments for we/19/05/06
Note on E180: ASellars: Corrected for rounding errors in the effluent flow integrator. See comments for we/19/05/06
Note on E181: ASellars: Corrected for rounding errors in the effluent flow integrator. See comments for we/19/05/06
Note on E182: ASellars: Corrected for rounding errors in the effluent flow integrator. See comments for we/19/05/06
Note on E183: ASellars: Corrected for rounding errors in the effluent flow integrator. See comments for we/19/05/06
Note on E184: ASellars: Corrected for rounding errors in the effluent flow integrator. See comments for we/19/05/06
Note on E185: ASellars: There were problems with the effluent flow integrator on SCADA. The real flow for this week was 37.2% higher. This can be seen by either taking the average hourly flow for the week and muliplying by 24 x 7 or from the number of effluent samples taken. Both of these are logged on Historical trends. The cause of the problem was found to be due to rounding errors in the plc which was corrected on 23/05/06. All results for the period 01/04/06 to 26/05/06 have been affected and have been corrected using the information detailed above.
Note on E186: ASellars: Corrected for rounding errors in the effluent flow integrator. See comments for we/19/05/06
Note on E201: SL3Lab: corrected to account for resetting after 500,000
Note on E458: lfllab: Shutdown week
Note on E474: lflsll: Effluent flow meter resets automatically at 500,000 m3.
Note on E546: lfllab: Flow meter automatically resets at 500000m3
Note on E584: lfllab: Flow meter automatically resets at 500000m3
Note on E874: Lab Sl3 - LGL: flow reset @ 499990 499990-491760=8230 8230+3920=12150
Note on E949: Lab Sl3 - LGL: Actual figure recorded - sequences are now reset to 7 day flows.
Note on E969: Lab Sl3 - LGL flow reset. 499,999-496,300= 3699 10550+3699= 14249
Note on G58: SL3Lab:REPEAT TSS previously above limit at 50.8 mg/l
Note on G74: SL3Lab: Repeat result still giving an out of spec result of 65
Note on G98: SL3Lab: result was still the same, above limit, when we dried the paper again to make sure it was completely dry
Note on G130: SL3Lab: 58.4 & 52.8 Average = 55.6
Note on G131: SL3Lab: Average of 54.4 & 66.4
Note on G134: SL3Lab: 52.0 & 60.8 Average = 56.4
Note on G137: SL3Lab: 53.2 & 58.8 Average = 56.0 mg/l
Note on G139: SL3Lab: 51.6 & 32.8 Average = 42.2 mg/l
Note on G142: av of 98.4 and 50.8
Note on G188: SL3Lab: This is a result of a retest,
Note on G197: ASellars: High TSS due to site shutdown. Low flows and cleaning operations.
Note on G241: LFLLAB: Retested using 100ml instead of 250 ml result = 54mg/l
Note on G244: LFLLAB: retested using 100ml instead of 250ml result = 82mg/l
Note on G253: LFLLAB: repeated with a repeat result of 61
Note on G254: Alan Sellars: Effluent sampler bleached on 10/09/07
Note on G301: LFLLAB: Retested at 123 mg/l on a 100 ml sample.
Note on G319: LFLLAB: retest result 120.8
Note on G366: LFLLAB: Effluent sampler cistern found to be badly affected by bacterial growth. Monthly cleaniung schedule had not been carried out due to absence. Ref email from A Sellars to S Gorringe.
Note on G369: LFLLAB: Retested using 100ml result was 132 mg/l Investigation into high result instigated. Initial findings: Flow through sampler pipework too low, this will affect the sample with regard to TSS, due to solids being settled and disturbed within the extended pipe work installed due to the requirements of MCERTs, the intial cause appears to be the 1" valve on the return line to the effluent pit, being blocked. Flow control valve to the effluent sampler adjusted, as an intermediate measure to improve flow through the system and WO entered for faulty valve. Result to be reviewed on 04/12/09. SG
Note on G370: LFLLAB: result from 100 ml sample. Effluent return line from TOD hut found to be blocked, affecting sample quality (wrt TSS). Drain line cleared 04/12/09 @10:00 and effluent sample line flushed clear of aggregated solids. Sampler flows reset.
Note on G371: LFLLAB: on 100 ml sample, slow filtering
Note on G410: lfllab: retested 100ml = 106mg/l retested 250ml = 123.2mg/l SG - See emails PP/AS
Note on G422: lfllab: retested using 100ml result was 140mg/l
Note on G446: lfllab: retest 80.4mg/l
Note on G457: Stuart Gorringe: Effluent sampler cistern found to be badly affected by bacterial growth. Monthly cleaniung schedule had not been carried out due to absence. Recalibrated at 85.7 based on a 3 week average
Note on G499: lfllab: initial result 175.2
Note on G514: lfllab: repeat 113.6 mg/l lflgos: Recalculated at 79.4based on a 3 week average Having looked at the filter papers used for the effluent analysis in the laboratory, and discussed with relevant people, the effluent composite sample analysed on 7th September contained additional contamination from the Sirco sampler. Hence the TSS analysis on this sample will have given an erroneously high result. The system has been a thorough clean and the pipe work disinfected. We expect that this week's composite will be back to normal.
Note on G646: lfllab: initial ersult 45.2
Note on G716: Lab Sl3 - LGL: original 124.0 on 250 ml sample
Note on G760: Lab Sl3 - LGL: Rpt 106
Note on G761: lfllab: rpt 122.0 on x10 dilution
Note on G840: Lab Sl3 - LGL: average of original 104.0 and repeat 102.0 mg/l
Note on G1029: Lab Sl3 - LGL: repeat 121.2
Note on G1069: Lab Sl3 - LGL: repeated sample result 128
Note on G1129: Lab Sl3 - LGL: Done with 100ml
Note on G1137: Lab Sl3 - LGL: retest 92.8
Note on H556: lfllab: awaiting replacement machine
Note on H616: Lab Sl3 - LGL: repeats 3833.4, 4035.2 x2 dilution filtered
Note on H617: Lab Sl3 - LGL: filtered x2 dilution
Note on H619: Lab Sl3 - LGL: Faullty PeCOD
Note on H631: Lab Sl3 - LGL: Initial result 2478.60 Repeat 2994.60
Note on H648: Drury Laura - LGL: PeCOD out of order
Note on H722: Lab Sl3 - LGL: requires cleaning
Note on I206: SL3Lab: Retest result used. Original result (2006) was clearly in error as, (a) did not correlate with AO losses, (b) did not correlate with on-line TOD measurements.
Note on I293: LFLLAB: mean of 2 results 1051 and 1122
Note on I357: LFLLAB: original result was 958 with a high standard (795),
Note on I362: LFLLAB: original 988 with low standard of 702
Note on I426: lfllab: x10 dilution gave result of 1480
Note on I427: lfllab: repeat 1449 standard still out of spec to be repeated mon/tue
Note on I460: lfllab: also carried out test with x5 dilution with a test result of 2428
Note on I467: lfllab: original result 1646 erratic, repeated with 5x dilution
Note on I474: lfllab: average of two results 1988.5 - 1915.6
Note on I498: lfllab: original result 1850
Note on I501: lfllab: initial result 2060 standard off spec repeated 12/6/12
Note on I515: lfllab: x5 dilution gives 2421 mg/l
Note on I576: lfllab: new standard required. Sample will be rerun. result expected to be lower
Note on I939: Lab Sl3 - LGL: duplicate test
Note on I1066: Lab Sl3 - LGL: Adjusted 7/6 to acount for Thursday testing due to easter bank holiday
Note on I1067: Lab Sl3 - LGL: Adjusted result by 7/8 to account for the extra day due to last sampling being the previous Thursday due to Easter weekend.
Note on I1089: Drury Laura: Tuesday effluent loading 1084
Note on J648: Letts Penny - LGL: Result corrected for 6 day week. Eflluent sample collected on Thursday due to Easter.
Note on J649: Letts Penny - LGL: Result corrected for 8 day week. Eflluent sample collected on Thursday due to Easter.
Note on J859: Lab Sl3 - LGL: 16018 adjusted by 7/6 due to Easter sampling 1 day early giving 18688
Note on J860: Lab Sl3 - LGL: 33890 adjusted by 7/8 due to Easter sampling 1 day early giving 29653
Note on J910: Lab Sl3 - LGL: Adjusted by 7/6 due to easter sampling one day early. Same as 18/04/19
Note on J911: Lab Sl3 - LGL: Adjusted result by 7/8 to account for the extra day due to last sampling being the previous Thursday due to Easter weekend.
Note on J914: Lab Sl3 - LGL: Figure adjusted to accound for sampling on Thursday rather than Friday due to a bank holiday.
Note on J915: Lab Sl3 - LGL: Adjusted by 7//8 to account for 8 days passing due to last sampling being the previous Thursday.
Note on J947: Lab Sl3 - LGL: Adjusted by 7/6 to account for sampling on a Thursday.
Note on J948: Lab Sl3 - LGL: Sample collected between Thursday 24/12 and Thursday 31/12
Note on J949: Lab Sl3 - LGL: Friday ( 8 days) reported as 7
Note on J961: Lab Sl3 - LGL: Adjusted by 7/6 to account for sampling on a Thursday.
Note on J962: Lab Sl3 - LGL: Adjusted result by 7/8 to account for the extra day due to last sampling being the previous Thursday due to Easter weekend.
Note on J1015: Lab Sl3 - LGL: Adjusted by 7/6 to account for sampling on a Thursday.
Note on J1016: Lab Sl3 - LGL: Adjusted result by 7/8 to account for the extra day due to last sampling being the previous Thursday due to Easter weekend.
Note on J1089: Drury Laura: Tuesday effluent loading result 15850 (extrapolated)
Note on J1117: Lab Sl3 - LGL: Adjusted by 7/6 to account for sampling on a Thursday.
Note on J1118: Lab Sl3 - LGL: *by 7/8 for 8day sample
Note on K218: ASellars: Measurement of Free Chlorine not required under PPC.Analysis ceased from Q1 2007.
Note on L213: Alan Sellars: Phosphate results carried out by Alan Sellars prior to acceptance of method.
Note on L214: Alan Sellars: Phosphate results carried out by Alan Sellars prior to acceptance of method.
Note on L224: LFLLAB: Initial result of 32.07 was obtained from incorrect Abs setting on the UV Vis.
Note on L271: lfllab: repeat of original reading of 46.53
Note on L275: lfllab: repeat of original reading of 30.6
Note on L280: lfllab: average of two test readings: 84.3 and 82.5
Note on L283: lfllab: average of results 79.44 and 91.6
Note on L337: LFLLAB: retest result = 106mg/l High conc due to 70% production being A100.
Note on L340: LFLLAB: high A100 production
Note on L341: LFLLAB: high A100
Note on L342: LFLLAB: average of 38.39 and 39.16
Note on L347: LFLLAB: high a100 production
Note on L348: LFLLAB: high a100 production
Note on L432: lfllab: repeat confirmed result
Note on L446: lfllab: retested result reported original result 175.01
Note on L467: lfllab: repeat confirms result
Note on L470: lfllab: initial result 183.9
Note on L474: lfllab: This result is an average of 166, 162.8
Note on L476: lfllab: average of two analysis 162.1 - 160.3
Note on L477: lfllab: average of two analysis 176.9 - 174.0
Note on L481: lfllab: average of two analysis 133.6 & 144.9
Note on L486: lfllab: average of two analysis 130.8 & 133.7
Note on L501: lfllab: Phosphate repeated 12/6/12, standard in spec, result 133.1
Note on L510: lfllab: average of 170.5 and 160.7
Note on L511: lfllab: retesting std due to high result
Note on L518: lfllab: averge of two tests 1st = 142.7 2nd = 142.6
Note on L565: lfllab: repeat 59.61
Note on L580: lfllab: average of 21.83 and 21.36
Note on L644: Lab Sl3 - LGL: Repeat 150.9
Note on L649: Lab Sl3 - LGL: repeat = 184.7
Note on L658: Lab Sl3 - LGL: repeat = 162.3
Note on L665: Lab Sl3 - LGL: av of 140.8, 141.8
Note on L676: Lab Sl3 - LGL: Average of 144.5 / 146.7
Note on L677: lfllab: average of 137.8, 156.2
Note on L681: Lab Sl3 - LGL: average of 148.5, 145.6
Note on L688: Lab Sl3 - LGL: average of 140 retest and original 157.2
Note on L706: Lab Sl3 - LGL: average of 140.4, 140.7
Note on L711: lfllab: average of 147, 148.4
Note on L712: Lab Sl3 - LGL: average of 156.7, 155.9
Note on L718: Lab Sl3 - LGL: Ave of 27.61/22.9
Note on L726: Lab Sl3 - LGL: Ave of 163.1/166.3
Note on L734: lfllab: average of 157.1, 160.3
Note on L751: lfllab: average of 168.1 and 167.5
Note on L825: lfllab: repeat 141.2 hg
Note on M300: LFLLAB: original result 313 01/08/08
Note on M368: LFLLAB: result reported from x 2 dilution
Note on M489: lfllab: Result from 21/03/12 due to HPLC maintenance
Note on N300: LFLLAB: original result 197 01/08/08
Note on O300: LFLLAB: original result 60 01/08/08
Note on O591: Lab Sl3 - LGL: worst case
Note on O904: Lab Sl3 - LGL: new column for separation showing difference in chromatography to previous analysis.
Note on P300: LFLLAB: original result 01/08/08 572
Note on P426: lfllab: X10 dilution reported undiluted 494
Note on P427: lfllab: X10 dilution reported undiluted 449 (35 M, 263 NMMO, 151 MM)
Note on P428: lfllab: HPLC currently out of order
Note on P431: lfllab: x2 dilution used
Note on P515: lfllab: x2 dilution 1236 X5 dilution 1301
Note on P519: lfllab: result from undiluted sample
Note on P1089: Drury Laura: Tuesday effluent loading result 244
Note on Q300: LFLLAB: 04/08/08 repeat of sl3 eff for 01/08/08
Note on Q345: Alan Sellars: High reading due to both streams running at full rate and Ao carry over from the evaporator on 09/06/09.
Note on Q498: lfllab: results reported from x2 dilution, confirmed original result
Note on Q515: Penny Letts: Test result 21/09/12: 15369 when HPLC had new column and recalibration
Note on Q648: Letts Penny - LGL: Result corrected for 6 day week. Eflluent sample collect on Thursday due to Easter
Note on Q649: Letts Penny - LGL: Result corrected for 8 day week. Eflluent sample collect on Thursday due to Easter
Note on Q728: lfllab: amines reported on x2 dilution
Note on Q859: Lab Sl3 - LGL: Adjusted for 6 days due to Easter .Figure multiplied by 7/6.
Note on Q860: Lab Sl3 - LGL: Adjusted for 8 days due to Easter .Figure multiplied by 7/8.
Note on Q910: Lab Sl3 - LGL: Adjusted by 7/6 due to easter sampling one day early. Same as on 18/04/19.
Note on Q911: Lab Sl3 - LGL: Result adjusted by 7/8 due to the additional day since last tested the previous Thurday due to Easter weekend.
Note on Q914: Lab Sl3 - LGL: Figure adjusted to account for sampling on Thursday rather than Friday due to a bank holiday.
Note on Q915: Lab Sl3 - LGL: Adjusted by 7//8 to account for 8 days passing due to last sampling being the previous Thursday.
Note on Q947: Lab Sl3 - LGL: Adjusted by 7/6 to account for sampling on a Thursday.
Note on Q948: Lab Sl3 - LGL: Sample collected between Thursday 24/12 and Thursday 31/12
Note on Q961: Lab Sl3 - LGL: Adjusted by 7/6 to account for sampling on a Thursday.
Note on Q962: Lab Sl3 - LGL: Adjusted result by 7/8 to account for the extra day due to last sampling being the previous Thursday due to Easter weekend.
Note on Q1015: Lab Sl3 - LGL: Adjusted by 7/6 to account for sampling on a Thursday.
Note on Q1016: Lab Sl3 - LGL: Adjusted result by 7/8 to account for the extra day due to last sampling being the previous Thursday due to Easter weekend.
Note on Q1066: Lab Sl3 - LGL: Adjusted 7/6 to acount for Thursday testing due to easter bank holiday
Note on Q1067: Lab Sl3 - LGL: Adjusted result by 7/8 to account for the extra day due to last sampling being the previous Thursday due to Easter weekend.
Note on Q1089: Drury Laura: Tuesday effluent loading result 4550 (extrapolated)
Note on Q1117: Lab Sl3 - LGL: Adjusted by 7/6 to account for sampling on a Thursday.
Note on Q1118: Lab Sl3 - LGL: *7/8 for 8 day sampling
Note on T682: Lab Sl3 - LGL: original 5.79
Note on T684: Lab Sl3 - LGL: initial 2.73
Note on T694: Lab Sl3 - LGL: Result from 22/02/16 as not available on the 19/02/16.
Note on T696: lfllab: no sample received
Note on T702: Lab Sl3 - LGL: Initial 2.19
Note on T707: Lab Sl3 - LGL: 19/05/16 2.56 NMM 20/05/16 0 NMM
Note on T723: Lab Sl3 - LGL: sample 9/9/16 13:10
Note on T750: Lab Sl3 - LGL: RO unit not running
Note on T757: lfllab: RO unit not running
Note on T762: lfllab: RO unit not running
Note on T764: Lab Sl3 - LGL: RO unit not running
Note on T766: Lab Sl3 - LGL: RO unit not running
Note on T767: lfllab: RO unit not running
Note on T794: Lab Sl3 - LGL: repeated
Note on T908: Lab Sl3 - LGL: not sampled, tanks cordened off
Note on T978: Lab Sl3 - LGL: unaable to sample
Note on T985: Lab Sl3 - LGL: Unable to sample. Gauge attached to tap.
Note on T986: Lab Sl3 - LGL: Unable to sample. Gauge attached to tap.
Note on T987: Lab Sl3 - LGL: Unable to sample. Gauge attached to tap.
Note on T988: Lab Sl3 - LGL: Unable to sample. Gauge attached to tap.
Note on T989: Lab Sl3 - LGL: Unable to sample. Gauge attached to tap.
Note on T990: Lab Sl3 - LGL: Unable to sample. Gauge attached to tap.
Note on T991: Lab Sl3 - LGL: Unable to sample. Gauge attached to tap.
Note on T992: Lab Sl3 - LGL: Unable to sample. Gauge attached to tap.
Note on T993: Lab Sl3 - LGL: Unable to sample. Gauge attached to tap.
Note on T994: Lab Sl3 - LGL: Unable to sample. Gauge attached to tap.
Note on T995: Lab Sl3 - LGL: Unable to sample. Gauge attached to tap.
Note on T996: Lab Sl3 - LGL: Unable to sample. Gauge attached to tap.
Note on T997: Lab Sl3 - LGL: Unable to sample. Gauge attached to tap.
Note on T998: Lab Sl3 - LGL: Unable to sample. Gauge attached to tap.
Note on T999: Lab Sl3 - LGL: Unable to sample. Gauge attached to tap.
Note on T1000: Lab Sl3 - LGL: Unable to sample. Gauge attached to tap.
Note on T1001: Lab Sl3 - LGL: Unable to sample. Gauge attached to tap.
Note on T1002: Lab Sl3 - LGL: Unable to sample. Gauge attached to tap.
Note on T1045: Lab Sl3 - LGL: resampled 136.37
Note on T1046: Lab Sl3 - LGL:
Note on T1047: Lab Sl3 - LGL:
Note on T1048: Lab Sl3 - LGL: Unable to sample.
Note on T1050: Lab Sl3 - LGL: unable to sample
Note on T1074: Lab Sl3 - LGL: re sampled result: 137.35
Note on T1080: Lab Sl3 - LGL: RO offline
Note on T1081: Lab Sl3 - LGL: RO offline LS
Note on T1082: Lab Sl3 - LGL: unable to sample
Note on T1083: Lab Sl3 - LGL: unable to sample
Note on T1084: Lab Sl3 - LGL: unable to sample
Note on T1085: Lab Sl3 - LGL: unable to sample