## Model Element Summary
Project ¦ Properties
Topic: | Noise
Type of prediction: | Noise (national methods)
Rating following:: | No rating | No. | Period | Duration/h
|  | 1 | AnyTime | 24
Project notes
Work area
| from ... | to ... | Dimensions | Area
x /m | 513930 | 517620 | 3690 | 16.13 km²
y /m | 417050 | 421420 | 4370
z /m | -10 | 90 | 100
Terrain height in the corners
xmin / ymax (z4) | 0 | xmax / ymax (z3) | 0
xmin / ymin (z1) | 0 | xmax / ymin (z2) | 0
Attribution of element groups to variants
Element group | Variant 0
Group 0 | +
Available calculation areas
Name | x min | x max | y min | y max | dx | dy | nx | ny | Reference | Height/m | Range
| /m | /m | /m | /m | /m | /m
Grid 0 | 513930 | 517620 | 417050 | 421420 | 20 | 20 | 185 | 219 | relative | 4 | Work area
Calculation parameters | KLCP CCGT Settings
Calculation model: General | Point calculation | Grid calculation
Adapt assessment area seamlessly to the receiver position
L /m
Terrain triangulation edges are obstacle | Yes | Yes
consider negative loop way at terraine triangular lines | Yes | Yes
Improved interpolation in boundary areas | Yes | Yes
Free field in front of refl. surfaces/m
acc. to sources | 1 | 1
acc. to immission points | 1 | 1
House: white border in grid | No | No
Intermediate messages: | No | No
Calculation model: Parameters | Optimised | Optimised
Limiting range of sound sources:
* Limit the search radius (distance source-IP): | No | No
* minimum level difference /dB: | No | No
Projection of line sound sources | Yes | Yes
Projection of area sound sources | Yes | Yes
Limit projection | No | No
* Radius /m around source:
* Radius /m around IP:
Minimum length for sections /m | 1 | 1
Variable min. length for sections:
* in percent of the distance from the IP source | No | No
Add. factor for distance criterion | 1 | 1
Barrier attenuation differing from guideline: | No | No
* Cut-off limit for insertion loss:
* Limit /dB for single screens:
* Limit /dB for multiple screens:
Calculate attenuation for VDI 2720, ISO9613
* Lateral pathway | Yes | Yes
* Lateral pathway for image sources | No | No
Reflection
Reflection (max. order) | 1 | 1
Limit the search radius (distance source-IP): | No | No
* Search radius /m
Limiting range of reflecting surfaces /m:
* Radius around source or IP /m: | No | No
* minimum level difference /dB: | No | No
Image source from projection | Yes | Yes
No refl. if entirely screened | Yes | Yes
Save rays as help lines | No | No
section control
Section control acc. Schall 03 [2012]: | Yes | Yes
Section control for other calculation methods, too: | No | No
Accelerated iteration (approximation): | No | No
Requested accuracy /dB: | 0.1 | 0.1
Show intermediate results: | No | No
Global parameters | KLCP CCGT Settings
Default for G outside DBOD-elements | 1
Temperature /°C | 10
Relative humidity /% | 70
Living area per inhab-/m² (=0.8*gross) | 40
Average storey height /m | 2.8
Simplified meteorology (Guideline Int. Comp. Methods): | Day | Evening | Night
Simplified meteorology (Guideline Int. Comp. Methods): | 2 | 1 | 0
Parameters of library: ISO 9613-2 | KLCP CCGT Settings
Downwind conditions | Yes
Simplified equation (Nr. 7.3.2) for ground effect
for frequency-dependent calculation | No
for frequency-independent calculation | Yes
Evaluating the mean height hm | according to ISO 9613-2 (2024)
Simplified calculation using free propagation conditions (release 7/2002)(obsolete) | No
Attenuation due to screening - subtract negative ground effect | No
Deduction no more than to -Dz | No
"Additional recommendations" - ISO TR 17534-3 | Yes
ABar acc. "Erlass Thüringen" (2015-01-10) | No
Accounts for vegetation | Yes
Accounts for housing | Yes
Accounts for ground effect | Yes
Emission variant
T1 | AnyTime
Receiver point (9) |  |  |  | Variant 0
Element | Name | Group | Display |  | Number of nodes | Length/ m | Area /m²
IPkt001 | 1: Marsh Lane | Group 0 | IPkt |  | 1 | --- | ---
IPkt002 | 2: Skitter Road | Group 0 | IPkt |  | 1 | --- | ---
IPkt003 | 3: Station Road | Group 0 | IPkt |  | 1 | --- | ---
IPkt004 | 4: Kettlebridge Lane | Group 0 | IPkt |  | 1 | --- | ---
IPkt005 | 5: Swinster Lane | Group 0 | IPkt |  | 1 | --- | ---
IPkt006 | 6: Scrub Lane | Group 0 | IPkt |  | 1 | --- | ---
IPkt007 | 7: Brick Lane | Group 0 | IPkt |  | 1 | --- | ---
IPkt008 | 10: Old Vicarage | Group 0 | IPkt |  | 1 | --- | ---
IPkt009 | ARUP Haven Pits ECO | Group 0 | IPkt |  | 1 | --- | ---
Building (48) |  |  |  | Variant 0
Element | Name | Group | Display |  | Number of nodes | Length/ m | Area /m²
HAUS001 | HLIN /WÄNDE | Group 0 | HAUS |  | 5 | 59.32 | 211.08
HAUS002 | HLIN /WÄNDE | Group 0 | HAUS |  | 5 | 110.07 | 730.97
HAUS003 | HLIN /WÄNDE | Group 0 | HAUS |  | 5 | 81.34 | 330.29
HAUS004 | HLIN /WÄNDE | Group 0 | HAUS |  | 5 | 136.92 | 1081.79
HAUS005 | HLIN /WÄNDE | Group 0 | HAUS |  | 5 | 257.51 | 3344.16
HAUS006 | HLIN /WÄNDE | Group 0 | HAUS |  | 7 | 93.67 | 460.96
HAUS007 | HLIN /WÄNDE | Group 0 | HAUS |  | 5 | 231.25 | 1813.76
HAUS008 | HLIN /WÄNDE | Group 0 | HAUS |  | 5 | 274.41 | 1637.37
HAUS009 | HLIN /WÄNDE | Group 0 | HAUS |  | 5 | 105.76 | 583.09
HAUS010 | HLIN /WÄNDE | Group 0 | HAUS |  | 5 | 55.32 | 190.67
HAUS011 | Extra Building | Group 0 | HAUS |  | 5 | 205.93 | 1084.12
HAUS012 | HLIN /WÄNDE* | Group 0 | HAUS |  | 5 | 231.25 | 1813.76
HAUS013 | Haus | Group 0 | HAUS |  | 9 | 209.29 | 1882.41
HAUS014 | Haus | Group 0 | HAUS |  | 7 | 118.84 | 568.29
HAUS015 | SyncComp Building Footprint | Group 0 | HAUS |  | 5 | 275.21 | 3275.16
HAUS016 | GT11 Duct | Group 0 | HAUS |  | 5 | 50.03 | 95.47
HAUS017 | GT12 Duct | Group 0 | HAUS |  | 5 | 50.03 | 95.47
HAUS018 | GT21 Duct | Group 0 | HAUS |  | 5 | 50.03 | 95.47
HAUS019 | GT22 Duct | Group 0 | HAUS |  | 5 | 50.03 | 95.47
HAUS020 | Xformer/Barriers | Group 0 | HAUS |  | 5 | 43.5 | 118.19
HAUS021 | Xformer 3 | Group 0 | HAUS |  | 5 | 43.5 | 118.19
HAUS022 | Xformer 4 | Group 0 | HAUS |  | 5 | 43.5 | 118.19
HAUS023 | Xformer 1 | Group 0 | HAUS |  | 5 | 43.5 | 118.19
HAUS024 | Hornsea1 | Group 0 | HAUS |  | 5 | 129.95 | 1049.67
HAUS025 | Hornsea2 | Group 0 | HAUS |  | 5 | 249.76 | 2120.22
HAUS026 | Hornsea3 | Group 0 | HAUS |  | 5 | 80.94 | 406.33
HAUS027 | Hornsea4 | Group 0 | HAUS |  | 5 | 80.91 | 406.04
HAUS028 | Hornsea5 | Group 0 | HAUS |  | 5 | 80.92 | 406.14
HAUS029 | Hornsea6 | Group 0 | HAUS |  | 5 | 195.79 | 1331.5
HAUS030 | UBA: PCC11/Barriers | Group 0 | HAUS |  | 5 | 32.98 | 56.4
HAUS031 | ULA: Feedwater Pump Station/Barriers | Group 0 | HAUS |  | 6 | 89.52 | 496.07
HAUS032 | UGC: Demin Tank/Barriers | Group 0 | HAUS |  | 12 | 37.58 | 109.32
HAUS033 | UHA: HRSG (02)/Barriers | Group 0 | HAUS |  | 5 | 30.87 | 59.06
HAUS034 | UBA: PCC7/Barriers | Group 0 | HAUS |  | 5 | 63.11 | 236.76
HAUS035 | UHA: HRSG/Barriers | Group 0 | HAUS |  | 5 | 129.65 | 1024.62
HAUS036 | UMX: Diffuser Duct/Barriers | Group 0 | HAUS |  | 5 | 48.46 | 138.44
HAUS037 | UMC: GT&ST Building/Barriers | Group 0 | HAUS |  | 5 | 201.77 | 2393.29
HAUS038 | URA: Hybrid Cooling Tower/Barriers | Group 0 | HAUS |  | 5 | 225.66 | 2589.09
HAUS039 | UGD: WT Plant Container/Barriers | Group 0 | HAUS |  | 5 | 109.41 | 553.66
HAUS040 | UGE: Neutralization Tank/Barriers | Group 0 | HAUS |  | 5 | 30.28 | 57.29
HAUS041 | UYE: Gatehouse/Barriers | Group 0 | HAUS |  | 5 | 33.03 | 67.68
HAUS042 | UGJ: CW Pumps ( & ULX)/Barriers | Group 0 | HAUS |  | 5 | 123.07 | 928.63
HAUS043 | UCA: Control & Admin Building/Barriers | Group 0 | HAUS |  | 5 | 102.44 | 494.1
HAUS044 | UST: Workshop & Storage/Barriers | Group 0 | HAUS |  | 5 | 135.22 | 913
HAUS045 | UHN: Stack/Barriers | Group 0 | HAUS |  | 13 | 24.44 | 46.46
HAUS046 | UBA: PCC8/Barriers | Group 0 | HAUS |  | 5 | 34.22 | 60.55
HAUS047 | UMC: GT&ST Building Lower/Barriers | Group 0 | HAUS |  | 5 | 231.17 | 3315.54
HAUS048 | UGA: Tank/Barriers | Group 0 | HAUS |  | 12 | 37.7 | 109.98
Ground effect (12) |  |  |  | Variant 0
Element | Name | Group | Display |  | Number of nodes | Length/ m | Area /m²
DBod001 | Site Perimeter | Group 0 | DBod |  | 16 | 1981.52 | 142523.84
DBod002 | HLIN | Group 0 | DBod |  | 12 | 1148.39 | 69469.92
DBod003 | HLIN | Group 0 | DBod |  | 5 | 290.58 | 3770.66
DBod004 | HLIN | Group 0 | DBod |  | 5 | 133.94 | 1118.73
DBod005 | HLIN | Group 0 | DBod |  | 5 | 383.89 | 8472.83
DBod006 | HLIN | Group 0 | DBod |  | 10 | 858.87 | 43415.57
DBod007 | HLIN | Group 0 | DBod |  | 10 | 1698.58 | 163320.23
DBod008 | HLIN | Group 0 | DBod |  | 5 | 667.39 | 25248.15
DBod009 | HLIN | Group 0 | DBod |  | 5 | 304.62 | 5358.26
DBod010 | HLIN | Group 0 | DBod |  | 31 | 5041.9 | 1030292.3
DBod011 | HLIN | Group 0 | DBod |  | 21 | 5487.43 | 1822298.58
DBod012 | HLIN | Group 0 | DBod |  | 22 | 6016.02 | 1711433.82
Point source /ISO 96 (9) |  |  |  | Variant 0
Element | Name | Group | Display |  | Number of nodes | Length/ m | Area /m²
EZQi001 | UMY: Steam pipes | Group 0 | EZQi |  | 1 | --- | ---
EZQi002 | ULY: Pipe Bridge | Group 0 | EZQi |  | 1 | --- | ---
EZQi003 | UEN: Fuel PRS | Group 0 | EZQi |  | 1 | --- | ---
EZQi004 | UHX02: Sampling Container | Group 0 | EZQi |  | 1 | --- | ---
EZQi005 | UEN: Fuel Preheater&Metering | Group 0 | EZQi |  | 1 | --- | ---
EZQi006 | UBF: Generator Transformer | Group 0 | EZQi |  | 1 | --- | ---
EZQi007 | UBE: Aux Power Transformer | Group 0 | EZQi |  | 1 | --- | ---
EZQi008 | MBL: Filterhouse | Group 0 | EZQi |  | 1 | --- | ---
EZQi009 | URO: Cooling Tower Treatment Plant | Group 0 | EZQi |  | 1 | --- | ---
Area source/ISO 9613 (29) |  |  |  | Variant 0
Element | Name | Group | Display |  | Number of nodes | Length/ m | Area /m²
FLQi001 | UHA: HRSG/WAND1 | Group 0 | FLQi |  | 5 | 165.17 | 1691.31
FLQi002 | UHA: HRSG/WAND2 | Group 0 | FLQi |  | 5 | 145.34 | 1245.04
FLQi003 | UHA: HRSG/WAND3 | Group 0 | FLQi |  | 5 | 165.63 | 1701.61
FLQi004 | UHA: HRSG/WAND4 | Group 0 | FLQi |  | 5 | 144.76 | 1232.21
FLQi005 | UHA: HRSG/DACH | Group 0 | FLQi |  | 5 | 130.45 | 1037.63
FLQi006 | UMC: GT&ST Building/WAND1 | Group 0 | FLQi |  | 5 | 158.97 | 1041.6
FLQi007 | UMC: GT&ST Building/WAND2 | Group 0 | FLQi |  | 5 | 109.56 | 632.72
FLQi008 | UMC: GT&ST Building/WAND3 | Group 0 | FLQi |  | 5 | 158.97 | 1041.58
FLQi009 | UMC: GT&ST Building/WAND4 | Group 0 | FLQi |  | 5 | 110.03 | 636.63
FLQi010 | UMC: GT&ST Building/DACH | Group 0 | FLQi |  | 5 | 202.57 | 2413.5
FLQi011 | UMC: GT&ST Building Lower/WAND1 | Group 0 | FLQi |  | 5 | 155.97 | 947.19
FLQi012 | UMC: GT&ST Building Lower/WAND2 | Group 0 | FLQi |  | 5 | 136.38 | 799.75
FLQi013 | UMC: GT&ST Building Lower/WAND3 | Group 0 | FLQi |  | 5 | 156 | 947.4
FLQi014 | UMC: GT&ST Building Lower/WAND4 | Group 0 | FLQi |  | 5 | 135.99 | 796.84
FLQi015 | UBA: PCC11/DACH | Group 0 | FLQi |  | 5 | 33.78 | 59.74
FLQi016 | ULA: Feedwater Pump Station/DACH | Group 0 | FLQi |  | 6 | 90.32 | 505.06
FLQi017 | UBA: PCC7/DACH | Group 0 | FLQi |  | 5 | 63.91 | 243.11
FLQi018 | UMX: Diffuser Duct/WAND1 | Group 0 | FLQi |  | 5 | 34.62 | 74.48
FLQi019 | UMX: Diffuser Duct/WAND3 | Group 0 | FLQi |  | 5 | 35.11 | 76.43
FLQi020 | UMX: Diffuser Duct/DACH | Group 0 | FLQi |  | 5 | 49.26 | 143.33
FLQi021 | URA: Hybrid Cooling Tower/WAND2 | Group 0 | FLQi |  | 5 | 205.32 | 1744.93
FLQi022 | URA: Hybrid Cooling Tower/WAND4 | Group 0 | FLQi |  | 5 | 204.58 | 1737
FLQi023 | URA: Hybrid Cooling Tower/DACH | Group 0 | FLQi |  | 5 | 226.46 | 2611.7
FLQi024 | UGD: WT Plant Container/DACH | Group 0 | FLQi |  | 5 | 110.21 | 564.64
FLQi025 | UGJ: CW Pumps ( & ULX)/DACH | Group 0 | FLQi |  | 5 | 123.87 | 940.98
FLQi026 | UCA: Control & Admin Building/DACH | Group 0 | FLQi |  | 5 | 103.24 | 504.38
FLQi027 | UST: Workshop & Storage/DACH | Group 0 | FLQi |  | 5 | 136.02 | 926.56
FLQi028 | UHN: Stack/DACH | Group 0 | FLQi |  | 13 | 25.09 | 48.93
FLQi029 | UBA: PCC8/DACH | Group 0 | FLQi |  | 5 | 35.02 | 64.01

## Sound Emission Sources
Emission variant
T1 | AnyTime
Point source /ISO 96 (9) | [6 empty] | Variant 0
EZQi001 | Label |  | UMY: Steam pipes |  |  |  |  | Action radius/m |  |  |  | 99999
| Group |  | Group 0 |  |  |  |  | Lw (AnyTime) /dB(A) |  |  |  | 81.74
| Number of nodes |  | 1 |  |  |  |  | D0 |  |  |  | 0
| Length/ m |  | --- |  |  |  |  | High building/high noise source |  |  |  | No
| Length/ m (2D) |  | --- |  |  |  |  | Emission is |  |  |  | Sound power level (Lw)
| Area /m² |  | ---
| Emiss. variant |  | Sum | 16 Hz | 31.5 Hz | 63 Hz |  | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | 8000 Hz
| AnyTime | Lw /dB | 107.6 | - | 106.4 | 101.2 |  | 87.1 | 83.6 | 77.2 | 74 | 69.8 | 66 | 59.1
EZQi002 | Label |  | ULY: Pipe Bridge |  |  |  |  | Action radius/m |  |  |  | 99999
| Group |  | Group 0 |  |  |  |  | Lw (AnyTime) /dB(A) |  |  |  | 81.74
| Number of nodes |  | 1 |  |  |  |  | D0 |  |  |  | 0
| Length/ m |  | --- |  |  |  |  | High building/high noise source |  |  |  | No
| Length/ m (2D) |  | --- |  |  |  |  | Emission is |  |  |  | Sound power level (Lw)
| Area /m² |  | ---
| Emiss. variant |  | Sum | 16 Hz | 31.5 Hz | 63 Hz |  | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | 8000 Hz
| AnyTime | Lw /dB | 107.6 | - | 106.4 | 101.2 |  | 87.1 | 83.6 | 77.2 | 74 | 69.8 | 66 | 59.1
EZQi003 | Label |  | UEN: Fuel PRS |  |  |  |  | Action radius/m |  |  |  | 99999
| Group |  | Group 0 |  |  |  |  | Lw (AnyTime) /dB(A) |  |  |  | 97.48
| Number of nodes |  | 1 |  |  |  |  | D0 |  |  |  | 0
| Length/ m |  | --- |  |  |  |  | High building/high noise source |  |  |  | No
| Length/ m (2D) |  | --- |  |  |  |  | Emission is |  |  |  | Sound power level (Lw)
| Area /m² |  | ---
| Emiss. variant |  | Sum | 16 Hz | 31.5 Hz | 63 Hz |  | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | 8000 Hz
| AnyTime | Lw /dB | 110.3 | - | 106.4 | 105.2 |  | 101.1 | 100.6 | 95.2 | 91 | 84.8 | 84 | 78.1
EZQi004 | Label |  | UHX02: Sampling Container |  |  |  |  | Action radius/m |  |  |  | 99999
| Group |  | Group 0 |  |  |  |  | Lw (AnyTime) /dB(A) |  |  |  | 87.93
| Number of nodes |  | 1 |  |  |  |  | D0 |  |  |  | 0
| Length/ m |  | --- |  |  |  |  | High building/high noise source |  |  |  | No
| Length/ m (2D) |  | --- |  |  |  |  | Emission is |  |  |  | Sound power level (Lw)
| Area /m² |  | ---
| Emiss. variant |  | Sum | 16 Hz | 31.5 Hz | 63 Hz |  | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | 8000 Hz
| AnyTime | Lw /dB | 93.9 | - | 81.4 | 84.2 |  | 90.1 | 85.6 | 85.2 | 84 | 77.8 | 75 | 73.1
EZQi005 | Label |  | UEN: Fuel Preheater&Metering |  |  |  |  | Action radius/m |  |  |  | 99999
| Group |  | Group 0 |  |  |  |  | Lw (AnyTime) /dB(A) |  |  |  | 83.15
| Number of nodes |  | 1 |  |  |  |  | D0 |  |  |  | 0
| Length/ m |  | --- |  |  |  |  | High building/high noise source |  |  |  | No
| Length/ m (2D) |  | --- |  |  |  |  | Emission is |  |  |  | Sound power level (Lw)
| Area /m² |  | ---
| Emiss. variant |  | Sum | 16 Hz | 31.5 Hz | 63 Hz |  | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | 8000 Hz
| AnyTime | Lw /dB | 93.1 | - | 83.4 | 86.2 |  | 90.1 | 83.6 | 77.2 | 74 | 73.8 | 77 | 67.1
EZQi006 | Label |  | UBF: Generator Transformer |  |  |  |  | Action radius/m |  |  |  | 99999
| Group |  | Group 0 |  |  |  |  | Lw (AnyTime) /dB(A) |  |  |  | 98.91
| Number of nodes |  | 1 |  |  |  |  | D0 |  |  |  | 0
| Length/ m |  | --- |  |  |  |  | High building/high noise source |  |  |  | No
| Length/ m (2D) |  | --- |  |  |  |  | Emission is |  |  |  | Sound power level (Lw)
| Area /m² |  | ---
| Emiss. variant |  | Sum | 16 Hz | 31.5 Hz | 63 Hz |  | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | 8000 Hz
| AnyTime | Lw /dB | 116.4 | - | 104.4 | 114.2 |  | 111.1 | 100.6 | 96.2 | 84 | 78.8 | 75 | 72.1
EZQi007 | Label |  | UBE: Aux Power Transformer |  |  |  |  | Action radius/m |  |  |  | 99999
| Group |  | Group 0 |  |  |  |  | Lw (AnyTime) /dB(A) |  |  |  | 79.91
| Number of nodes |  | 1 |  |  |  |  | D0 |  |  |  | 0
| Length/ m |  | --- |  |  |  |  | High building/high noise source |  |  |  | No
| Length/ m (2D) |  | --- |  |  |  |  | Emission is |  |  |  | Sound power level (Lw)
| Area /m² |  | ---
| Emiss. variant |  | Sum | 16 Hz | 31.5 Hz | 63 Hz |  | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | 8000 Hz
| AnyTime | Lw /dB | 97.4 | - | 85.4 | 95.2 |  | 92.1 | 81.6 | 77.2 | 65 | 59.8 | 56 | 53.1
EZQi008 | Label |  | MBL: Filterhouse |  |  |  |  | Action radius/m |  |  |  | 99999
| Group |  | Group 0 |  |  |  |  | Lw (AnyTime) /dB(A) |  |  |  | 95.49
| Number of nodes |  | 1 |  |  |  |  | D0 |  |  |  | 0
| Length/ m |  | --- |  |  |  |  | High building/high noise source |  |  |  | No
| Length/ m (2D) |  | --- |  |  |  |  | Emission is |  |  |  | Sound power level (Lw)
| Area /m² |  | ---
| Emiss. variant |  | Sum | 16 Hz | 31.5 Hz | 63 Hz |  | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | 8000 Hz
| AnyTime | Lw /dB | 123 | - | 122.4 | 114.2 |  | 100.1 | 95.6 | 92.2 | 89 | 82.8 | 75 | 80.1
EZQi009 | Label |  | URO: Cooling Tower Treatment Plant |  |  |  |  | Action radius/m |  |  |  | 99999
| Group |  | Group 0 |  |  |  |  | Lw (AnyTime) /dB(A) |  |  |  | 85.52
| Number of nodes |  | 1 |  |  |  |  | D0 |  |  |  | 0
| Length/ m |  | --- |  |  |  |  | High building/high noise source |  |  |  | No
| Length/ m (2D) |  | --- |  |  |  |  | Emission is |  |  |  | Sound power level (Lw)
| Area /m² |  | ---
| Emiss. variant |  | Sum | 16 Hz | 31.5 Hz | 63 Hz |  | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | 8000 Hz
| AnyTime | Lw /dB | 101.8 | - | 97.4 | 95.2 |  | 97.1 | 89.6 | 82.2 | 72 | 55.8 | 42 | 34.1
Area source/ISO 9613 (29) | [6 empty] | Variant 0
FLQi001 | Label |  | UHA: HRSG/WAND1 |  |  |  |  | Action radius/m |  |  |  | 99999
| Group |  | Group 0 |  |  |  |  | Lw (AnyTime) /dB(A) |  |  |  | 88.25
| Number of nodes |  | 5 |  |  |  |  | Lw" (AnyTime) /dB(A) |  |  |  | 55.97
| Length/ m |  | 165.17 |  |  |  |  | D0 |  |  |  | 0
| Length/ m (2D) |  | 75.17 |  |  |  |  | High building/high noise source |  |  |  | No
| Area /m² |  | 1691.31 |  |  |  |  | Emission is |  |  |  | SPL per unit area (Lw/m²)
| Emiss. variant |  | Sum | 16 Hz | 31.5 Hz | 63 Hz |  | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | 8000 Hz
| AnyTime | Lw" /dB | 66.5 | - | - | 63.8 |  | 61.7 | 54.2 | 48.8 | 46.6 | 47.4 | 50.6 | 43.7
FLQi002 | Label |  | UHA: HRSG/WAND2 |  |  |  |  | Action radius/m |  |  |  | 99999
| Group |  | Group 0 |  |  |  |  | Lw (AnyTime) /dB(A) |  |  |  | 86.92
| Number of nodes |  | 5 |  |  |  |  | Lw" (AnyTime) /dB(A) |  |  |  | 55.97
| Length/ m |  | 145.34 |  |  |  |  | D0 |  |  |  | 0
| Length/ m (2D) |  | 55.34 |  |  |  |  | High building/high noise source |  |  |  | No
| Area /m² |  | 1245.04 |  |  |  |  | Emission is |  |  |  | SPL per unit area (Lw/m²)
| Emiss. variant |  | Sum | 16 Hz | 31.5 Hz | 63 Hz |  | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | 8000 Hz
| AnyTime | Lw" /dB | 66.5 | - | - | 63.8 |  | 61.7 | 54.2 | 48.8 | 46.6 | 47.4 | 50.6 | 43.7
FLQi003 | Label |  | UHA: HRSG/WAND3 |  |  |  |  | Action radius/m |  |  |  | 99999
| Group |  | Group 0 |  |  |  |  | Lw (AnyTime) /dB(A) |  |  |  | 88.28
| Number of nodes |  | 5 |  |  |  |  | Lw" (AnyTime) /dB(A) |  |  |  | 55.97
| Length/ m |  | 165.63 |  |  |  |  | D0 |  |  |  | 0
| Length/ m (2D) |  | 75.63 |  |  |  |  | High building/high noise source |  |  |  | No
| Area /m² |  | 1701.61 |  |  |  |  | Emission is |  |  |  | SPL per unit area (Lw/m²)
| Emiss. variant |  | Sum | 16 Hz | 31.5 Hz | 63 Hz |  | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | 8000 Hz
| AnyTime | Lw" /dB | 66.5 | - | - | 63.8 |  | 61.7 | 54.2 | 48.8 | 46.6 | 47.4 | 50.6 | 43.7
FLQi004 | Label |  | UHA: HRSG/WAND4 |  |  |  |  | Action radius/m |  |  |  | 99999
| Group |  | Group 0 |  |  |  |  | Lw (AnyTime) /dB(A) |  |  |  | 86.88
| Number of nodes |  | 5 |  |  |  |  | Lw" (AnyTime) /dB(A) |  |  |  | 55.97
| Length/ m |  | 144.76 |  |  |  |  | D0 |  |  |  | 0
| Length/ m (2D) |  | 54.76 |  |  |  |  | High building/high noise source |  |  |  | No
| Area /m² |  | 1232.21 |  |  |  |  | Emission is |  |  |  | SPL per unit area (Lw/m²)
| Emiss. variant |  | Sum | 16 Hz | 31.5 Hz | 63 Hz |  | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | 8000 Hz
| AnyTime | Lw" /dB | 66.5 | - | - | 63.8 |  | 61.7 | 54.2 | 48.8 | 46.6 | 47.4 | 50.6 | 43.7
FLQi005 | Label |  | UHA: HRSG/DACH |  |  |  |  | Action radius/m |  |  |  | 99999
| Group |  | Group 0 |  |  |  |  | Lw (AnyTime) /dB(A) |  |  |  | 86.13
| Number of nodes |  | 5 |  |  |  |  | Lw" (AnyTime) /dB(A) |  |  |  | 55.97
| Length/ m |  | 130.45 |  |  |  |  | D0 |  |  |  | 0
| Length/ m (2D) |  | 130.45 |  |  |  |  | High building/high noise source |  |  |  | No
| Area /m² |  | 1037.63 |  |  |  |  | Emission is |  |  |  | SPL per unit area (Lw/m²)
| Emiss. variant |  | Sum | 16 Hz | 31.5 Hz | 63 Hz |  | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | 8000 Hz
| AnyTime | Lw" /dB | 66.5 | - | - | 63.8 |  | 61.7 | 54.2 | 48.8 | 46.6 | 47.4 | 50.6 | 43.7
FLQi006 | Label |  | UMC: GT&ST Building/WAND1 |  |  |  |  | Action radius/m |  |  |  | 99999
| Group |  | Group 0 |  |  |  |  | Lw (AnyTime) /dB(A) |  |  |  | 78.06
| Number of nodes |  | 5 |  |  |  |  | Lw" (AnyTime) /dB(A) |  |  |  | 47.88
| Length/ m |  | 158.97 |  |  |  |  | D0 |  |  |  | 0
| Length/ m (2D) |  | 125.87 |  |  |  |  | High building/high noise source |  |  |  | No
| Area /m² |  | 1041.6 |  |  |  |  | Emission is |  |  |  | SPL per unit area (Lw/m²)
| Emiss. variant |  | Sum | 16 Hz | 31.5 Hz | 63 Hz |  | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | 8000 Hz
| AnyTime | Lw" /dB | 75.6 | - | 74.7 | 67.5 |  | 58.4 | 46.9 | 41.5 | 34.3 | 35.1 | 36.3 | 33.4
FLQi007 | Label |  | UMC: GT&ST Building/WAND2 |  |  |  |  | Action radius/m |  |  |  | 99999
| Group |  | Group 0 |  |  |  |  | Lw (AnyTime) /dB(A) |  |  |  | 75.89
| Number of nodes |  | 5 |  |  |  |  | Lw" (AnyTime) /dB(A) |  |  |  | 47.88
| Length/ m |  | 109.56 |  |  |  |  | D0 |  |  |  | 0
| Length/ m (2D) |  | 76.46 |  |  |  |  | High building/high noise source |  |  |  | No
| Area /m² |  | 632.72 |  |  |  |  | Emission is |  |  |  | SPL per unit area (Lw/m²)
| Emiss. variant |  | Sum | 16 Hz | 31.5 Hz | 63 Hz |  | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | 8000 Hz
| AnyTime | Lw" /dB | 75.6 | - | 74.7 | 67.5 |  | 58.4 | 46.9 | 41.5 | 34.3 | 35.1 | 36.3 | 33.4
FLQi008 | Label |  | UMC: GT&ST Building/WAND3 |  |  |  |  | Action radius/m |  |  |  | 99999
| Group |  | Group 0 |  |  |  |  | Lw (AnyTime) /dB(A) |  |  |  | 78.06
| Number of nodes |  | 5 |  |  |  |  | Lw" (AnyTime) /dB(A) |  |  |  | 47.88
| Length/ m |  | 158.97 |  |  |  |  | D0 |  |  |  | 0
| Length/ m (2D) |  | 125.87 |  |  |  |  | High building/high noise source |  |  |  | No
| Area /m² |  | 1041.58 |  |  |  |  | Emission is |  |  |  | SPL per unit area (Lw/m²)
| Emiss. variant |  | Sum | 16 Hz | 31.5 Hz | 63 Hz |  | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | 8000 Hz
| AnyTime | Lw" /dB | 75.6 | - | 74.7 | 67.5 |  | 58.4 | 46.9 | 41.5 | 34.3 | 35.1 | 36.3 | 33.4
FLQi009 | Label |  | UMC: GT&ST Building/WAND4 |  |  |  |  | Action radius/m |  |  |  | 99999
| Group |  | Group 0 |  |  |  |  | Lw (AnyTime) /dB(A) |  |  |  | 75.92
| Number of nodes |  | 5 |  |  |  |  | Lw" (AnyTime) /dB(A) |  |  |  | 47.88
| Length/ m |  | 110.03 |  |  |  |  | D0 |  |  |  | 0
| Length/ m (2D) |  | 76.93 |  |  |  |  | High building/high noise source |  |  |  | No
| Area /m² |  | 636.63 |  |  |  |  | Emission is |  |  |  | SPL per unit area (Lw/m²)
| Emiss. variant |  | Sum | 16 Hz | 31.5 Hz | 63 Hz |  | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | 8000 Hz
| AnyTime | Lw" /dB | 75.6 | - | 74.7 | 67.5 |  | 58.4 | 46.9 | 41.5 | 34.3 | 35.1 | 36.3 | 33.4
FLQi010 | Label |  | UMC: GT&ST Building/DACH |  |  |  |  | Action radius/m |  |  |  | 99999
| Group |  | Group 0 |  |  |  |  | Lw (AnyTime) /dB(A) |  |  |  | 81.71
| Number of nodes |  | 5 |  |  |  |  | Lw" (AnyTime) /dB(A) |  |  |  | 47.88
| Length/ m |  | 202.57 |  |  |  |  | D0 |  |  |  | 0
| Length/ m (2D) |  | 202.57 |  |  |  |  | High building/high noise source |  |  |  | No
| Area /m² |  | 2413.5 |  |  |  |  | Emission is |  |  |  | SPL per unit area (Lw/m²)
| Emiss. variant |  | Sum | 16 Hz | 31.5 Hz | 63 Hz |  | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | 8000 Hz
| AnyTime | Lw" /dB | 75.6 | - | 74.7 | 67.5 |  | 58.4 | 46.9 | 41.5 | 34.3 | 35.1 | 36.3 | 33.4
FLQi011 | Label |  | UMC: GT&ST Building Lower/WAND1 |  |  |  |  | Action radius/m |  |  |  | 99999
| Group |  | Group 0 |  |  |  |  | Lw (AnyTime) /dB(A) |  |  |  | 77.65
| Number of nodes |  | 5 |  |  |  |  | Lw" (AnyTime) /dB(A) |  |  |  | 47.88
| Length/ m |  | 155.97 |  |  |  |  | D0 |  |  |  | 0
| Length/ m (2D) |  | 125.87 |  |  |  |  | High building/high noise source |  |  |  | No
| Area /m² |  | 947.19 |  |  |  |  | Emission is |  |  |  | SPL per unit area (Lw/m²)
| Emiss. variant |  | Sum | 16 Hz | 31.5 Hz | 63 Hz |  | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | 8000 Hz
| AnyTime | Lw" /dB | 75.6 | - | 74.7 | 67.5 |  | 58.4 | 46.9 | 41.5 | 34.3 | 35.1 | 36.3 | 33.4
FLQi012 | Label |  | UMC: GT&ST Building Lower/WAND2 |  |  |  |  | Action radius/m |  |  |  | 99999
| Group |  | Group 0 |  |  |  |  | Lw (AnyTime) /dB(A) |  |  |  | 76.91
| Number of nodes |  | 5 |  |  |  |  | Lw" (AnyTime) /dB(A) |  |  |  | 47.88
| Length/ m |  | 136.38 |  |  |  |  | D0 |  |  |  | 0
| Length/ m (2D) |  | 106.28 |  |  |  |  | High building/high noise source |  |  |  | No
| Area /m² |  | 799.75 |  |  |  |  | Emission is |  |  |  | SPL per unit area (Lw/m²)
| Emiss. variant |  | Sum | 16 Hz | 31.5 Hz | 63 Hz |  | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | 8000 Hz
| AnyTime | Lw" /dB | 75.6 | - | 74.7 | 67.5 |  | 58.4 | 46.9 | 41.5 | 34.3 | 35.1 | 36.3 | 33.4
FLQi013 | Label |  | UMC: GT&ST Building Lower/WAND3 |  |  |  |  | Action radius/m |  |  |  | 99999
| Group |  | Group 0 |  |  |  |  | Lw (AnyTime) /dB(A) |  |  |  | 77.65
| Number of nodes |  | 5 |  |  |  |  | Lw" (AnyTime) /dB(A) |  |  |  | 47.88
| Length/ m |  | 156 |  |  |  |  | D0 |  |  |  | 0
| Length/ m (2D) |  | 125.9 |  |  |  |  | High building/high noise source |  |  |  | No
| Area /m² |  | 947.4 |  |  |  |  | Emission is |  |  |  | SPL per unit area (Lw/m²)
| Emiss. variant |  | Sum | 16 Hz | 31.5 Hz | 63 Hz |  | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | 8000 Hz
| AnyTime | Lw" /dB | 75.6 | - | 74.7 | 67.5 |  | 58.4 | 46.9 | 41.5 | 34.3 | 35.1 | 36.3 | 33.4
FLQi014 | Label |  | UMC: GT&ST Building Lower/WAND4 |  |  |  |  | Action radius/m |  |  |  | 99999
| Group |  | Group 0 |  |  |  |  | Lw (AnyTime) /dB(A) |  |  |  | 76.9
| Number of nodes |  | 5 |  |  |  |  | Lw" (AnyTime) /dB(A) |  |  |  | 47.88
| Length/ m |  | 135.99 |  |  |  |  | D0 |  |  |  | 0
| Length/ m (2D) |  | 105.89 |  |  |  |  | High building/high noise source |  |  |  | No
| Area /m² |  | 796.84 |  |  |  |  | Emission is |  |  |  | SPL per unit area (Lw/m²)
| Emiss. variant |  | Sum | 16 Hz | 31.5 Hz | 63 Hz |  | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | 8000 Hz
| AnyTime | Lw" /dB | 75.6 | - | 74.7 | 67.5 |  | 58.4 | 46.9 | 41.5 | 34.3 | 35.1 | 36.3 | 33.4
FLQi015 | Label |  | UBA: PCC11/DACH |  |  |  |  | Action radius/m |  |  |  | 99999
| Group |  | Group 0 |  |  |  |  | Lw (AnyTime) /dB(A) |  |  |  | 87.97
| Number of nodes |  | 5 |  |  |  |  | Lw" (AnyTime) /dB(A) |  |  |  | 70.21
| Length/ m |  | 33.78 |  |  |  |  | D0 |  |  |  | 0
| Length/ m (2D) |  | 33.78 |  |  |  |  | High building/high noise source |  |  |  | No
| Area /m² |  | 59.74 |  |  |  |  | Emission is |  |  |  | SPL per unit area (Lw/m²)
| Emiss. variant |  | Sum | 16 Hz | 31.5 Hz | 63 Hz |  | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | 8000 Hz
| AnyTime | Lw" /dB | 82.6 | - | 78.6 | 77.4 |  | 73.3 | 72.8 | 69.4 | 63.2 | 57 | 51.2 | 43.3
FLQi016 | Label |  | ULA: Feedwater Pump Station/DACH |  |  |  |  | Action radius/m |  |  |  | 99999
| Group |  | Group 0 |  |  |  |  | Lw (AnyTime) /dB(A) |  |  |  | 92.29
| Number of nodes |  | 6 |  |  |  |  | Lw" (AnyTime) /dB(A) |  |  |  | 65.25
| Length/ m |  | 90.32 |  |  |  |  | D0 |  |  |  | 0
| Length/ m (2D) |  | 90.32 |  |  |  |  | High building/high noise source |  |  |  | No
| Area /m² |  | 505.06 |  |  |  |  | Emission is |  |  |  | SPL per unit area (Lw/m²)
| Emiss. variant |  | Sum | 16 Hz | 31.5 Hz | 63 Hz |  | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | 8000 Hz
| AnyTime | Lw" /dB | 86.3 | - | 85.4 | 77.2 |  | 73.1 | 65.6 | 61.2 | 59 | 55.8 | 53 | 46.1
FLQi017 | Label |  | UBA: PCC7/DACH |  |  |  |  | Action radius/m |  |  |  | 99999
| Group |  | Group 0 |  |  |  |  | Lw (AnyTime) /dB(A) |  |  |  | 87.97
| Number of nodes |  | 5 |  |  |  |  | Lw" (AnyTime) /dB(A) |  |  |  | 64.11
| Length/ m |  | 63.91 |  |  |  |  | D0 |  |  |  | 0
| Length/ m (2D) |  | 63.91 |  |  |  |  | High building/high noise source |  |  |  | No
| Area /m² |  | 243.11 |  |  |  |  | Emission is |  |  |  | SPL per unit area (Lw/m²)
| Emiss. variant |  | Sum | 16 Hz | 31.5 Hz | 63 Hz |  | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | 8000 Hz
| AnyTime | Lw" /dB | 76.5 | - | 72.5 | 71.3 |  | 67.2 | 66.7 | 63.3 | 57.1 | 50.9 | 45.1 | 37.2
FLQi018 | Label |  | UMX: Diffuser Duct/WAND1 |  |  |  |  | Action radius/m |  |  |  | 99999
| Group |  | Group 0 |  |  |  |  | Lw (AnyTime) /dB(A) |  |  |  | 83.31
| Number of nodes |  | 5 |  |  |  |  | Lw" (AnyTime) /dB(A) |  |  |  | 64.59
| Length/ m |  | 34.62 |  |  |  |  | D0 |  |  |  | 0
| Length/ m (2D) |  | 18.62 |  |  |  |  | High building/high noise source |  |  |  | No
| Area /m² |  | 74.48 |  |  |  |  | Emission is |  |  |  | SPL per unit area (Lw/m²)
| Emiss. variant |  | Sum | 16 Hz | 31.5 Hz | 63 Hz |  | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | 8000 Hz
| AnyTime | Lw" /dB | 81.9 | - | 80.7 | 74.5 |  | 67.4 | 61.9 | 55.5 | 52.3 | 61.1 | 54.3 | 49.4
FLQi019 | Label |  | UMX: Diffuser Duct/WAND3 |  |  |  |  | Action radius/m |  |  |  | 99999
| Group |  | Group 0 |  |  |  |  | Lw (AnyTime) /dB(A) |  |  |  | 83.42
| Number of nodes |  | 5 |  |  |  |  | Lw" (AnyTime) /dB(A) |  |  |  | 64.59
| Length/ m |  | 35.11 |  |  |  |  | D0 |  |  |  | 0
| Length/ m (2D) |  | 19.11 |  |  |  |  | High building/high noise source |  |  |  | No
| Area /m² |  | 76.43 |  |  |  |  | Emission is |  |  |  | SPL per unit area (Lw/m²)
| Emiss. variant |  | Sum | 16 Hz | 31.5 Hz | 63 Hz |  | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | 8000 Hz
| AnyTime | Lw" /dB | 81.9 | - | 80.7 | 74.5 |  | 67.4 | 61.9 | 55.5 | 52.3 | 61.1 | 54.3 | 49.4
FLQi020 | Label |  | UMX: Diffuser Duct/DACH |  |  |  |  | Action radius/m |  |  |  | 99999
| Group |  | Group 0 |  |  |  |  | Lw (AnyTime) /dB(A) |  |  |  | 86.15
| Number of nodes |  | 5 |  |  |  |  | Lw" (AnyTime) /dB(A) |  |  |  | 64.59
| Length/ m |  | 49.26 |  |  |  |  | D0 |  |  |  | 0
| Length/ m (2D) |  | 49.26 |  |  |  |  | High building/high noise source |  |  |  | No
| Area /m² |  | 143.33 |  |  |  |  | Emission is |  |  |  | SPL per unit area (Lw/m²)
| Emiss. variant |  | Sum | 16 Hz | 31.5 Hz | 63 Hz |  | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | 8000 Hz
| AnyTime | Lw" /dB | 81.9 | - | 80.7 | 74.5 |  | 67.4 | 61.9 | 55.5 | 52.3 | 61.1 | 54.3 | 49.4
FLQi021 | Label |  | URA: Hybrid Cooling Tower/WAND2 |  |  |  |  | Action radius/m |  |  |  | 99999
| Group |  | Group 0 |  |  |  |  | Lw (AnyTime) /dB(A) |  |  |  | 97.11
| Number of nodes |  | 5 |  |  |  |  | Lw" (AnyTime) /dB(A) |  |  |  | 64.69
| Length/ m |  | 205.32 |  |  |  |  | D0 |  |  |  | 0
| Length/ m (2D) |  | 162.32 |  |  |  |  | High building/high noise source |  |  |  | No
| Area /m² |  | 1744.93 |  |  |  |  | Emission is |  |  |  | SPL per unit area (Lw/m²)
| Emiss. variant |  | Sum | 16 Hz | 31.5 Hz | 63 Hz |  | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | 8000 Hz
| AnyTime | Lw" /dB | 81.5 | - | 78.6 | 76.4 |  | 73.3 | 64.8 | 53.4 | 51.2 | 54 | 57.2 | 59.3
FLQi022 | Label |  | URA: Hybrid Cooling Tower/WAND4 |  |  |  |  | Action radius/m |  |  |  | 99999
| Group |  | Group 0 |  |  |  |  | Lw (AnyTime) /dB(A) |  |  |  | 97.09
| Number of nodes |  | 5 |  |  |  |  | Lw" (AnyTime) /dB(A) |  |  |  | 64.69
| Length/ m |  | 204.58 |  |  |  |  | D0 |  |  |  | 0
| Length/ m (2D) |  | 161.58 |  |  |  |  | High building/high noise source |  |  |  | No
| Area /m² |  | 1737 |  |  |  |  | Emission is |  |  |  | SPL per unit area (Lw/m²)
| Emiss. variant |  | Sum | 16 Hz | 31.5 Hz | 63 Hz |  | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | 8000 Hz
| AnyTime | Lw" /dB | 81.5 | - | 78.6 | 76.4 |  | 73.3 | 64.8 | 53.4 | 51.2 | 54 | 57.2 | 59.3
FLQi023 | Label |  | URA: Hybrid Cooling Tower/DACH |  |  |  |  | Action radius/m |  |  |  | 99999
| Group |  | Group 0 |  |  |  |  | Lw (AnyTime) /dB(A) |  |  |  | 98.86
| Number of nodes |  | 5 |  |  |  |  | Lw" (AnyTime) /dB(A) |  |  |  | 64.69
| Length/ m |  | 226.46 |  |  |  |  | D0 |  |  |  | 0
| Length/ m (2D) |  | 226.46 |  |  |  |  | High building/high noise source |  |  |  | No
| Area /m² |  | 2611.7 |  |  |  |  | Emission is |  |  |  | SPL per unit area (Lw/m²)
| Emiss. variant |  | Sum | 16 Hz | 31.5 Hz | 63 Hz |  | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | 8000 Hz
| AnyTime | Lw" /dB | 81.5 | - | 78.6 | 76.4 |  | 73.3 | 64.8 | 53.4 | 51.2 | 54 | 57.2 | 59.3
FLQi024 | Label |  | UGD: WT Plant Container/DACH |  |  |  |  | Action radius/m |  |  |  | 99999
| Group |  | Group 0 |  |  |  |  | Lw (AnyTime) /dB(A) |  |  |  | 86.05
| Number of nodes |  | 5 |  |  |  |  | Lw" (AnyTime) /dB(A) |  |  |  | 58.54
| Length/ m |  | 110.21 |  |  |  |  | D0 |  |  |  | 0
| Length/ m (2D) |  | 110.21 |  |  |  |  | High building/high noise source |  |  |  | No
| Area /m² |  | 564.64 |  |  |  |  | Emission is |  |  |  | SPL per unit area (Lw/m²)
| Emiss. variant |  | Sum | 16 Hz | 31.5 Hz | 63 Hz |  | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | 8000 Hz
| AnyTime | Lw" /dB | 67.3 | - | 61.9 | 58.7 |  | 59.6 | 62.1 | 54.7 | 52.5 | 49.3 | 43.5 | 40.6
FLQi025 | Label |  | UGJ: CW Pumps ( & ULX)/DACH |  |  |  |  | Action radius/m |  |  |  | 99999
| Group |  | Group 0 |  |  |  |  | Lw (AnyTime) /dB(A) |  |  |  | 85.48
| Number of nodes |  | 5 |  |  |  |  | Lw" (AnyTime) /dB(A) |  |  |  | 55.74
| Length/ m |  | 123.87 |  |  |  |  | D0 |  |  |  | 0
| Length/ m (2D) |  | 123.87 |  |  |  |  | High building/high noise source |  |  |  | No
| Area /m² |  | 940.98 |  |  |  |  | Emission is |  |  |  | SPL per unit area (Lw/m²)
| Emiss. variant |  | Sum | 16 Hz | 31.5 Hz | 63 Hz |  | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | 8000 Hz
| AnyTime | Lw" /dB | 74.2 | - | 70.7 | 70.5 |  | 63.4 | 58.9 | 53.5 | 47.3 | 42.1 | 36.3 | 33.4
FLQi026 | Label |  | UCA: Control & Admin Building/DACH |  |  |  |  | Action radius/m |  |  |  | 99999
| Group |  | Group 0 |  |  |  |  | Lw (AnyTime) /dB(A) |  |  |  | 88.38
| Number of nodes |  | 5 |  |  |  |  | Lw" (AnyTime) /dB(A) |  |  |  | 61.36
| Length/ m |  | 103.24 |  |  |  |  | D0 |  |  |  | 0
| Length/ m (2D) |  | 103.24 |  |  |  |  | High building/high noise source |  |  |  | No
| Area /m² |  | 504.38 |  |  |  |  | Emission is |  |  |  | SPL per unit area (Lw/m²)
| Emiss. variant |  | Sum | 16 Hz | 31.5 Hz | 63 Hz |  | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | 8000 Hz
| AnyTime | Lw" /dB | 79.3 | - | 78.4 | 70.2 |  | 65.1 | 61.6 | 60.2 | 56 | 49.8 | 44 | 39.1
FLQi027 | Label |  | UST: Workshop & Storage/DACH |  |  |  |  | Action radius/m |  |  |  | 99999
| Group |  | Group 0 |  |  |  |  | Lw (AnyTime) /dB(A) |  |  |  | 87.22
| Number of nodes |  | 5 |  |  |  |  | Lw" (AnyTime) /dB(A) |  |  |  | 57.55
| Length/ m |  | 136.02 |  |  |  |  | D0 |  |  |  | 0
| Length/ m (2D) |  | 136.02 |  |  |  |  | High building/high noise source |  |  |  | No
| Area /m² |  | 926.56 |  |  |  |  | Emission is |  |  |  | SPL per unit area (Lw/m²)
| Emiss. variant |  | Sum | 16 Hz | 31.5 Hz | 63 Hz |  | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | 8000 Hz
| AnyTime | Lw" /dB | 68.1 | - | 65.7 | 59.5 |  | 57.4 | 57.9 | 55.5 | 52.3 | 48.1 | 44.3 | 38.4
FLQi028 | Label |  | UHN: Stack/DACH |  |  |  |  | Action radius/m |  |  |  | 99999
| Group |  | Group 0 |  |  |  |  | Lw (AnyTime) /dB(A) |  |  |  | 94.37
| Number of nodes |  | 13 |  |  |  |  | Lw" (AnyTime) /dB(A) |  |  |  | 77.48
| Length/ m |  | 25.09 |  |  |  |  | D0 |  |  |  | 0
| Length/ m (2D) |  | 25.09 |  |  |  |  | High building/high noise source |  |  |  | No
| Area /m² |  | 48.93 |  |  |  |  | Emission is |  |  |  | SPL per unit area (Lw/m²)
| Emiss. variant |  | Sum | 16 Hz | 31.5 Hz | 63 Hz |  | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | 8000 Hz
| AnyTime | Lw" /dB | 88 | - | - | 85.3 |  | 83.2 | 75.7 | 70.3 | 68.1 | 68.9 | 72.1 | 65.2
FLQi029 | Label |  | UBA: PCC8/DACH |  |  |  |  | Action radius/m |  |  |  | 99999
| Group |  | Group 0 |  |  |  |  | Lw (AnyTime) /dB(A) |  |  |  | 87.97
| Number of nodes |  | 5 |  |  |  |  | Lw" (AnyTime) /dB(A) |  |  |  | 69.91
| Length/ m |  | 35.02 |  |  |  |  | D0 |  |  |  | 0
| Length/ m (2D) |  | 35.02 |  |  |  |  | High building/high noise source |  |  |  | No
| Area /m² |  | 64.01 |  |  |  |  | Emission is |  |  |  | SPL per unit area (Lw/m²)
| Emiss. variant |  | Sum | 16 Hz | 31.5 Hz | 63 Hz |  | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | 8000 Hz
| AnyTime | Lw" /dB | 82.3 | - | 78.3 | 77.1 |  | 73 | 72.5 | 69.1 | 62.9 | 56.7 | 50.9 | 43

## NSR Locations
No. | Name | Label | Group | ABS_HEIGHT | xmin / m | xmax / m | ymin / m | ymax / m
1 | IPkt001 | 1: Marsh Lane | Group 0 | 4 | 515569.38 | 515569.38 | 421413.26 | 421413.26
2 | IPkt002 | 2: Skitter Road | Group 0 | 4 | 514071.6 | 514071.6 | 420625.57 | 420625.57
3 | IPkt003 | 3: Station Road | Group 0 | 4 | 513943.55 | 513943.55 | 420229.78 | 420229.78
4 | IPkt004 | 4: Kettlebridge Lane | Group 0 | 4 | 514114.28 | 514114.28 | 419678.78 | 419678.78
5 | IPkt005 | 5: Swinster Lane | Group 0 | 4 | 514323 | 514323 | 419316 | 419316
6 | IPkt006 | 6: Scrub Lane | Group 0 | 4 | 514270 | 514270 | 419050 | 419050
7 | IPkt007 | 7: Brick Lane | Group 0 | 4 | 514641 | 514641 | 418828 | 418828
8 | IPkt008 | 10: Old Vicarage | Group 0 | 4 | 514426 | 514426 | 418206 | 418206
9 | IPkt009 | ARUP Haven Pits ECO | Group 0 | 1 | 516233 | 516233 | 419710 | 419710
- END OF LIST -

## Industrial Buildings
No. | Name | Label | Group | ABS_HEIGHT | H_REL_KNT1 | Number of nodes | Element length in m (3D) | Element total area in m² | Absolute definition of z. | xmin / m | xmax / m | ymin / m | ymax / m | zmin / m | zmax / m
1 | HAUS001 | HLIN /WÄNDE | Group 0 | 5 | 5 | 5 | 59.32 | 211.08 | Yes | 515233.23 | 515254.23 | 418773.95 | 418792.63 | 5 | 5
2 | HAUS002 | HLIN /WÄNDE | Group 0 | 5 | 5 | 5 | 110.07 | 730.97 | Yes | 515269.99 | 515304.84 | 418781.96 | 418821.22 | 5 | 5
3 | HAUS003 | HLIN /WÄNDE | Group 0 | 5 | 5 | 5 | 81.34 | 330.29 | Yes | 515297.73 | 515321.08 | 418798.71 | 418830.05 | 5 | 5
4 | HAUS004 | HLIN /WÄNDE | Group 0 | 5 | 5 | 5 | 136.92 | 1081.79 | Yes | 515316.78 | 515358.51 | 418796.5 | 418846.67 | 5 | 5
5 | HAUS005 | HLIN /WÄNDE | Group 0 | 21 | 21 | 5 | 257.51 | 3344.16 | Yes | 515322.22 | 515421.2 | 418928.46 | 419002.74 | 21 | 21
6 | HAUS006 | HLIN /WÄNDE | Group 0 | 5 | 5 | 7 | 93.67 | 460.96 | Yes | 515249.04 | 515276.45 | 418837.65 | 418873.14 | 5 | 5
7 | HAUS007 | HLIN /WÄNDE | Group 0 | 10 | 10 | 5 | 231.25 | 1813.76 | Yes | 515297.48 | 515392.37 | 418975.82 | 419036.65 | 10 | 10
8 | HAUS008 | HLIN /WÄNDE | Group 0 | 13 | 13 | 5 | 274.41 | 1637.37 | Yes | 515227.93 | 515344.14 | 419067.87 | 419136.58 | 13 | 13
9 | HAUS009 | HLIN /WÄNDE | Group 0 | 8 | 8 | 5 | 105.76 | 583.09 | Yes | 515349.74 | 515389.86 | 419120.02 | 419150.83 | 8 | 8
10 | HAUS010 | HLIN /WÄNDE | Group 0 | 5 | 5 | 5 | 55.32 | 190.67 | Yes | 515387.32 | 515406.28 | 419166.43 | 419184.74 | 5 | 5
11 | HAUS011 | Extra Building | Group 0 | 5 | 5 | 5 | 205.93 | 1084.12 | Yes | 515295.18 | 515381.46 | 418994.08 | 419046.31 | 5 | 5
12 | HAUS012 | HLIN /WÄNDE* | Group 0 | 10 | 10 | 5 | 231.25 | 1813.76 | Yes | 515297.48 | 515392.37 | 418975.82 | 419036.65 | 10 | 10
13 | HAUS013 | Haus | Group 0 | 8 | 8 | 9 | 209.29 | 1882.41 | Yes | 515377.23 | 515443.18 | 418799.41 | 418864.73 | 8 | 8
14 | HAUS014 | Haus | Group 0 | 9 | 9 | 7 | 118.84 | 568.29 | Yes | 515439.56 | 515482.59 | 418858.66 | 418885.69 | 9 | 9
15 | HAUS015 | SyncComp Building Footprint | Group 0 | 21 | 21 | 5 | 275.21 | 3275.16 | Yes | 515348.86 | 515458.11 | 418878.35 | 418954.23 | 21 | 21
16 | HAUS016 | GT11 Duct | Group 0 | 2.5 | 2.5 | 5 | 50.03 | 95.47 | Yes | 515321.02 | 515334.77 | 418964.54 | 418984.53 | 2.5 | 2.5
17 | HAUS017 | GT12 Duct | Group 0 | 2.5 | 2.5 | 5 | 50.03 | 95.47 | Yes | 515341.67 | 515355.42 | 418975.37 | 418995.36 | 2.5 | 2.5
18 | HAUS018 | GT21 Duct | Group 0 | 2.5 | 2.5 | 5 | 50.03 | 95.47 | Yes | 515362.03 | 515375.78 | 418985.74 | 419005.74 | 2.5 | 2.5
19 | HAUS019 | GT22 Duct | Group 0 | 2.5 | 2.5 | 5 | 50.03 | 95.47 | Yes | 515382.62 | 515396.37 | 418996.31 | 419016.3 | 2.5 | 2.5
20 | HAUS020 | Xformer/Barriers | Group 0 | 4 | 4 | 5 | 43.5 | 118.19 | Yes | 515307.41 | 515322.03 | 419022.69 | 419037.36 | 4 | 4
21 | HAUS021 | Xformer 3 | Group 0 | 4 | 4 | 5 | 43.5 | 118.19 | Yes | 515327.64 | 515342.26 | 419032.68 | 419047.36 | 4 | 4
22 | HAUS022 | Xformer 4 | Group 0 | 4 | 4 | 5 | 43.5 | 118.19 | Yes | 515348.27 | 515362.89 | 419043.39 | 419058.07 | 4 | 4
23 | HAUS023 | Xformer 1 | Group 0 | 4 | 4 | 5 | 43.5 | 118.19 | Yes | 515286.46 | 515301.08 | 419012.61 | 419027.29 | 4 | 4
24 | HAUS024 | Hornsea1 | Group 0 | 6 | 6 | 5 | 129.95 | 1049.67 | Yes | 514934.54 | 514978.92 | 419319.58 | 419361.64 | 6 | 6
25 | HAUS025 | Hornsea2 | Group 0 | 15 | 15 | 5 | 249.76 | 2120.22 | Yes | 514998.09 | 515101.54 | 419347.49 | 419409.86 | 15 | 15
26 | HAUS026 | Hornsea3 | Group 0 | 10 | 10 | 5 | 80.94 | 406.33 | Yes | 514978.19 | 515004.25 | 419227.27 | 419255.04 | 10 | 10
27 | HAUS027 | Hornsea4 | Group 0 | 10 | 10 | 5 | 80.91 | 406.04 | Yes | 515019.4 | 515045.45 | 419246.24 | 419274 | 10 | 10
28 | HAUS028 | Hornsea5 | Group 0 | 10 | 10 | 5 | 80.92 | 406.14 | Yes | 515060.36 | 515086.19 | 419265.46 | 419293.09 | 10 | 10
29 | HAUS029 | Hornsea6 | Group 0 | 14 | 14 | 5 | 195.79 | 1331.5 | Yes | 515018.06 | 515098.94 | 419183.52 | 419232.64 | 14 | 14
30 | HAUS030 | UBA: PCC11/Barriers | Group 0 | 5.5 | 5.5 | 5 | 32.98 | 56.4 | Yes | 515625.05 | 515634.32 | 419635.52 | 419648.15 | 5.5 | 5.5
31 | HAUS031 | ULA: Feedwater Pump Station/Barriers | Group 0 | 11.5 | 11.5 | 6 | 89.52 | 496.07 | Yes | 515629.76 | 515660.08 | 419639.36 | 419668.26 | 11.5 | 11.5
32 | HAUS032 | UGC: Demin Tank/Barriers | Group 0 | 10 | 10 | 12 | 37.58 | 109.32 | Yes | 515803.26 | 515815.22 | 419668.02 | 419680 | 10 | 10
33 | HAUS033 | UHA: HRSG (02)/Barriers | Group 0 | 5 | 5 | 5 | 30.87 | 59.06 | Yes | 515628.17 | 515638.76 | 419661.44 | 419671.28 | 5 | 5
34 | HAUS034 | UBA: PCC7/Barriers | Group 0 | 5.5 | 5.5 | 5 | 63.11 | 236.76 | Yes | 515726.46 | 515749.05 | 419667.32 | 419686.74 | 5.5 | 5.5
35 | HAUS035 | UHA: HRSG/Barriers | Group 0 | 45 | 45 | 5 | 129.65 | 1024.62 | Yes | 515631.15 | 515676.71 | 419664.72 | 419704.92 | 45 | 45
36 | HAUS036 | UMX: Diffuser Duct/Barriers | Group 0 | 8 | 8 | 5 | 48.46 | 138.44 | Yes | 515667.23 | 515681.96 | 419687.87 | 419705.28 | 8 | 8
37 | HAUS037 | UMC: GT&ST Building/Barriers | Group 0 | 31.6 | 31.6 | 5 | 201.77 | 2393.29 | Yes | 515671.57 | 515744.38 | 419681.19 | 419741.94 | 31.6 | 31.6
38 | HAUS038 | URA: Hybrid Cooling Tower/Barriers | Group 0 | 21.5 | 21.5 | 5 | 225.66 | 2589.09 | Yes | 515796.33 | 515858.61 | 419707.6 | 419794.63 | 21.5 | 21.5
39 | HAUS039 | UGD: WT Plant Container/Barriers | Group 0 | 8.75 | 8.75 | 5 | 109.41 | 553.66 | Yes | 515771.83 | 515801.06 | 419659.07 | 419702.24 | 8.75 | 8.75
40 | HAUS040 | UGE: Neutralization Tank/Barriers | Group 0 | 5.2 | 5.2 | 5 | 30.28 | 57.29 | Yes | 515786.88 | 515796.83 | 419694.19 | 419704.33 | 5.2 | 5.2
41 | HAUS041 | UYE: Gatehouse/Barriers | Group 0 | 4 | 4 | 5 | 33.03 | 67.68 | Yes | 515850.77 | 515861.2 | 419655.77 | 419667.06 | 4 | 4
42 | HAUS042 | UGJ: CW Pumps ( & ULX)/Barriers | Group 0 | 11.5 | 11.5 | 5 | 123.07 | 928.63 | Yes | 515744.17 | 515787.17 | 419601.55 | 419640.04 | 11.5 | 11.5
43 | HAUS043 | UCA: Control & Admin Building/Barriers | Group 0 | 5.65 | 5.65 | 5 | 102.44 | 494.1 | Yes | 515758.94 | 515799.18 | 419573.67 | 419601.2 | 5.65 | 5.65
44 | HAUS044 | UST: Workshop & Storage/Barriers | Group 0 | 8 | 8 | 5 | 135.22 | 913 | Yes | 515761.63 | 515813.88 | 419537.18 | 419574.36 | 8 | 8
45 | HAUS045 | UHN: Stack/Barriers | Group 0 | 85 | 85 | 13 | 24.44 | 46.46 | Yes | 515627.12 | 515634.84 | 419671.78 | 419679.51 | 85 | 85
46 | HAUS046 | UBA: PCC8/Barriers | Group 0 | 5.5 | 5.5 | 5 | 34.22 | 60.55 | Yes | 515705.04 | 515714.73 | 419658.27 | 419671.21 | 5.5 | 5.5
47 | HAUS047 | UMC: GT&ST Building Lower/Barriers | Group 0 | 15.05 | 15.05 | 5 | 231.17 | 3315.54 | Yes | 515671.57 | 515750.53 | 419667.99 | 419741.94 | 15.05 | 15.05
48 | HAUS048 | UGA: Tank/Barriers | Group 0 | 10 | 10 | 12 | 37.7 | 109.98 | Yes | 515797.08 | 515809.12 | 419681.75 | 419693.69 | 10 | 10
- END OF LIST -

## Hard Ground Areas
No. | Name | Label | Group | Number of nodes | Element length in m (3D) | Element total area in m² | xmin / m | xmax / m | ymin / m | ymax / m
1 | DBod001 | Site Perimeter | Group 0 | 16 | 1981.52 | 142523.84 | 515468.61 | 515975.52 | 419266.69 | 419854.16
2 | DBod002 | HLIN | Group 0 | 12 | 1148.39 | 69469.92 | 514903.68 | 515208.62 | 419086.32 | 419486.22
3 | DBod003 | HLIN | Group 0 | 5 | 290.58 | 3770.66 | 515333.19 | 515448.83 | 419350.39 | 419427.48
4 | DBod004 | HLIN | Group 0 | 5 | 133.94 | 1118.73 | 515498.02 | 515543.79 | 419381.35 | 419423.93
5 | DBod005 | HLIN | Group 0 | 5 | 383.89 | 8472.83 | 515351.18 | 515490.68 | 419279.3 | 419393.34
6 | DBod006 | HLIN | Group 0 | 10 | 858.87 | 43415.57 | 515253.29 | 515524.94 | 419389.67 | 419646.64
7 | DBod007 | HLIN | Group 0 | 10 | 1698.58 | 163320.23 | 515136.79 | 515658.08 | 418686.3 | 419208.57
8 | DBod008 | HLIN | Group 0 | 5 | 667.39 | 25248.15 | 514778.75 | 514934.4 | 418972.4 | 419234.75
9 | DBod009 | HLIN | Group 0 | 5 | 304.62 | 5358.26 | 514854.37 | 514966.46 | 418540.68 | 418633.19
10 | DBod010 | HLIN | Group 0 | 31 | 5041.9 | 1030292.3 | 515368.44 | 516733.9 | 419559.46 | 421139.05
11 | DBod011 | HLIN | Group 0 | 21 | 5487.43 | 1822298.58 | 515868.43 | 517606.09 | 417961.94 | 419679.42
12 | DBod012 | HLIN | Group 0 | 22 | 6016.02 | 1711433.82 | 514801.18 | 516408.79 | 417058.36 | 418753.98
- END OF LIST -

## Point Sources
No. | Name | Label | Group | ABS_HEIGHT | xmin / m | xmax / m | ymin / m | ymax / m | zmin / m | zmax / m | Lw | Directivity on/off? | high noise source?
1 | EZQi001 | UMY: Steam pipes | Group 0 | 5 | 515676.53 | 515676.53 | 419677.01 | 419677.01 | 5 | 5 | 81.74 | No | No
2 | EZQi002 | ULY: Pipe Bridge | Group 0 | 5 | 515653.37 | 515653.37 | 419666.21 | 419666.21 | 5 | 5 | 81.74 | No | No
3 | EZQi003 | UEN: Fuel PRS | Group 0 | 1 | 515619.48 | 515619.48 | 419727.89 | 419727.89 | 1 | 1 | 97.48 | No | No
4 | EZQi004 | UHX02: Sampling Container | Group 0 | 3 | 515627.71 | 515627.71 | 419690.56 | 419690.56 | 3 | 3 | 87.93 | No | No
5 | EZQi005 | UEN: Fuel Preheater&Metering | Group 0 | 1 | 515671.49 | 515671.49 | 419661.35 | 419661.35 | 1 | 1 | 83.15 | No | No
6 | EZQi006 | UBF: Generator Transformer | Group 0 | 2 | 515702.33 | 515702.33 | 419637.08 | 419637.08 | 2 | 2 | 98.91 | No | No
7 | EZQi007 | UBE: Aux Power Transformer | Group 0 | 2 | 515717.22 | 515717.22 | 419643.4 | 419643.4 | 2 | 2 | 79.91 | No | No
8 | EZQi008 | MBL: Filterhouse | Group 0 | 25 | 515706.61 | 515706.61 | 419680.08 | 419680.08 | 25 | 25 | 95.49 | No | No
9 | EZQi009 | URO: Cooling Tower Treatment Plant | Group 0 | 2 | 515807.37 | 515807.37 | 419724.35 | 419724.35 | 2 | 2 | 85.52 | No | No
- END OF LIST -

## Area Sources
No. | Name | Label | Group | ABS_HEIGHT | H_REL_KNT1 | Number of nodes | Element length in m (3D) | Element total area in m² | xmin / m | xmax / m | ymin / m | ymax / m | zmin / m | zmax / m | zmin(rel)/ m | zmax(rel)/ m | zmin(abs)/ m | zmax(abs)/ m | Lw (Overall Sound Power Level dBA) | LW_2STR ( Sound Power Level per m2 dBA) | high noise source?
1 | FLQi001 | UHA: HRSG/WAND1 | Group 0 | 0 | 0 | 5 | 165.17 | 1691.31 | 515631.02 | 515665.25 | 419689.54 | 419705.05 | 0 | 45 | 0 | 45 | 0 | 45 | 88.25 | 55.97 | No
2 | FLQi002 | UHA: HRSG/WAND2 | Group 0 | 0 | 0 | 5 | 145.34 | 1245.04 | 515665.25 | 515676.84 | 419679.92 | 419705.05 | 0 | 45 | 0 | 45 | 0 | 45 | 86.92 | 55.97 | No
3 | FLQi003 | UHA: HRSG/WAND3 | Group 0 | 0 | 0 | 5 | 165.63 | 1701.61 | 515642.28 | 515676.84 | 419664.58 | 419679.92 | 0 | 45 | 0 | 45 | 0 | 45 | 88.28 | 55.97 | No
4 | FLQi004 | UHA: HRSG/WAND4 | Group 0 | 0 | 0 | 5 | 144.76 | 1232.21 | 515631.02 | 515642.28 | 419664.58 | 419689.54 | 0 | 45 | 0 | 45 | 0 | 45 | 86.88 | 55.97 | No
5 | FLQi005 | UHA: HRSG/DACH | Group 0 | 45 | 45 | 5 | 130.45 | 1037.63 | 515631.02 | 515676.84 | 419664.58 | 419705.05 | 45 | 45 | 45 | 45 | 45 | 45 | 86.13 | 55.97 | No
6 | FLQi006 | UMC: GT&ST Building/WAND1 | Group 0 | 15.05 | 15.05 | 5 | 158.97 | 1041.6 | 515671.44 | 515728.77 | 419716.11 | 419742.07 | 15.05 | 31.6 | 15.05 | 31.6 | 15.05 | 31.6 | 78.06 | 47.88 | No
7 | FLQi007 | UMC: GT&ST Building/WAND2 | Group 0 | 15.05 | 15.05 | 5 | 109.56 | 632.72 | 515728.77 | 515744.52 | 419707.23 | 419742.07 | 15.05 | 31.6 | 15.05 | 31.6 | 15.05 | 31.6 | 75.89 | 47.88 | No
8 | FLQi008 | UMC: GT&ST Building/WAND3 | Group 0 | 15.05 | 15.05 | 5 | 158.97 | 1041.58 | 515687.28 | 515744.52 | 419681.06 | 419707.23 | 15.05 | 31.6 | 15.05 | 31.6 | 15.05 | 31.6 | 78.06 | 47.88 | No
9 | FLQi009 | UMC: GT&ST Building/WAND4 | Group 0 | 15.05 | 15.05 | 5 | 110.03 | 636.63 | 515671.44 | 515687.28 | 419681.06 | 419716.11 | 15.05 | 31.6 | 15.05 | 31.6 | 15.05 | 31.6 | 75.92 | 47.88 | No
10 | FLQi010 | UMC: GT&ST Building/DACH | Group 0 | 31.6 | 31.6 | 5 | 202.57 | 2413.5 | 515671.44 | 515744.52 | 419681.06 | 419742.07 | 31.6 | 31.6 | 31.6 | 31.6 | 31.6 | 31.6 | 81.71 | 47.88 | No
11 | FLQi011 | UMC: GT&ST Building Lower/WAND1 | Group 0 | 0 | 0 | 5 | 155.97 | 947.19 | 515671.44 | 515728.77 | 419716.11 | 419742.07 | 0 | 15.05 | 0 | 15.05 | 0 | 15.05 | 77.65 | 47.88 | No
12 | FLQi012 | UMC: GT&ST Building Lower/WAND2 | Group 0 | 0 | 0 | 5 | 136.38 | 799.75 | 515728.77 | 515750.66 | 419693.65 | 419742.07 | 0 | 15.05 | 0 | 15.05 | 0 | 15.05 | 76.91 | 47.88 | No
13 | FLQi013 | UMC: GT&ST Building Lower/WAND3 | Group 0 | 0 | 0 | 5 | 156 | 947.4 | 515693.23 | 515750.66 | 419667.86 | 419693.65 | 0 | 15.05 | 0 | 15.05 | 0 | 15.05 | 77.65 | 47.88 | No
14 | FLQi014 | UMC: GT&ST Building Lower/WAND4 | Group 0 | 0 | 0 | 5 | 135.99 | 796.84 | 515671.44 | 515693.23 | 419667.86 | 419716.11 | 0 | 15.05 | 0 | 15.05 | 0 | 15.05 | 76.9 | 47.88 | No
15 | FLQi015 | UBA: PCC11/DACH | Group 0 | 5.5 | 5.5 | 5 | 33.78 | 59.74 | 515624.92 | 515634.45 | 419635.39 | 419648.29 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 87.97 | 70.21 | No
16 | FLQi016 | ULA: Feedwater Pump Station/DACH | Group 0 | 11.5 | 11.5 | 6 | 90.32 | 505.06 | 515629.62 | 515660.21 | 419639.23 | 419668.4 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 92.29 | 65.25 | No
17 | FLQi017 | UBA: PCC7/DACH | Group 0 | 5.5 | 5.5 | 5 | 63.91 | 243.11 | 515726.33 | 515749.18 | 419667.19 | 419686.88 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 87.97 | 64.11 | No
18 | FLQi018 | UMX: Diffuser Duct/WAND1 | Group 0 | 0 | 0 | 5 | 34.62 | 74.48 | 515667.1 | 515675.56 | 419701.53 | 419705.41 | 0 | 8 | 0 | 8 | 0 | 8 | 83.31 | 64.59 | No
19 | FLQi019 | UMX: Diffuser Duct/WAND3 | Group 0 | 0 | 0 | 5 | 35.11 | 76.43 | 515673.38 | 515682.09 | 419687.74 | 419691.65 | 0 | 8 | 0 | 8 | 0 | 8 | 83.42 | 64.59 | No
20 | FLQi020 | UMX: Diffuser Duct/DACH | Group 0 | 8 | 8 | 5 | 49.26 | 143.33 | 515667.1 | 515682.09 | 419687.74 | 419705.41 | 8 | 8 | 8 | 8 | 8 | 8 | 86.15 | 64.59 | No
21 | FLQi021 | URA: Hybrid Cooling Tower/WAND2 | Group 0 | 0 | 0 | 5 | 205.32 | 1744.93 | 515825.53 | 515858.74 | 419720.71 | 419794.76 | 0 | 21.5 | 0 | 21.5 | 0 | 21.5 | 97.11 | 64.69 | No
22 | FLQi022 | URA: Hybrid Cooling Tower/WAND4 | Group 0 | 0 | 0 | 5 | 204.58 | 1737 | 515796.2 | 515829.45 | 419707.47 | 419781.1 | 0 | 21.5 | 0 | 21.5 | 0 | 21.5 | 97.09 | 64.69 | No
23 | FLQi023 | URA: Hybrid Cooling Tower/DACH | Group 0 | 21.5 | 21.5 | 5 | 226.46 | 2611.7 | 515796.2 | 515858.74 | 419707.47 | 419794.76 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 98.86 | 64.69 | No
24 | FLQi024 | UGD: WT Plant Container/DACH | Group 0 | 8.75 | 8.75 | 5 | 110.21 | 564.64 | 515771.7 | 515801.2 | 419658.94 | 419702.37 | 8.75 | 8.75 | 8.75 | 8.75 | 8.75 | 8.75 | 86.05 | 58.54 | No
25 | FLQi025 | UGJ: CW Pumps ( & ULX)/DACH | Group 0 | 11.5 | 11.5 | 5 | 123.87 | 940.98 | 515744.04 | 515787.31 | 419601.42 | 419640.17 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 85.48 | 55.74 | No
26 | FLQi026 | UCA: Control & Admin Building/DACH | Group 0 | 5.65 | 5.65 | 5 | 103.24 | 504.38 | 515758.81 | 515799.31 | 419573.53 | 419601.34 | 5.65 | 5.65 | 5.65 | 5.65 | 5.65 | 5.65 | 88.38 | 61.36 | No
27 | FLQi027 | UST: Workshop & Storage/DACH | Group 0 | 8 | 8 | 5 | 136.02 | 926.56 | 515761.5 | 515814.01 | 419537.05 | 419574.49 | 8 | 8 | 8 | 8 | 8 | 8 | 87.22 | 57.55 | No
28 | FLQi028 | UHN: Stack/DACH | Group 0 | 85 | 85 | 13 | 25.09 | 48.93 | 515627.01 | 515634.95 | 419671.68 | 419679.61 | 85 | 85 | 85 | 85 | 85 | 85 | 94.37 | 77.48 | No
29 | FLQi029 | UBA: PCC8/DACH | Group 0 | 5.5 | 5.5 | 5 | 35.02 | 64.01 | 515704.9 | 515714.86 | 419658.14 | 419671.34 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 87.97 | 69.91 | No
- END OF LIST -

## IMMI Model Configuration
Calculation parameters | KLCP CCGT Settings |  | Reference setting
Calculation model: General | Point calculation | Grid calculation | Point calculation | Grid calculation
Adapt assessment area seamlessly to the receiver position
L /m
Terrain triangulation edges are obstacle | Yes | Yes |  | Yes
consider negative loop way at terraine triangular lines | Yes | Yes |  | Yes
Improved interpolation in boundary areas | Yes | Yes |  | Yes
Free field in front of refl. surfaces/m
acc. to sources | 1 | 1 |  | 1
acc. to immission points | 1 | 1 |  | 1
House: white border in grid | No | No |  | No
Intermediate messages: | No | No |  | No
Calculation model: Parameters | Optimised | Optimised |  | "reference settings"
Limiting range of sound sources:
* Limit the search radius (distance source-IP): | No | No |  | No
* minimum level difference /dB: | No | No |  | No
Projection of line sound sources | Yes | Yes |  | Yes
Projection of area sound sources | Yes | Yes |  | Yes
Limit projection | No | No |  | No
* Radius /m around source:
* Radius /m around IP:
Minimum length for sections /m | 1 | 1 |  | 1
Variable min. length for sections:
* in percent of the distance from the IP source | No | No |  | No
Add. factor for distance criterion | 1 | 1 |  | 1
Barrier attenuation differing from guideline: | No | No |  | No
* Cut-off limit for insertion loss:
* Limit /dB for single screens:
* Limit /dB for multiple screens:
Calculate attenuation for VDI 2720, ISO9613
* Lateral pathway | Yes | Yes |  | Yes
* Lateral pathway for image sources | No | No |  | No
Reflection
Reflection (max. order) | 1 | 1 |  | 1
Limit the search radius (distance source-IP): | No | No |  | No
* Search radius /m
Limiting range of reflecting surfaces /m:
* Radius around source or IP /m: | No | No |  | No
* minimum level difference /dB: | No | No |  | No
Image source from projection | Yes | Yes |  | Yes
No refl. if entirely screened | Yes | Yes |  | Yes
Save rays as help lines | No | No |  | No
section control
Section control acc. Schall 03 [2012]: | Yes | Yes |  | Yes
Section control for other calculation methods, too: | No | No |  | No
Accelerated iteration (approximation): | No | No |  | No
Requested accuracy /dB: | 0.1 | 0.1 |  | 0.1
Show intermediate results: | No | No |  | No
Global parameters | KLCP CCGT Settings | [Reference setting]
Default for G outside DBOD-elements | 1 | 0
Temperature /°C | 10 | 10
Relative humidity /% | 70 | 70
Living area per inhab-/m² (=0.8*gross) | 40 | 40
Average storey height /m | 2.8 | 2.8
Parameters of library: ISO 9613-2 | KLCP CCGT Settings | [Reference setting]
Downwind conditions | Yes | Yes
Simplified equation (Nr. 7.3.2) for ground effect
for frequency-dependent calculation | No | No
for frequency-independent calculation | Yes | Yes
Evaluating the mean height hm | according to ISO 9613-2 (2024) | according to ISO 9613-2 (1999)
Simplified calculation using free propagation conditions (release 7/2002)(obsolete) | No | No
Attenuation due to screening - subtract negative ground effect | No | No
Deduction no more than to -Dz | No | No
"Additional recommendations" - ISO TR 17534-3 | Yes | Yes
ABar acc. "Erlass Thüringen" (2015-01-10) | No | No
Accounts for vegetation | Yes | Yes
Accounts for housing | Yes | Yes
Accounts for ground effect | Yes | Yes