## Slide 1: Water Supply Failure
Possible cause (what would this look like) | Effect | Outline Recovery & Continuity Plan | Specific contact details required | RTO
Most likely local pipework issues on site leakage or blockage/damage due to groundworks Draught -Thames Water would restrict in a time window or volume, usually with a weeks notice Water company working on the lines Burst Thames Water pipe | Volume of water stored onsite? 2hrs worth of production on 5 lines onsite in water treatment plant. c500cube Avg daily usage? 200cube an hour Impact on Production? Potentially 2hrs of production. Staff welfare impact? Water for toilets – how long can we keep staff onsite without water for sanitary requirements? 8 Hours can be achieved using stored bottled water that is kept on site. | How are we alerted? Water treatment alarm – low incoming pressure alarm. Could haulage play a part? We have an external water inlet but a 30k tank wont last very long, all the neighbours would also want that What will we do? Blend Hand washing and toilets Kitchen could still operate Bypass in place to facilitate welfare water Staffside – Training, 5S, basic maintenance Decision to be made around sending staff home/stopping them coming in. Pallets of drinking water onsite What does ramp up look like? System flushed through, water come back gradually Switch lines on by priority | Thames water hotline 08003169800 Castle Water 01250 718718 Portable Toilet Hire (London) Ltd Barking 02085943673 | How long to start up after water has come back on? Dependent on how much water received from a pressure perspective. Flushing system through is very quick, 30mins max. C4-8hrs recovery, mainly due to CIPs etc.. Product dependent. Any watchouts? Bypass> sanitary water enabled keeping people on site

## Slide 2: Loss of electricity/Power
Possible cause | Effect | Outline Recovery & Continuity Plan | Specific contact details required | RTO
1 Issues with Power lines in 2 Issue with Transformers 3 How many lines in? 1 incoming into HV then low voltage then splits into L5 and PET | How much power does site use? 60,000kw/h Cant operate site - no generators Emergency lighting - 4hrs min | What’s the plan? Can offload CO2 -, -Sugar is blown into silo but would lose safety so not viable. -Gates would open so ISS would have to upscale to guard gates -H&S – staff to be taken safely off site -Potential issue around Uninterpretable power supplies UPS – (12hrs)s and Electrical Panels not coming back on. (Learning from Spector) -No bulk liquid as no pumps of low meters would function -Some engineering work still possible depending on light levels what is the appropriate level? -Hire in Diesel Generators -6 to 8 hrs – there is space, straight to transformer -No manual workaround if SAP drops Develop: -Skeleton recovery plan -Priority -Whats in tank -Staff available | Who do we need to contact? Generator supplier Aggreko 03330163417 Power Testing Ltd: 01245266800 Eon – Electricity Emergency Team 03450520000 National Grid 02070043000 ISS – to escalate for more staff George Thatcher 07725900601 | When was most recent? What happened? What did we do? How long outage? Cable failed (HV-LV) How long to ramp back up? -c2hrs -but if in a CIP potentially 6hrs -The longer the outage the longer the clean Watchouts? A good learning from Spector – installation of UPS

## Slide 3: Loss of Steam
Possible cause | Effect | Outline Recovery & Continuity Plan | Specific contact details required | RTO
Boiler breakdown/defect Loss of GAS | How much steam do we need? 2x gas boilers –only 1 currently required No boilers – no production | How do we recover? We have N+2 Beckton year on year - 33m cases Transitioning in chilling, adding 2x GEA chilling plants (May/June 2021) Mobile boiler No boilers – just cleaning and engineering work could be completed L1 large PET 2ltr - 16k an hour L2 Large PET 2ltr and pasteurised – 18k L3 Small PET – 500ml and 375ml – 48k L4 375ml – 22k /2ltr – 18k L5 Large PET 1.5 – 41k /2ltr – 36k carbs . Stls 850ml 1ltr – 47k /2ltr -25k /3ltr – 15k | Emergency E on Gas Supply: 0800111999 Byworth Boilers: 01535665225 | Ramp up Mobile boiler – c2-3 days to order and then plug in..
Notes: L1 large PET 2ltr - 16k an hour
L2 Large PET 2ltr and pasteurised – 18k
L3 Small PET – 500ml and 375ml – 48k
L4 375ml – 22k /2ltr – 18k
L5 Large PET 1.5 – 41k /2ltr – 36k carbs . Stls 850ml 1ltr – 47k /2ltr -25k /3ltr – 15k

## Slide 4
Potential issues | Effect | Actions | Specific contact details required | RTO
Fire onsite Some staff might not know the plan or what to do | Impact to staff safety Impact to environment (emissions and soot) Impact to production Potential destruction of stock and consequent impact to Customer service | Follow Fire procedures as expressed in the DEP and conduct appropriate FRAs Assess likelihood of environmental emission impact Once all staff are safe, alert neighbours Watch out for potential damage to neighbouring properties – EE – or vice versa Alert the Risk Team | Neighbouring sites (detail in DEP) Environment Agency: David Rushton 02030259016 Fire Brigade: 999 East Ham Fire Station: 02085551200 | RTO: Dependent on Fire Brigade Ongoing actions: We have a relationship with LFB – ensure this is a continuous item not just annual Conduct annual review/update/exercise of DEP including Fire response procedures Conduct Fire Alarm tests annually Maintain Sprinkler systems and Automatic Fire detection
Fire

## Slide 5: Major effluent leak/drainage
Possible cause | Effect | Outline Recovery & Continuity Plan | Specific contact details required | RTO
1) Broken pipe underground Possible internal drain problem – gone external Vandalism 2) Leak into Holding pit – eg Tanker of Orange Juice 3) Failure of ability to discharge process effluent through the ETP It is considered very unlikely for a vessel that is large enough to overwhelm the Holding Pit to be ruptured. Eg: a HCL tanker of 30,000ltrs crashing and rupturing, there would still be excess capacity in the Holding Pit | 1)Potential for groundwater contamination Surface leak would go into surface water drain with potential for environmental contamination (Site is surrounded by industrial units on 2 sides / Greenway (Council sewer) on 2 sides. No nearby watercourses or nature reserves/protected environments.) 2)Any leak into the Holding Pit would be captured. Holding Pit is very large 128,000ltr and rarely more than 20% full. 3) A large build up of process effluent potentially breaching the on-site capacity of 288m³. Any Environmental leak would have a Reputational risk | What’s the plan? 1) Contact EA and alert to potential of ‘untreated release’ and advise on next steps Contact Thames Water Escalate internally at Britvic Stop discharge – potential to reroute into effluent/trade to treat. If the liquid was of a high concentration might have to hold and impact production. 2) Holding pit has very large volume: If required we could initiate pumping and transfer from Holding to Effluent – would have to measure acidity 3) Production to be informed to stop batch make up on all lines and CIP (lines to continue to produce) and escalation raised to Managers. If the process effluent cannot be contained within the site capacity Production lines will be stopped. In addition water treatment process such as de-alk regens, carbon bed backwash and cleaning process will also be stopped. Arrangement for tanker to remove waste water to be implemented until the situation is resolved. Please refer to Containment tab on R61 Response Tool for tank & bund capacities. | Section 5 form for EA Drainage specialists – Dynarod: 03332422178 Escalate to Risk Team Thames Water: 08003169800 | If we have to transfer a large volume into effluent- this would impact production by impacting volume removed off site 70cubes effluent from 200cubes per/h. However this is considered unlikely given capacity of Holding Pit Further actions: No bladders and no Enviro valves at site. Site to investigate potential and cost of installing. Owner: Vinnie Gallo SEM NOTE: Drains are vetted every 5 yrs by law Potential benefit for installation of bladders and emergency stops for discharge Robust HACCP plans and intensive Site security apparatus in place to prevent unauthorised access

## Slide 6: Major Flooding
Possible cause | Effect | Outline Recovery & Continuity Plan | Specific contact details required | RTO
1)Rain/River www.gov.uk.checkflooding Suggests that site is a very low Flood risk. Never previously effected by flooding. 2) Sprinkler failure – Fire water 3)Torrential rain and roof leaks | Potential impact to plant rooms – electrical issue Water ingress in building could damage equipment Slip hazard for staff Very worst case: Holding pit could become overwhelmed leading to contaminated water across site Potential environmental impact if large enough volume of water floods 2) Fire suppression isolated Potential damage to package and material stores | **Member of Floodlines Warning direct, 3 stage warning system Key actions: People safety – is it safe to get people off site – otherwise get them to the canteen Contact EA if potential for environmental impact Isolate critical equipment – look to shut down the electric asap Early assessment of Holding Pit capacity impact Utilise cleaning company to remove silt and clean residue Engineers to assess for damage from motors and re-start 2) Isolate the supply Clean up involving multiple people , drains cant handle water Try and cover/protect critical electrics Dry out panels using heaters Phase re-switch on and monitor panels Understand spare parts holding Check packaging and materials | Britvic Beckton Service Engineers: Martin Campbell: 07841511441 Dan Meechan: 07808097831 Richard Thorpe: 07921113320 QBE/Risk team: Peter Holmes: 07808098023 Thames Water: 08003169800 Environment Agency: 0800807060 Cleaning Company ISS: George Thatcher: 07725900601 | NB: At Leeds and FLT driver struck a 6” main. Flooding does happen RTO: 1hr for inspection post soaking Further actions: Update and review Beckton Flood plan annually

## Slide 7: Loss of access
Possible cause | Effect | Outline Recovery & Continuity Plan | Specific contact details required | RTO
Eg: Truck crash on Roding Road 2 entry gates to site so could utilise 1 but would slow things down | 110 ESL trucks coming on/off site everyday If both entrances blocked, could we continue production? Until exhausted materials – c24hrs Capacity to load onto trucks onsite, - potentially half a day People cant get onto site and materials and goods cant get on and off Staff would not be able to drive off site, limited parking in local area. 2hr stay limit at Asda etc | Emergency services – initiate road clearance Production: Understand line priorities for last bit of production Shut lines down in a clean manner to facilitate swift start SOM to escalate to Nigel P and he would trigger network execution to contact incoming Site to contact staff not to come in. Team Leaders know number of members and ability to use MyHR | Numbers required Demand & Supply Planning: Ben Tootell: 07834962966 Chief Supply Officer: Nigel Paine: 07808098426 Britvic Network execution Shaun Bye: 07808098676 Police: 999 ISS – to ensure ongoing security George Thatcher: 07725900601 | 

## Slide 8: Protesters shutting down site
Possible cause | Effect | Outline Recovery & Continuity Plan | Specific contact details required | RTO
Protesters shut down the site | Could shut down production Protesters glued to machinery Negative press/Reputational Impact | Internally there are no areas that need card access Response? Restrict access, barriers down, but protesters could easily get into site quickly. Call the police and follow their instruction Attempt to restrict access to key areas Do not man handle protestors Try and lock down parts shed Alert Risk team asap due to negative comms potential | Police: 999 Britvic Risk Team Peter Holmes: 07808098023 Britvic Corporate Communication: Stephanie Macduff Duncan: 07808097680 | If police are called – once they deem safe