WRM

wrm-ltd.co.uk

01943 468138

Fire Prevention Plan

v2.0

Environmental and sustainability solutions provided to

Advanced Demolition Limited

WRM-LTD.CO.UK

This report was prepared by Walker Resource Management Ltd (WRM’) within the terms of its engagement and in direct response to a scope of services. This report is strictly limited to the purpose and the facts and matters stated in it and does not apply directly or indirectly and must not be used for any other application, purpose, use or matter. In preparing the report, WRM may have relied upon information provided to it at the time by other parties. WRM accepts no responsibility as to the accuracy or completeness of information provided by those parties at the time of preparing the report. The report does not take into account any changes in information that may have occurred since the publication of the report. If the information relied upon is subsequently determined to be false, inaccurate, or incomplete then it is possible that the observations and conclusions expressed in the report may have changed. WRM does not warrant the contents of this report and shall not assume any responsibility or liability for loss whatsoever to any third party caused by, related to, or arising out of any use or reliance on the report howsoever. No part of this report, its attachments or appendices may be reproduced by any process without the written consent of WRM. All enquiries should be directed to WRM.

| Document Title | Fire Prevention Plan |  |
| --- | --- | --- |
| Client | Advanced Demolition Limited |  |
| Revision | v2.0 |  |
| Date | 18/12/2025 |  |
| Document Reference | EPR-B03 |  |
| Project Reference | 1496/J05 |  |
| Author: Ellen MacCallum |  | Reviewer: Graeme Kennett |

Copyright ©

All material on these pages, including without limitation text, logos, icons and photographs, is copyright material of Walker Resource Management Ltd (WRM). Use of this material may only be made with the express, prior, written permission of WRM. This document was produced solely for use by the named client to whom the document refers. The methodology (if any) contained in this report is provided to you in confidence and must not be disclosed or copied to third parties without the prior written agreement of WRM. Disclosure of that information may constitute an actionable breach of confidence or may otherwise prejudice our commercial interests.

| Revision | Details | Date |
| --- | --- | --- |
| 0.1 | Initial Draft | 20/06/2025 |
| 1.0 | First Issue | 27/06/2025 |
| 2.0 | Second issue | 08/01/2026 |

Revision Log

CONTENTS

Contents

1.0	Introduction	1

1.1	FPP availability	2

1.2	Roles and responsibilities	2

1.3	Purpose	2

1.4	Scope	3

1.5	Objectives	3

2.0	The site	4

2.1	General location	4

2.2	Site buildings	4

2.3	Sensitive receptors	5

3.0	Combustible Waste Types	24

3.1	Combustible held waste on the site	24

3.2	Combustible waste produced on site	24

4.0	Using this Fire Prevention Plan	25

4.1	Fire Prevention Plan location and staff awareness	25

4.2	Testing the Fire Prevention Plan and staff training	25

4.3	Fire drills	26

5.0	Fire Prevention Plan Contents	28

5.1	Fire risk overview	28

5.2	Site plan	30

5.3	Sensitive receptor plan	30

6.0	Manage Common Causes of Fire	31

6.1	Site security measures	31

6.2	Fencing	31

6.3	CCTV	31

6.4	Plant and equipment	31

6.5	Fire prevention measures fitted to equipment and shift end procedures	32

6.6	Electrical faults including damaged or exposed electrical cables	32

6.7	Discarded smoking materials	32

6.8	Hot works safe working practices	33

6.9	Use of industrial heaters	33

6.10	Hot exhausts and engine parts	33

6.11	Fire watch procedures	34

6.12	Ignition sources	34

6.13	Batteries	34

6.14	Lithium-ion batteries	34

6.15	Persistent Organic Pollutants	35

6.16	Batteries in End-of-life Vehicles (ELVs)	35

6.17	Leaks and spillages of oils and fuels	35

6.18	Build-up of loose combustible waste, dust and fluff	35

6.19	Reactions between wastes	36

6.20	Waste acceptance and deposited hot loads	36

6.21	Hot and dry weather	37

6.22	Action if heating is detected	38

6.23	Weather monitoring	39

6.24	Fire detection and suppression	39

7.0	Prevent Self-Combustion	40

7.1	Preventing self-combustion	40

8.0	Monitor and Control Temperature	42

8.1	Auto-suppression within the building	43

8.2	Certification for the systems	44

8.3	Detection of a fire during operational hours	44

8.4	Detecting of a fire outside of operational hours	44

9.0	Manage Waste Piles	46

9.1	Storing waste materials in their largest form	46

9.2	Maximum pile sizes for the waste held on site	46

10.0	Where Maximum Pile Sizes do not Apply	47

10.1	Whole ELVs	47

10.2	Waste stored in containers	47

10.3	Compost production	47

11.0	Prevent Fire Spreading	48

11.1	Separation distances	48

11.2	Fire walls and bays	49

12.0	Fire Quarantine Area (Fqa)	50

12.1	Area	50

12.2	Quarantine area location and size	51

12.3	How to use the quarantine area if there is a fire	51

12.4	Procedure to remove material stored temporarily if there is a fire	51

12.5	Purpose:	51

12.6	Site manager and emergency services assessment	52

13.0	Detecting Fires	53

13.1	Detection system in use	53

13.2	Detecting of a fire outside of operational hours	53

13.3	Detection of a fire during operational hours	53

13.4	Certification for the systems	54

14.0	Suppressing Fires	55

14.1	Auto-suppression within the building	55

15.0	Firefighting Techniques	56

15.1	Active firefighting	56

15.2	Small fires	56

15.3	Uncontainable small fire or large fire	57

16.0	Water Supplies	58

16.1	Available water supply on site	58

17.0	Managing Fire Water	59

17.1	Assessing risks to groundwater from fire water	59

18.0	During and After an Incident	60

18.1	During an event	60

18.2	Post event procedures	60

18.3	Making the site operational after a fire	61

18.4	Follow up action	62

Appendix A – Fire Safety Management Plan	63

Appendix B – Fire Emergency Procedure	64

Table 2-1: Premises details	4

Table 2-2: Sensitive receptor table	5

Table 4-1: Training schedules	25

Table 4-2: Emergency contact list	27

Table 5-1: Fire risk overview from on-site activities	28

Table 6-1: Machinery list	32

Table 8-1: Factors influencing heating rate	42

Table 9-1: Combustible waste storage area details	46

Table 11-1: Fire prevention and control process	48

Table 16-1: Water supply calculation	58

# Introduction

This Fire Prevention Plan (FPP)  follows the latest Fire prevention plans: environmental permits - GOV.UK from the Environment Agency (EA) and details the required mitigation and management methods to prevent a fire of combustible materials stored at the Advanced Demolition Limited (ADL) site at Hoddesdon in Hertfordshire.

This FPP has been prepared to mirror the contents of the guidance to allow for ease of assessment and for users of this document to readily locate the specific information and on-site provisions relating to each topic. It identifies measures to be employed to reduce the likelihood of fires at the site. In addition, the plan identifies measures to be employed in the event of a fire to limit the damage caused to the environment or human health.

As such, and in accordance with EA guidance, the objectives of this FPP are to:

- The likelihood of a fire starting is minimised

- A fire will aim to be extinguished within 4 hours

- The outbreak and/or spread of fire will be minimised by the measures contained within this FPP.

- The impact of the effects of fire on people, the environment and other businesses are minimised.

This FPP forms part of the management system and working plan for the site. It is prepared for use as a standalone document such that all staff can easily refer to any information or operational requirements that relate to the prevention of fire or the procedures that in in place in the event of a fire.

The existence and location of the FPP will be notified to all staff and will be readily accessible, in both hard and electronic copy, at all times, including during an incident and a further copy with Hertfordshire Fire and Rescue (HFRS). All staff will be trained on the contents and requirements of the FPP (suitable to their role) and site inductions will include a summary of the FPP and notices of its location.

ADL will test the provisions of this FPP annually to ensure that the measures are effective and remain applicable to the operations on-site. Such tests may take the form of physical drills or desk-based assessments as relevant to the element of this FPP that is under test. The nature of each test, the results and appropriate actions (including where no action is required) will be maintained for inspection by the EA, on request.

Under current fire safety legislation, a responsible person must carry out, or appoint a competent person to carry out, a suitable and sufficient assessment of the risks of fire to employees and others who may be affected by the site. A fire risk assessment will be carried out on an annual basis, or in the event of any substantive change to operations on site.

FPP availability

This FPP will be made available to:

- All staff

- Site visitors

- Contractors working at the site

ANY CHANGES TO OPERATIONS THAT WILL IMPACT UPON THE FPP MUST BE APPROVED BY THE ENVIRONMENT AGENCY PRIOR TO IMPLEMENTATION.

Roles and responsibilities

Advanced Demolition Limited (ADL), ‘the operator’, has the overall responsibility for ensuring these procedures are adhered to. Please see section 1.2.

As with wider Health and Safety issues, overall responsibility for fire safety and prevention lies with the senior management team of the operator. Responsibility for FPP implementation rests with the Board and is implemented through the control of the Managing Director (MD).

Purpose

The primary purpose of this FPP is to guide staff and contractors in the prevention of fire. It will also confirm the actions to be taken in the event of fire to minimise any impact on the environment and to control the fire where appropriate. This FPP will be distributed to the Fire and Rescue Service (FRS) and be available at the site in the event of a fire to aid with firefighting.

Scope

This FPP is a standalone document that also forms part of the EMS with the individual fire emergency procedures for the site forming part of the FPP and has been prepared in accordance with the latest EA guidance.

It relates to the storage of combustible waste, both pre-and post-treatment, at the site. All waste materials stored at the site have been considered in this plan.

The measures prescribed in the EA-approved FPP guidance and templates will be regularly reviewed to ensure that operations on site remain compliant. The review will also ensure that the approved document still conforms to the latest version of the guidance.

Objectives

The fire prevention measures in this document have been designed to meet these 3 objectives:

- minimise the likelihood of a fire happening

- aim for a fire to be extinguished within 4 hours

- minimise the spread of fire within the site and to neighbouring sites

The ADL FPP will also meet the objectives by ensuring that awareness and training is provided to all staff and contractors and putting in place and that using the fire prevention measures will reduce the likelihood of a fire happening, which is the highest priority to prevent environmental harm.

All personnel will similarly understand that should these measures fail, the EA may take enforcement action on the site.

# The site

Table 2-1: Premises details

| Premises Particulars |  |
| --- | --- |
| Premises name: Advanced Demolition Limited Address: Advanced Demolition Limited Pindar Road, Hoddesdon, EN11 0BZ Tel no: TBC Site opening times: Monday to Friday 06:00 – 17:00 Saturday 06:00-12:00. | Activities undertaken: The permit authorises the operation of a waste facility transferring and treating a range of non-hazardous wastes. |
|  | Owner/employer/person in control of the workplace: Site Manager – Billy Marchant |

General location

The site is situated on Pindar Road off Essex Road which is adjoined to the A1170 and is approximately 1.2km northeast of Hoddesdon town centre. It is surrounded by mixed-use industrial and commercial developments with the nearest residential receptor located approximately 170m west of the site. The New River runs along approximately 150m to the west of the site.

Site buildings

On site there are the following buildings including:

- Site office

- workshop,

## Sensitive receptors

The site is located approximately.

- 900m southwest of Rye Meads SSSI

Other sensitive receptors are listed below in table 2-2.

Figure 2-1: Wind rose (Meteoblue)

Table 2-2: Sensitive receptor table

| Receptor | Land Use | Approximate distance from the site (m) | Grid Reference (Easting, Northing) |
| --- | --- | --- | --- |
| SR01 – Industrial Property within Industrial Estate | Industrial | 60m | 538062, 209010 |
| SR02 – Industrial Property within Industrial Estate | Industrial | 66m | 538052, 209117 |
| SR03 – Industrial Property within Industrial Estate | Industrial | 21m | 538135, 209112 |
| SR04 - Industrial Property within Industrial Estate | Industrial | 31m | 538110, 209126 |
| SR05 - Industrial Property within Industrial Estate | Industrial | 50m | 538156, 209136 |
| SR06 - Industrial Property within Industrial Estate | Industrial | 60m | 538131, 209151 |
| SR07 - Industrial Property within Industrial Estate | Industrial | 70m | 538082, 209168 |
| SR08 - Industrial Property within Industrial Estate | Industrial | 83m | 538172, 209165 |
| SR09 - Industrial Property within Industrial Estate | Industrial | 110m | 538162, 209192 |
| SR10 - Industrial Property within Industrial Estate | Industrial | 126m | 538121, 209217 |
| SR11 - Industrial Property within Industrial Estate | Industrial | 154m | 538141, 209249 |
| SR12 – Industrial Property within Industrial Estate | Industrial | 140m | 538202, 209211 |
| SR13 – Industrial Property within Industrial Estate | Industrial | 180m | 538194, 209265 |
| SR14 - Industrial Property within Industrial Estate | Industrial | 210m | 538215, 209283 |
| SR15 - Industrial Property within Industrial Estate | Industrial | 240m | 538225, 209324 |
| SR16 - Industrial Property within Industrial Estate | Industrial | 276m | 538232, 209346 |
| SR17 - Industrial Property within Industrial Estate | Industrial | 264m | 538274, 209310 |
| SR18 - Industrial Property within Industrial Estate | Industrial | 291m | 538268, 209343 |
| SR19 - Industrial Property within Industrial Estate | Industrial | 309m | 538283, 209358 |
| SR20 - Industrial Property within Industrial Estate | Industrial | 340m | 538306, 209383 |
| SR21 - Industrial Property within Industrial Estate | Industrial | 50m | 538221, 209093 |
| SR22 - Industrial Property within Industrial Estate | Industrial | 125m | 538236, 208967 |
| SR23 - Industrial Property within Industrial Estate | Industrial | 140m | 538294, 209053 |
| SR24 - Industrial Property within Industrial Estate | Industrial | 161m | 538312, 209091 |
| SR25 - Industrial Property within Industrial Estate | Industrial | 174m | 538322, 209116 |
| SR26 - Industrial Property within Industrial Estate | Industrial | 195m | 538340, 209130 |
| SR27 - Industrial Property within Industrial Estate | Industrial | 218m | 538352, 209155 |
| SR28 - Industrial Property within Industrial Estate | Industrial | 235m | 538363, 209180 |
| SR29 - Industrial Property within Industrial Estate | Industrial | 260m | 538377, 209197 |
| SR30 - Industrial Property within Industrial Estate | Industrial | 275m | 538384, 209221 |
| SR31 - Industrial Property within Industrial Estate | Industrial | 303m | 538396, 209245 |
| SR32 - Industrial Property within Industrial Estate | Industrial | 320m | 538398, 209277 |
| SR33 - Industrial Property within Industrial Estate | Industrial | 270m | 538350, 209278 |
| SR34 - Industrial Property within Industrial Estate | Industrial | 215m | 537940, 208927 |
| SR35 - Industrial Property within Industrial Estate | Industrial | 289m | 537915, 208838 |
| SR36 - Industrial Property within Industrial Estate | Industrial | 371m | 537897, 208767 |
| SR37 - Industrial Property within Industrial Estate | Industrial | 170m | 538025, 208933 |
| SR38 - Industrial Property within Industrial Estate | Industrial | 202m | 538086, 208919 |
| SR39 - Industrial Property within Industrial Estate | Industrial | 265m | 538006, 208867 |
| SR40 - Industrial Property within Industrial Estate | Industrial | 310m | 537959, 208812 |
| SR41 - Industrial Property within Industrial Estate | Industrial | 327m | 537973, 208778 |
| SR42 - Industrial Property within Industrial Estate | Industrial | 350m | 537981, 208725 |
| SR43 - Industrial Property within Industrial Estate | Industrial | 148 | 538081, 208923 |
| SR44 - Industrial Property within Industrial Estate | Industrial | 160 | 538115, 208865 |
| SR45 - Industrial Property within Industrial Estate | Industrial | 339 | 538076, 208719 |
| SR46 - Industrial Property within Industrial Estate | Industrial | 425 | 537939, 208669 |
| SR47 - Industrial Property within Industrial Estate | Industrial | 414 | 537994, 208672 |
| SR48 - Industrial Property within Industrial Estate | Industrial | 490 | 537966, 208595 |
| SR49 - Industrial Property within Industrial Estate | Industrial | 550 | 537972, 208521 |
| SR50 - Industrial Property within Industrial Estate | Industrial | 460 | 537900, 208662 |
| SR51 - Industrial Property within Industrial Estate | Industrial | 507 | 537898, 208609 |
| SR52 - Industrial Property within Industrial Estate | Industrial | 545 | 537893, 208548 |
| SR53 - Industrial Property within Industrial Estate | Industrial | 551 | 538031, 208491 |
| SR54 - Industrial Property within Industrial Estate | Industrial | 392 | 538116, 208605 |
| SR55 - Industrial Property within Industrial Estate | Industrial | 382 | 538180, 208686 |
| SR56 - Industrial Property within Industrial Estate | Industrial | 322 | 538219, 208744 |
| SR57 - Industrial Property within Industrial Estate | Industrial | 225 | 538216, 208834 |
| SR58 - Industrial Property within Industrial Estate | Industrial | 281 | 538277, 208813 |
| SR59 - Industrial Property within Industrial Estate | Industrial | 201 | 538286, 208920 |
| SR60 - Industrial Property within Industrial Estate | Industrial | 247 | 538326, 208888 |
| SR61 - Industrial Property within Industrial Estate | Industrial | 215 | 538368, 208968 |
| SR62 - Industrial Property within Industrial Estate | Industrial | 226 | 538378, 209000 |
| SR63 - Industrial Property within Industrial Estate | Industrial | 243 | 538387, 209069 |
| SR64 - Industrial Property within Industrial Estate | Industrial | 256 | 538400, 209093 |
| SR65 - Industrial Property within Industrial Estate | Industrial | 294 | 538442, 209061 |
| SR66 - Industrial Property within Industrial Estate | Industrial | 322 | 538470, 209036 |
| SR67 - Industrial Property within Industrial Estate | Industrial | 306 | 538446, 209019 |
| SR68 - Industrial Property within Industrial Estate | Industrial | 289 | 538461, 209119 |
| SR69 - Industrial Property within Industrial Estate | Industrial | 336 | 538475, 209197 |
| SR70 - Industrial Property within Industrial Estate | Industrial | 370 | 538480, 209250 |
| SR71 - Industrial Property within Industrial Estate | Industrial | 390 | 538458, 209311 |
| SR72 - Industrial Property within Industrial Estate | Industrial | 395 | 538454, 209364 |
| SR73 - Industrial Property within Industrial Estate | Industrial | 387 | 538453, 209458 |
| SR74 - Industrial Property within Industrial Estate | Industrial | 450 | 538453, 209515 |
| SR75 - Industrial Property within Industrial Estate | Industrial | 414 | 538392, 209465 |
| SR76 - Industrial Property within Industrial Estate | Industrial | 515 | 538463, 209537 |
| SR77 - Residential Properties on New River Close | Residential | 181 | 537928, 209114 |
| SR78 - Residential Properties on New River Close | Residential | 205 | 537942, 209142 |
| SR79 - Residential Properties on Marsh Close | Residential | 215 | 537908, 209080 |
| SR80 - Residential Properties on Stortford Road | Residential | 265 | 537864, 209118 |
| SR81 - Residential Properties on Stortford Road | Residential | 305 | 537825, 209151 |
| SR82 - Residential Properties on Stortford Road | Residential | 193 | 537998, 209225 |
| SR83 - Residential Properties on Stortford Road | Residential | 217 | 538065, 209289 |
| SR84 - Residential Properties on Stortford Road | Residential | 245 | 538108, 209333 |
| SR 85 - Residential Properties on Stortford Road | Residential | 350 | 538211, 209432 |
| SR86 – Residential Properties on Gladstone Road | Residential | 260 | 537900, 209346 |
| SR87 – Residential Properties on River Avenue | Residential | 372 | 537812, 209315 |
| SR88 - Residential Properties on Cranborne Road | Residential | 290 | 537993, 209398 |
| SR89 – Residential Properties on Aylsham Road | Residential | 370 | 538092, 209451 |
| SR90 – Residential Properties on Ivy Terrace | Residential | 395 | 538162, 209494 |
| SR91 – Residential Properties on Essex Road | Residential | 500 | 537644, 209168 |
| SR92 – Recreational Ground off Rye Road | Residential | 490 | 537640, 209366 |
| SR93 – Residential Properties on Rye Road | Residential | 505 | 537737, 209517 |
| SR94 – Residential Properties on Lilac Road | Residential | 669 | 537712, 209621 |
| SR95 – Residential Properties on Hawthorn Road | Residential | 761 | 537718, 209730 |
| SR96 – Residential Properties on Whitley Road | Residential | 806 | 537874, 209842 |
| SR97 – Residential Properties on Crossfield Road | Residential | 600 | 537886, 209658 |
| SR98 – Residential Properties on Walton Road | Residential | 594 | 538029, 209684 |
| SR99 – Residential Properties on Haward Road | Residential | 660 | 538105, 209750 |
| SR100 – Residential Properties on Rumbold Road | Residential | 555 | 538133, 209689 |
| SR101 – Industrial Property off Ratty’s Lane | Industrial | 375 | 538506, 208868 |
| SR102 – Power Station off Ratty’s Lane | Industrial | 600 | 538748, 209046 |

# Combustible Waste Types

Combustible held waste on the site

Permitted wastes are limited to non-hazardous wastes with a total quantity of waste that can be accepted at the site under the permit conditions will be less than 75,000 tonnes per year. A full list of the waste types accepted is given in the permit and the Waste Acceptance Procedure (EPR-OP01) and includes:

- Mixed skip wastes

- Inert wastes

- Paper, cardboard and/or plastics

- Rags and textiles

- Scrap metals contaminated or mixed with other waste such as oils or plastics

- Mixed waste containing any combustible wastes

- Wood

Combustible waste produced on site

- Oily rags

Produced on site due to ongoing plant maintenance and are stored in secure containers awaiting removal off site to an authorised facility.

- Office waste (general waste)

Minimal quantities of office waste are stored in the designated bins outside of the office away from other flammable substances and combustible wastes. These bins are always accessible.

- Plant maintenance wastes

Oil waste is produced as part of plant maintenance activity only and is not accepted inwards as waste imported waste stream. All oil wastes are stored appropriately in bunded containers and despatched to appropriately permitted facilities. Empty grease gun cartridges are placed within a covered receptacle awaiting collection and despatch from site.

# Using this Fire Prevention Plan

Fire Prevention Plan location and staff awareness

The Fire Prevention Plan (FPP) is a standalone document that forms part of the Environment Management System (EMS) for the site. It sets out the fire prevention measures and procedures that have been put in place and will be followed on site.

The FPP is kept along with the Fire Logbook in a prominent position in the office to be immediately accessible by any member of staff when required.

As part of the regular training all staff know where the FPP is located including during an incident.

All contractors working on site are inducted so that they understand the contents of the FPP so that they know what they must do:

- To prevent a fire occurring; and

- During a fire if one breaks out

Testing the Fire Prevention Plan and staff training

Regular exercises will be held to test how well the FPP plan works and make sure that staff, including security staff, understand what to do and the procedures to follow. The FPP forms a part of the toolbox talks.

These exercises are held at least annually, with the date, times and response recorded.

Table 4-1: Training schedules

| Personnel | Action |
| --- | --- |
| All new site staff and contractors (and existing site staff and contractors when the latest FPP is released) | To be trained on the FPP and ERP. |
| Existing site staff and contractors | To be trained on the FPP and ERP on 1st July and every 6 months thereafter. |
| Site Manager (SM) to carry out fire drill and test FPP and ERP | Every 3 months after release. |
| Site Manager | Annual review on 1st July each year or earlier in response to an incident or change on site. |

Any improvements required to the Emergency Response Plan (ERP) will be made without delay, and a new version replaced in the FPP grab pack and staff refresher training will be held on the updated sections.

Regular checks are made to ensure the latest version is available with previous versions removed and recycled.

Fire drills

Regular fire drills are carried out on site as per article 15 of The Regulatory Reform (Fire Safety) Order 2005 to ensure evacuation times are acceptable and that site staff remain informed of evacuation procedures. The operator may also appoint and train fire marshals on site, to aid in the above.

Fire drills (as a minimum, one fire drill per year as required by the latest Fire safety: guidance for those with legal duties - GOV.UK) are held on site and details are incorporated into WWM written drill procedure. Records are kept of attendance of each fire drill and are carried out using the following methods:

Inform all employees of that a fire drill is going to happen, providing them with specific details and also firmly letting them know their participation is required.

Nominate observers (if necessary) to assess the fire drill, paying attention to the appropriateness of actions, the behaviour of employees and any problems which may arise during the drill.

Additionally, should any visitors be present at the time of the fire drill, they will also be informed.

Table 4-2: Emergency contact list

| Regulatory Bodies/Authorities/Security |  |
| --- | --- |
| Body | Contact No. |
| Environment Agency (Welwyn Garden City Office) | 03708 506 506 |
| Environment Agency (Emergency) | 0800 80 70 60 |
| Health and Safety Executive | 01256 404000 |
| Anglian Water (Emergency) | 03457 145 145 |
| Borough of Broxbourne (Switchboard) | 01992 785555 |

# Fire Prevention Plan Contents

Fire risk overview

This FPP sets out the measures put in place to reduce the risk of a fire breaking out.

It identifies all the possible causes of a fire at the site and sets out the measures ADL have in place to address those fire risks. It considers any additional fire risks posed by both:

- Planned events – such as planned downtime

- Reasonably foreseeable unplanned events – such as temporary site closure

Table 5-1: Fire risk overview from on-site activities

| Activity/Equipment | Risk presented | Control measure | Section |
| --- | --- | --- | --- |
| Hot works | Hot fragments of metal could cause fire; incorrectly handled or stored gas equipment could leak and explode | Carried out in designated area away from combustible material stockpiles, all equipment (gas bottles etc.) fully disconnected and stored correctly when not in use. Fire watch carried out for 1 hour at end of day. Hot Works Permit in place which includes a fire risk assessment. | 6.5 |
| Arson | Trespassers or vandals could start a fire onsite if access is gained. | Whole site monitored CCTV in place. | 6.1 |
| Smoking | Discarded cigarettes could cause fire. | Strict non-smoking policy in place for all areas on the entire site. | 6.4 |
| Fuelling of vehicles and machines | Any fuel or oil spilled during fuelling would produce a puddle of highly combustible material. | Fuelling of mobile plant takes place away from the storage and processing areas. | 6.12 |
| Mobile plant onsite | Dust build-up on hot areas could start a fire, oil or fuel leaks could cause puddles of combustible material. | Strict daily check procedures are in place for machinery. Machines are parked in the designated area away from combustible material when not in use. | 6.2 6.8 |
| Electrical equipment | If not tested or functioning properly, sparks could cause a fire. | The electrical equipment on-site has been installed and certified by a suitably qualified electrician. Regular safety checks and daily inspections are recorded in the site diary. All electrical and electronic equipment is PAT tested by an external contractor and all three-phase electrical equipment is subject to an inspection by a trained person before use. | 6.3 |
| Industrial heater use | Improperly vented/ dusty heaters present ignition risk, heaters left on unattended may overheat or malfunction and ignite | Use of industrial heaters is not permitted on site. | 6.6 |
| Waste acceptance | Incompatible waste types may come into contact with each other and cause a reaction resulting in fire. | Strict pre-waste and waste acceptance procedures categorise the waste inputs prior to storage at the site. Incompatible waste types rejected from the site. | 6.15 |
| Storage of waste | Waste stored over time may accumulate heat if material isn’t monitored regularly | Strict storage procedures are in place to ensure a FIFO system is maintained and stockpile sizes are controlled. Stockpile sizes are checked daily. | Table 7-3 |
| Housekeeping/build-up of waste or dust around plant | Dust/waste around hot components of equipment or electrics may catch light if not cleared regularly | The daily checks carried out and recorded include checking for any build-up of wastes and thorough housekeeping is part of the Site Manager’s role profile. | 6.13 |
| Dust/fluff build-up around site | Flammable dusts and fluff around site present an extra risk of fire spreading and risk of ignition from various sources (including heat build-up from sunlight) | Dust build-up regularly removed. | 6.13 6.7 |
| Plant maintenance | Plant that is poorly maintained is at higher risk of electrical issues or heat build-up and combustion around gearbox/ hydraulic components (e.g., oil leaks) | Each item of equipment is given a pre-use inspection, and all machines have a daily inspection checklist that is completed each morning. All defects are reported and rectified immediately. | - |
| Repairs and maintenance/servicing | Use of cutting tools may produce sparks that could ignite combustible materials, servicing can result in oil spillages that may combust. | If plant/equipment is mobile, then repairs/servicing are carried out away from combustible materials and any spills cleared up immediately. Any fixed plant repairs are carried out in a temporary Safe Zone with barriers and a dynamic risk assessment. Any mobile plant servicing will be undertaken in the vehicle parking area. Where an oil change is required, this will be undertaken by qualified engineers using the appropriate equipment with easy access to spill kits. | - |

Site plan

The site plan is kept updated with any changes to site operations.

Sensitive receptor plan

Although less likely to change over time, the sensitive receptor plan is kept updated with any changes to site operations.

# Manage Common Causes of Fire

Site security measures

Security measures are in place to prevent the potential for arson. There are no Public Rights of Way (PRoW), or any other form of legitimate pedestrian access to the site.

Fencing

The site has secure fencing along all boundaries, and the boundary is regularly inspected with all inspections recorded. Access to the site is restricted to the lockable, 2.2m high steel gates which are only opened to allow individual access/egress and are kept locked outside of business hours.

Any defects are repaired by the end of each working day where possible.

CCTV

The integrated CCTV system has multi-lens cameras that show both panoramas and detailed, zoomed-in views of the site at the same time. The facility is continually manned during operational hours, and CCTV is provided which is accessible remotely and monitored by the operator and security provider out of hours. Routine security patrols are carried out on a regular, randomised basis. These checks are not limited to fire detection but also investigating any signs of unlawful entry.

Where signs of entry are observed, security personnel contact the Site Manager without delay.

Plant and equipment

All machinery is serviced and maintained to manufacturer standards, who leave visit reports of any work carried out.

A fire extinguisher is kept in the cab of each item of mobile plant which also has a battery isolation switch to disconnect the battery when the item of equipment is not in use, i.e., will prevent the battery causing a spark when the site is closed.

When not in use plant and equipment is parked in a designated area.

Table 6-1: Machinery list

| Item | Manufacturer | Model number |
| --- | --- | --- |
| Loading shovel | JCB | 436 |

Fire prevention measures fitted to equipment and shift end procedures

- Mobile plant equipped with individual fire extinguishers.

- Mobile plant equipped with approved exhaust spark arrestors.

- All machines subject to an end of working day inspection in the vehicle parking area.

- Designated parking areas for mobile plant which are away from waste storage areas.

- Plant and equipment is lubricated, where appropriate, and cleaned down.

- Any accumulating debris (fines) under plant removed.

- Electrical power is shut-off and locked-off at shift end.

- Following clean down a fire watch check is undertaken prior to shift end.

Electrical faults including damaged or exposed electrical cables

The risk of electrical fault is minimised by having all electrics on site certified by a full-time electrician. There is a documented maintenance schedule in place that conforms to The Electricity at Work Regulations 1989.

Any potential ignition sources from suspected electrical faults will be isolated and an electrical engineer contacted immediately to rectify the situation. Where possible, staff will immediately remove any stored wastes from the vicinity of the fault area or cable traverse if safe to do so.

Discarded smoking materials

Smoking on site policy states that smoking is not permitted within the site boundary, including site visitors/haulage drivers, and this safety rule is strictly enforced by management.

Hot works safe working practices

Hot work such as welding, grinding, cutting and similar activities may be undertaken at the site in relation to repair activities. All such works will be undertaken in accordance with a Hot Works Procedure which includes:

- A permit to work (PTW) system in place to ensure appropriate controls during and after any hot work.

- Fire extinguishers present at the point of any hot work so that they can be used immediately should a fire occur. Extinguishers will be stationed adjacent to the pathway of escape from the work area and operators undertaking hot work will be trained in the use of fire extinguishers.

- Sources of combustible material removed from the area where hot work is taking place before work commences. Where this is not possible then such materials, including mobile plant hydraulic lines, will be covered by a fire blanket/screen and/or damped down with water before work commences.

- A fire watch will be present during all hot works and for 1 hour after such hot works have ceased to ensure that sparks from works are not smouldering.

Use of industrial heaters

The use of industrial heaters with open heat / ignition sources such as portable electric bar heaters, paraffin heaters, space heaters etc., are strictly forbidden at the site.

Hot exhausts and engine parts

All machines operated on site are fitted with spark arrestors, as all legislation regarding the operation of a diesel engine includes a mandatory requirement to fit a tested and approved exhaust spark arrestor.

All machines are regularly inspected to ensure there is no build-up of dust on hot, mainly engine, surfaces.

Fire watch procedures

Due to the risk of undetected smouldering fires occurring, all staff are responsible for carrying out a shift end inspection on their immediate work area.

The site supervisor has additional responsibilities to ensure that each working area has been inspected at the end of the shift to ensure compliance with the fire prevention measures. Plant and machinery is switched off 1 hour before the site is vacated with mobile plant returned to the dedicated out of hours parking point.

All staff are trained to be vigilant in terms of fire detection.

Ignition sources

There will be no naked flames, heaters or other sources of ignition within 6m of combustible and flammable materials and waste.

Hot works which may introduce such sources will be controlled as outlined in section 6.5 above.

Batteries

Batteries found in in-coming waste streams will be stored in appropriate sealed containers, located away from waste piles, until removed from site by registered waste carriers.

Lithium-ion batteries

Lithium-ion batteries have the potential to explode when damaged, punctured or overheated and are a significant potential ignition source for fires on waste sites.

Site operatives are vigilant of items that may contain Lithium-ion batteries when sorting incoming waste, any discovered will be separated and stored separately to other combustible waste types. Lithium-ion batteries will be stored in a battery storage box within the waste treatment building.

Persistent Organic Pollutants

Some waste types stored on the Site i.e. uPVC windows may contain Persistent Organic Pollutants (POPs) and are stored separately to other wastes stored on the Site.  In the event of a fire, the fire service will be informed that there are wastes containing POPs on the site and will be notified where these are stored.

Batteries in End-of-life Vehicles (ELVs)

This section does not apply as ELVs are not accepted as part of the incoming waste stream.

Leaks and spillages of oils and fuels

Fuel is stored in sealed, internally bunded tanks capable of holding 110% of its capacity and is done so in line with permitting requirements. The fuel is stored in a bunded and protected area away from waste operations outside the permitted area and away vehicle movements.

All mobile equipment and plant are inspected daily for leaks prior to operation as part of the daily checks. If there are fuel leaks from vehicles operating on site, the vehicle is quarantined and any spilt fuel absorbed using a suitable material.

Absorbent materials and fuel spill kits are stored at strategic locations at the site and contaminated material placed in a designated container for subsequent removal for disposal at a licensed facility.

Build-up of loose combustible waste, dust and fluff

Combustible residues collecting around waste storage areas can present a fire risk.  Separated waste types will be stored within bays / skips.

The storage time of combustible waste on the Site is minimised.  Stockpiles and skips will be inspected on a weekly basis to identify when all combustible waste in a storage area has been removed.  Once empty, the storage area will be cleaned to remove any residual waste / dust / fluff.  A storage area will be cleared if the area has not been cleared within the maximum storage duration.  The clearing and cleaning down of bays will be recorded.  These checks will be recorded using a Stock Rotation Form.

A weekly, recorded, review of the Stock Rotation Forms will be carried out to ensure compliance with maximum storage duration times for the waste.

Dust, loose fibres settling on hot exhausts / engines can cause fires.  Therefore, an inspection is carried out at the end of the day to ensure all mobile plant / vehicles are cool and to remove any dust build-ups.  This inspection will ensure that mobile plant is monitored for 15 minutes after shutting down to ensure it has cooled.  Mobile plant is stored outside when not in use / at the end of the day, to aid in the dissipation of any heat.

Reactions between wastes

All waste is inspected on delivery to ensure it is of a nature suitable for the permitted acceptable waste of the permit. Any waste identified as not permissible will be segregated from the incoming waste stream into the designated quarantine area.

Any potentially reactive waste types identified within a load will be separated and stored appropriately, using a quarantine area if necessary. The location of the quarantine area can be seen on the Layout Plan. Such wastes will be identified on arrival on Site during the visual inspection which is part of the waste acceptance procedure.

Waste acceptance and deposited hot loads

The following actions are taken to prevent fire arising from a hot load:

- All drivers stop at the office before entering the site.

- If the vehicle contains hot material, or suspected hot material, the vehicle will not be allowed to tip its load. Instead, it will remain stationery, and extinguishers and/or water will be used and if necessary, the fire service will be contacted.

- If a load is found to be smouldering once it has been deposited within a reception area, if deemed safe to do so, a loading shovel will be used to move the smouldering material to the quarantine area. If it is not safe to do so, the material will be tackled using an extinguisher, water and or inert material to smother the waste.

- The quarantine area is a large area in the yard that is not confined by bay walls, which allows full access to the waste.

- The operator will have water on standby before the waste is spread out as this action will introduce oxygen to covered waste which can increase the fire risk.

- The waste will be spread out using a suitable item of plant.

- The temperature of the waste will be monitored, if the waste cools down naturally, this action will be sufficient.

- If the waste requires dampening down, ADL staff will dampen the waste down with water; and

- Only after the waste has cooled down to ambient temperature (which will be dependent upon temperature of that particular day), will the waste be removed from the quarantine areas and removed from site.

- No more waste will be deposited, and all deliveries will stop until the smouldering waste has been dealt with and the Site Manager has confirmed it is cooled and no longer a fire risk.

All staff will be trained to be vigilant for hot loads. All incidents of hot loads will be recorded in the site diary

Hot and dry weather

During periods of hot and dry weather, the risk of external heating of waste materials increases. To mitigate this, ADL will implement the following:

Regular monitoring

- During hot and dry conditions (typically when daytime temperatures exceed 25°C or during prolonged dry spells), the frequency of external temperature checks at waste stockpiles will increase.

- Trained site staff will carry out visual inspections and surface temperature monitoring of all external waste piles using non-contact infrared thermometers or thermal imaging cameras, at least twice daily (morning and mid-afternoon).

Particular attention paid to:

- Sun-facing sides of stockpiles

- Darker materials that may absorb heat more readily

- Recently delivered waste

- Areas near equipment or buildings that may reflect or radiate heat

Preventative measures

- Where areas of stockpiles indicate irregular temperature increases, the area will be turned or rotated where necessary to prevent heat build-up. Alternatively, the material will be removed from site.

Action if heating is detected

If surface temperatures exceed 50°C, or if there are signs of smouldering or odours indicating decomposition:

- The area will be immediately isolated and monitored closely.

- Mechanical plant used to break apart and turn the affected material to release heat and allow it to cool.

- Water misting or controlled dousing will be used to reduce temperature without over-saturating the waste, to avoid creating runoff or affecting waste structure.

- Incident will be logged, including time, location, waste type, and actions taken.

- Where the risk of ignition or issue persists, we will contact the Fire and Rescue Service will be contacted and notification to the Environment Agency, following the incident reporting procedure.

Weather monitoring

Local weather forecasts will be tracked daily, using UK weather warnings - Met Office to anticipate high-risk conditions. Site management will brief staff on heightened fire risk during these periods.

Fire detection and suppression

- Detection: Daily checks, thermal imaging, staff observations

- Suppression equipment: On-site water supply, hoses, extinguishers

# Prevent Self-Combustion

There is very little risk of self-combustion of the materials accepted on to and processed on site. The site operates a strict Waste Acceptance Procedure (EPR-OP01) which means that any waste and/or contaminants present that could cause localised ignition (hotspots) are likely to be screened out before the waste is brought on site.

From time to time certain, mainly organic, wastes undergo self-heating reactions. As the skips are tipped onto the floor prior to separation, the incoming material can be inspected for signs of heat build-up/burning. Any heat affected material can be rapidly isolated using the wheeled 360 excavator fitted with a clam-shell bucket.

Preventing self-combustion

- All site staff/operatives follow the sites Waste Acceptance Procedure

- A site operative fully trained in fire detection, will visually inspect the storage bays regularly throughout the day

- Surface temperatures are checked prior to checking temperatures further in the stockpiles. This is achieved by safely removing material to gain access to inside the pile. All temperature details are recorded.

- A temperature probe will be used to detect hotspots in waste bays should the visual check raise any concerns regarding the temperature of any waste

- Each load is inspected prior to going into designated bays

- Separated materials will be moved off site after a maximum <1week under normal operating conditions

- Should any material be held for longer than 14 days, daily temperature monitoring of the material will take place

- Where any of the material, through monitoring, is found to be above 50oC, the site will open the pile by moving the material to the quarantine area, monitoring the temperature on an hourly basis. If the temperature continues to rise, the material will be quenched with water

- Material will not be left unattended until the temperature has returned to below 50oC.

- During prolonged storage periods through extended hot weather, temperature monitoring frequencies of high-risk combustible materials will increase.

- Any pile subject to heat build-up will be turned, processed and/or scheduled for removal

# Monitor and Control Temperature

This section of the FPP shows how the operator will control heat to prevent self-combustion for any waste stored at the site.

The risk from localised ignition (hotspots) due to contamination is generally less likely in processed material.  This is because contaminants are removed before placement into stockpiles for short-term storage awaiting despatch.  However, there remains a risk that a hotspot could develop.

Table 8-1: Factors influencing heating rate

| Factor | Influence on heating |
| --- | --- |
| Particle size | Smaller particles heat faster due to larger surface area. |
| Moisture content | Optimal range (40–60%) supports microbial activity. |
| Oxygen availability | Essential to maintain aerobic conditions and avoid heat buildup. |
| Pile size & compaction | Large or dense piles restrict airflow and retain heat. |
| Ambient temperature | Warmer weather accelerates microbial heating. |

To detect hotspots within stockpiles of potentially combustible material, the operator will, using a temperature probe and/or a hand-held thermal imaging camera with a trigger temperature of 50°C, monitor any remaining stockpiles at the end of each working shift.

Should temperatures be discovered that exceed 50°C, the stockpile would be cautiously dismantled and carefully removed, to ensure sufficient oxygen is not introduced to increase the risk of combustion, to the quarantine area to allow cooling to take place.

Due to the low levels of material kept on site for short periods of time, along with robust pre-acceptance measures, reduces the risk of a hotspot becoming established.

There is specific evidence as to the combustion temperature of the material, and a temperature of 50°C will be the point at which action is taken.  The temperature will be monitored by using a temperature probe, like those used for the monitoring of compost piles.

As the material is sufficiently loose and friable so that penetration of the material by the temperature probe in the stockpile will be easy to accomplish.  An image is shown below as an example of the equipment available supplied by Freeland Scientific Ltd.

Figure 8-1: Thermal probe (Freeland Scientific)

Detection is via 2 x IR2 infrared flame detectors linked to an alarm panel in the weighbridge office with out of hours mobile phone alerting in addition to sounder/beacons in the tipping hall and weighbridge office.  The system is configured to alarm and then begin extinguishing the fire.  This auto system is intended to minimise the spread and intensity of a fire until the fire brigade arrive.

Auto-suppression within the building

The system is configured in a combination of ‘double-knock’ arrangements;

- Flame detector activates alarm only.

- If the second detector sees flame then the suppression system in activated automatically.

- Auto dialler contacts the designated numbers.

- Water is supplied to nozzles via an electric fire pump.

A tee is installed into the pipework at ground level between the pump and suppression system to allow a pressure fed supply to fire service appliances as required.  This facility allows water to be delivered to the affected bay without requiring entry into the building.

Nozzles are positioned over the bays, each nozzle delivering 117 litres/min.

Certification for the systems

The temperature probe and a hand-held thermal imaging camera are regularly checked for correct operation.

Pump and control systems are supplied to BS9251:2021 which is the British Standard for Fire Sprinkler Systems in the UK.

Fire Panel is supplied and installed to BS5839 fire detection and fire alarm systems for residential and commercial buildings.

Detection of a fire during operational hours

All members of staff are trained to be vigilant to the signs of fire and to report any incidents to site management.

The emergency services will be informed immediately, by the operator, if there is any evidence / suspicion of a fire on the Site.

The fire watch, during operational hours (in the morning / midday), is undertaken by site personnel, daily. These fire watches are recorded using Inspection Checklists (EMS).

Visual inspections are carried out throughout the working day to check for fires / potential causes of fire. Staff are working to sort / separate the waste throughout the day and will therefore be able to quickly identify any signs that the waste is heating up, producing smoke, or showing any other signs of a fire.

Detecting of a fire outside of operational hours

ADL implement the following measures to minimise the likelihood of a fire occurring during non-operational hours:

- Fire watch twice daily including at the end of the working day to inspects for signs of self-heating, smoke and fire, and ensure exhausts are cool etc.

- Dampening down of waste piles to reduce heat generation when outside temperatures are elevated.

- Minimise waste storage times – combustible waste is typically stored for a maximum of one month.

Hertfordshire Fire and Rescue Service average response time in 2019/20 was 7-minutes. However, as the site is within 1100m of Hoddesdon Fire Station, the response time is expected to be far less. It is therefore considered that the Fire and Rescue Service would be able to start firefighting procedures within 10-minutes of being alerted to a fire at the Site.

If the Operator (or other senior management) is the first responder, they will attempt to suppress the fire before the Emergency Services arrive if it is safe to do so.

All on call staff live within 1 mile of the Site and upon receiving notification that stockpile temperatures are increasing are able to attend the Site within 30 minutes.

Management resides within 20 miles of the Site and can attend Site within an hour.

Figure 8-2: Image showing proximate fire hydrants

# Manage Waste Piles

Storing waste materials in their largest form

No size reduction/shredding/screenin is undertaken on site, so materials are accepted in the form in which they arrive.

Maximum pile sizes for the waste held on site

The recommendations within the FPP Guidance in relation to stockpile sizes are proposed to be met on this site. Stockpile volumes of waste stored are less than the recommendations included within the FPP Guidance.

Storage areas are shown on the Layout Plan.  Table 9-1 below summarises the combustible waste storage area sizes and maximum individual pile sizes, the volume for each waste type and the maximum storage times. Bay contents are not fixed, but are allocated according to demand requirements.

A maximum pile height of 4m for combustible waste will be enforced in accordance with the FPP Guidance. The maximum pile height in bays / contained stockpiles is 2.1 m.

The minimum separation distance for combustible waste stockpiles stored, where waste is not stored within a bay or container is 6m.

The following table gives information about the waste piles.

Table 9-1: Combustible waste storage area details

| Storage bay contents | Facility | Size (LWH) | Volume | FPP guidance | Max storage time |
| --- | --- | --- | --- | --- | --- |
| External bays (x9) | Bay (4) | 6m x 6m x 3m | 108 m3 | 750m3 | 1 month |
| External bay (x1) | Bay (4) | 12m x 6m x 3m | 216 m3 | 750m3 | 1 month |

# Where Maximum Pile Sizes do not Apply

Whole ELVs

Waste ELVs are not accepted, produced or stored at the site.

Waste stored in containers

Waste may be stored in storage bays or skips/containers, see Site Layout Plan.  Combustible waste on Site will be stored in designated concrete bays/skip /storage container within the permitted area.

All storage bays on the Site are constructed from industry standard concrete which provides a thermal barrier - confirmed to have a fire resistance period of at least 120 minutes.

An appropriate ‘freeboard’ space of at least 1m will be maintained within the storage bays to prevent fire spreading over the walls.  The height of the walls is 4m, therefore the maximum height of waste in bays / contained stockpiles is 3m.

All combustible waste storage areas are accessible by mobile plant and firefighting equipment to allow for a fire to be put out.  The integrity of firewater containment infrastructure retaining water is checked as part of the inspection checklists (EMS).

Where appropriate, mobile plant will be used to remove burned waste from the vicinity of the fire, to minimise the likelihood of a fire spreading as burned waste may reignite. Burned waste will be transported to the Fire Quarantine Area.

Compost production

No compost produced on site

# Prevent Fire Spreading

The measures put in place to prevent a fire from spreading are as follows:

Table 11-1: Fire prevention and control process

| Measure | Control Process |
| --- | --- |
| Stock rotation | Stockpiles are identified to ensure stock rotation is always in place on a ‘first in, first out’ principle. The site manager is responsible for managing the rotation of waste. |
| Temperature checks | Waste undergoing longer storage will be subject to regular inspections by operatives. This will both be visually and using the positioned temperature probes to monitor for any developing hot spots. |
| The specification and construction of bay walls | LG8 blocks are manufactured to concrete grade A1 fire resistance in accordance with clause 4.3.4.4 of EN13369 with a 28-day cube strength equivalent to 50 N/mm² |
| Flame height taken into consideration | This stage begins at ignition, continues through a possible smouldering interval, into a flaming interval, and may be said to end prior to flashover. The buoyant gas stream is generally turbulent, except when the fire source is very small. |
| Bay freeboard | There is a maintained free board space between the top of each accumulation of waste materials and the top of the bay walls of at least 1m. |
| Quickly and effectively remove waste from bays and isolate it during an incident | The site-based mobile plant can be used to move at risk waste materials if required and place it into the quarantine area in the event of an incident. |

Separation distances

All open faces of storage bays have a separation distance of at least 6m between the waste and any other combustible material.

Fire walls and bays

Storage bays are constructed from concrete panels with a rating of at least 120 minutes (2 hours) fire resistance. Adjacent storage bays can be considered as being isolated with additional piles of material not considered part of the same pile..

The following measures are employed to minimise the risk of fire spreading:

- The specification and construction of the bays offer a thermal barrier exceeding 4 hours.

- The bays benefit from a freeboard of 1-m and open faces are located at least 6m from other sources of combustible materials to minimise the potential risk of lighted material igniting other wastes.

- In the event of a fire occurring in a bay, the quarantine area will be used to segregate non-burning waste to isolate and minimise the potential impact of the incident.

# Fire Quarantine Area (Fqa)

Area

The Fire Quarantine Area (FQA) (not the waste quarantine area) meets the FPP Guidance requirements;

- The FQA may be used for storing materials to prevent the spread of fire or to isolate materials that are likely to re-ignite or have been burned.  This will aid in the overall suppression of a fire.

- The FQA will be kept free of materials so that it can be used in the event of a fire.

- The FQA has a sufficient separation distance (minimum of 6m) from any sources of ignition or stored combustible waste.

- The FQA will be able to store approximately 108m3 of waste which is 50% of the volume of the largest stockpile of combustible waste stored on the Site.

Due to the layout of the Site, it is necessary to have a flexible FQA and the location will vary, however there will be an area of at least 3m x 3m, always kept free.  The FQA will not be located within 6 m of combustible waste, flammable materials e.g., fuel, or any sources of ignition.

The use of the FQA will be covered in the EMS training for new and existing staff.  Every staff member is aware that it must always be kept clear and not be located within 6m of combustible waste, flammable materials, or any sources of ignition.

The FQA will allow for faster active firefighting regarding the removal of burning or burned material.

The areas are sited as far as possible from any stockpiles or buildings. They will be used in the event of hot loads arriving on site or any fire within a waste stockpile when waste will be dragged out of the bay and placed within the area to allow ease of firefighting. The areas will be more than adequate for holding at least half of the volume of any stockpile.

Any waste on site that has any evidence of smoke or is very hot will be moved to the FQA to keep it separate from the main waste inputs. Here it will be either spread out to cool down or will be watered to prevent a fire.

Quarantine area location and size

See site layout plan.

How to use the quarantine area if there is a fire

If any of waste material, through monitoring or observation, shows the temperature to be above 50oC, then site operators will open up the stockpile. This would be accomplished using the site loading shovels in combination. The loading shovels are able to bulldoze a firebreak area around any burning material extremely quickly this will allow fire gaps to be constructed and to prevent the fire from spreading. It also allows any ‘hot’ material to be moved out of the windrow and isolated in the quarantine area. by moving the material to the quarantine area and monitoring the temperature on an hourly basis.

If the temperature continues to rise, the material will be dowsed with water. The material will not be left unattended until the temperature has returned to below 50oC.

Procedure to remove material stored temporarily if there is a fire

The intention of the FQA is that it will always be available should it be needed. However, should a 3rd party vehicle be present at the time of an emergency it will be directed to clear the area from the end nearest to the emergency in a way that doesn’t hinder use of the area, or traffic flow etc.

Purpose:

To safely manage the removal of material temporarily stored in the quarantine area during a fire, preventing fire spread, protecting people, and supporting emergency response operations.

Fire detection and initial response

- Immediately raise the alarm and initiate the site’s Fire Emergency Plan.

- Call the Fire and Rescue Service (999) and inform the Site Manager.

- Evacuate all non-essential personnel to the designated assembly point.

- Await authorisation from the Fire and Rescue Service or Site Manager before attempting to move any material.

Site manager and emergency services assessment

The Site Manager must assess the situation with the attending Fire Officer to determine if removal is safe and necessary.

Considerations include

- The location and intensity of the fire relative to the quarantine area.

- Whether material removal could prevent escalation or protect key infrastructure.

- Whether moving material may introduce risk to staff or interfere with fire suppression efforts.

Safe removal of material (if approved)

Only trained staff wearing suitable PPE, including RPE if smoke is present, are permitted to carry out removal.

Only unburnt or unaffected material may be moved.

Material must be moved using suitable plant or vehicles that are:

- Fire-resistant or fitted with fire suppression systems where possible.

- Operated in safe working order and away from ignition sources.

- Transport material to a pre-identified emergency relocation zone, which must be:

- At least 6 m from other combustible waste, buildings, or site boundaries.

- Accessible for firefighting appliances if needed.

# Detecting Fires

Detection system in use

Detection is via 2 x IR2 infrared flame detectors linked to an alarm panel in the weighbridge office with out of hours mobile phone alerting in addition to sounder/beacons in the tipping hall and weighbridge office.  The system is configured to alarm and then begin extinguishing the fire.  This auto system is intended to minimise the spread and intensity of a fire until the fire brigade arrive.

Detecting of a fire outside of operational hours

ADL implement the following measures to minimise the likelihood of a fire occurring during non-operational hours:

- Fire watch twice daily including at the end of the working day to inspects for signs of self-heating, smoke and fire, and ensure exhausts are cool etc.

- Dampening down of waste piles to reduce heat generation when outside temperatures are elevated.

- Minimise waste storage times – combustible waste is typically stored for a maximum of one month.

Detection of a fire during operational hours

All members of staff are trained to be vigilant to the signs of fire and to report any incidents to site management.

The emergency services will be informed immediately, by the operator, if there is any evidence / suspicion of a fire on the Site.

The fire watch, during operational hours (in the morning / midday), is undertaken by site personnel, daily. These fire watches are recorded using Inspection Checklists (EMS).

Visual inspections are carried out throughout the working day to check for fires / potential causes of fire. Staff are working to sort / separate the waste throughout the day and will therefore be able to quickly identify any

Certification for the systems

The temperature probe and a hand-held thermal imaging camera are regularly checked for correct operation.

Pump and control systems are supplied to BS9251:2021 which is the British Standard for Fire Sprinkler Systems in the UK.

Fire Panel is supplied and installed to BS5839 fire detection and fire alarm systems for residential and commercial buildings.

# Suppressing Fires

Auto-suppression within the building

The system is configured in a combination of ‘double-knock’ arrangements;

- Flame detector activates alarm only.

- If the second detector sees flame then the suppression system in activated automatically.

- Auto dialler contacts the designated numbers.

- Water is supplied to nozzles via an electric fire pump.

A tee is installed into the pipework at ground level between the pump and suppression system to allow a pressure fed supply to fire service appliances as required.  This facility allows water to be delivered to the affected bay without requiring entry into the building.

Nozzles are positioned over the bays, each nozzle delivering 117 litres/min.

# Firefighting Techniques

The site is located on an industrial estate with good highway access for fire and rescue vehicles, within ten minutes travel time, with immediate neighbours. The site layout is designed to allow for active firefighting. This will help allow a fire to be extinguished within 4 hours.

The resources available include:

- Plant that can be used to move waste around the site.

- Staff.

- During operational hours visual checks are carried out regularly around the site and are the responsibility of the Operations Manager (OM). The site operates a two-way radio system to communicate with each of the operatives. In the event of a fire all staff are alerted over the radio.

- Available water supply (nearest hydrant at corner of Pindar Road and Essex Road.

- Finances.

- Handheld fire extinguishers are also present at strategic locations on site and within mobile plant.

Active firefighting

For small, contained fires, the waste will be extinguished using an extinguisher or hose as it is removed from the pile. The burned portion will be moved to the quarantine area, and the unaffected waste returned to the pile. For larger, uncontained fires, the burning waste will be transferred to the quarantine area.

Small fires

A small fire or area of smouldering waste will be dealt with as follows.

Loading shovels will be used to pull the affected waste into the open and away from any further waste that could combust on contact, or bulldoze a firebreak around the affected area; and, depending on the size / nature / location of the fire the waste will either be:

- Extinguished immediately utilising the fire extinguishers/fire hose ; or

- Moved to the appropriate quarantine area and extinguished.

Uncontainable small fire or large fire

The following procedure will be followed in the event of a small fire becoming uncontainable or in the event of a major fire on site:

- The on-call Director and LFRS will be contacted immediately.

- Access routes will be cleared for emergency services.

- HFRS will be informed that the site processes waste wood and has a large amount of unprocessed material on site.

- Mobile plant will be used to pull the affected waste into the open and away from any further waste that could combust on contact, or bulldoze a firebreak around the affected area; and

- The Local Authority and EA will be notified at the first opportune moment.

Following arrival of HFRS, all Site staff will take instructions from the attending personnel which may include any of the following:

- If possible, waste that is unburnt will be dampened down to prevent the fire from spreading further.

- If possible, unburned material will be separated from the fire using mobile plant.

- The affected area will be isolated, and attempts will be made to extinguish the fire utilising the onsite fire extinguishers/hoses if safe to do so; and

- The Site will be evacuated.

# Water Supplies

Available water supply on site

A dedicated water supply is kept at the site in a large above ground tank (60m3).

The closest fire hydrant, towards the junction of Pindar Road with Essex Road, is within 75m of the site entrance.

Herts Fire and Rescue Service have advised that that all hydrants meet the British Standard (BS 750:2012) and therefore are able to deliver a maximum flow rate of 2,000 l/min to a device.  The emergency services can utilise the nearby fire hydrants in the event of a fire.

Table 16-1: Water supply calculation

| Max pile volume | Water supply reqd | Total water supply | Total water available |
| --- | --- | --- | --- |
| 216 m3 | 1440l/min | 259,329l | 60,000l |

# Managing Fire Water

Assessing risks to groundwater from fire water

Site

Figure 17-1: Groundwater vulnerability map

Combustible waste is stored and sorted within a secure building, on impermeable surfacing.  Firewater from such waste, in the event of a fire, will be contained within the building.

As the impermeable surface covers the entire site with a sealed drainage system in place, it is considered that the aquifer is fully protected from the activities and any fire water runoff from the site.

# During and After an Incident

During an event

During a substantial fire event, downwind residents will be notified so that they can take the correct precautions to prevent nuisance from smoke. The properties to be notified will depend upon the prevailing wind direction at the time of the event. This will be achieved by sending an email or by telephoning the closest residents.

During an event incoming waste is to be diverted to another site. ADL has access to other sites within the wider Sun Enviro Group that will accept waste if there is a shut-down at the site (as per the Contingency Plan).

Post event procedures

After a fire event, the following procedure will be implemented depending on the severity of the fire:

- A small and containable fire that can be safely dealt with in-house using suitably trained staff and firefighting equipment located on Site: The fire will be recorded in the Site Diary, including the causes of the fire and methods used to manage the fire. An assessment will be carried out to determine whether further mitigation measures could have prevented the fire. Any outcomes to be implemented onsite will be incorporated within this FPP and the Site’s EMS as required.

- A larger fire that requires the presence of HFRS: If the Site operatives have been told to evacuate or cease operations by HFRS, the Site will wait until told safe to re-enter and resume operations. Any closure of the Site will be followed by informing customers and the regulatory authorities. The fire will be recorded in the Site Diary and in an online incident report and will detail the causes of the fire and methods used to manage the fire. An assessment will be carried out to determine whether further mitigation measures could have prevented the fire. Any outcomes to be implemented onsite will be incorporated within this FPP and the Site’s EMS as required.

- Should damage be sufficient to prevent the Site from being able to store waste, the Site will cease accepting waste until the situation is resolved.

The SM will liaise with the EA to determine a plan-of-action to introduce normal operations at the Site, and the timescales involved to achieve this.  A visual assessment will be carried out by the SM to determine whether the waste can be treated on Site. Wherever possible, unburnt wastes will be separated from fire damaged piles.

The Site Management in conjunction with the insurance company and other relevant experts will determine the required decontamination measures to be carried out in proportion to the impact caused by the fire.

Once firewater and fire damaged waste have been removed the site will be cleaned using methods appropriate to the nature of the residues. This may include (but not be limited to) the following: on-site yard sweeping equipment, jet-washing or engaging a third part specialist cleaning company.

Any firewater contained on site following a fire will be removed from Site via tanker to a suitably permitted facility once it has been sampled and analysis received if it is not suitable for reuse as a firewater supply.

Making the site operational after a fire

The period taken to restore the Site, or affected part of the Site, to operational status will be determined by the nature and extent of the fire. If the affected area does not impact the rest of the Site’s operation, operations will re-start as and when appropriate.

After a significant incident, an assessment will be undertaken by a suitably qualified individual. Technically competent managers and/or engineers will assess the degree of damage caused by a fire and the residual risk from fire damaged waste, emissions or equipment. Burnt waste material will be kept on Site for a short period of time if required for a subsequent internal investigation. Following this, the material will be transferred to a suitably permitted disposal facility.

Follow up action

It is the responsibility of the SM, in conjunction with the IC and the Emergency Services where appropriate, to determine when the emergency incident has been brought under control, and it is safe for evacuated personnel to return to site and/or for the site to resume normal operation.

It is the responsibility of the SM, in conjunction with the IC, to ensure that any evidence connected with the emergency incident is preserved. In particular, any plant and equipment involved in the incident must not be moved or removed unless it represents an immediate health and safety risk.

It is the responsibility of the SM, in conjunction with key company personnel called to the emergency incident, to take witness records relevant to the incident at the earliest opportunity.

It is the responsibility of the SM in conjunction with key company personnel called to the emergency incident, to contact the Health and Safety Executive at the earliest opportunity and, if appropriate to do so, to report in accordance with the Reporting of Injuries, Diseases and Dangerous Occurrences Regulations 1995.

It is the responsibility of the key company personnel called to the emergency incident, in conjunction with site personnel, to carry out a full investigation into the incident and report its findings to all relevant parties.

It is the responsibility of the key company personnel called to the emergency incident to contact all other relevant company personnel.

It is the responsibility of the key company personnel involved in the emergency to arrange provision of counselling and support where necessary.

# Appendix A – Fire Safety Management Plan

| Procedure | Responsibility |
| --- | --- |
| Fire Safety Person with Overall Responsibility for Fire Safety | Site Manager |
| Fire Risk Assessment Person responsible for commissioning & review | Site Manager |
| Maintenance Programme Person Responsible for: - Maintenance of fire safety provisions - Fire alarm - Emergency lighting - Firefighting equipment - Escape routes - Fire safety signs/notices | Site Manager |
| Emergency Action Plan Person responsible for production & review | Site Manager |

# Appendix B – Fire Emergency Procedure

Assembly Point – Staff Car Park

If you discover a fire:

- Raise the alarm immediately. The Sine Manager and all other staff onsite to be informed of the fire by using the on-person radio, by stating FIRE FIRE FIRE, details of location and material involved.

- Tackle the fire using the appropriate firefighting equipment. (Only if you feel safe and are trained to do so)

- Leave the premises by the nearest safest available exit.

- Report to the assembly point

- Ensure that site management is aware of the fire.

- Call 999 for the fire brigade by mobile phone, if not already done.

- Do not leave site or re-enter any building until cleared to do so by the fire brigade or fire warden.

If you hear the alarm:

- Leave the premises by the nearest safest route.

- Do not stop to collect personal belongings.

- Ensure any one you meet on the way out is aware of the fire.

- Report to the assembly point.

- Call 999 for the fire brigade by mobile phone, if not already done.

- Do not leave site or re-enter any building until cleared to do so by the fire brigade or fire warden.

Machine / Mobile plant operators.

- Clear area of vehicles if safe to do so.

- Turn off equipment using emergency stops.

- Ensure compressed gas containers are isolated.

- If possible and safe to do so, commence active firefighting measures such as moving unburning waste material to the quarantine area.

- Remove mobile plant from site to facilitate access for the Fire and Rescue Service, save for any equipment that is deemed safe and appropriate to be used in tackling any fire, e.g. shovels and excavators.

- Report location of relevant vehicles remaining on site to the Fire Brigade at the assembly point.

Site Manager.

- Call the Fire Brigade. Tel: 999

- Announce “Fire, Fire, Fire. A fire has been reported at/in ****. All personnel are to report to the assembly point near the site entrance”. In addition, fire is called on the radio, with details of location and material involved provided.

- Report to assembly point with the employees and visitor book.

- Ensure that Visitors \ Contractors / employees are accounted for. (Use visitors and employees’ book).

- Site Manager to report to the scene of the fire.

- Liaise with Fire Brigade upon arrival.

- Brief Fire Brigade of any danger areas on site.

- Do not allow any other vehicles except emergency vehicles to enter site.