## MCP_or_generator_list
Plant Name | NACE Code (required information) | Traceable identifier for the individual medium combustion plant (MCP) or generator (required information)* | Plant Manufacturer* | Model Name* | Is the plant stationary or mobile? | Stack or emission point national grid reference (required information) | Easting | Northing | Latitude | Longitude | Date operation started (required information) | Rated thermal input of the individual MCP or generator in MW thermal (required information) | Total rated thermal input of all plant or generators on site in MWth | Technology or type (required information) | Main fuel type used (required information) | Secondary fuel type used (required information if plant is dual fired or uses a secondary fuel as a back up) | Is the secondary fuel used as a back up? and/or does the plant co fire using the secondary fuel? | Percentage of secondary fuel type used | Will the medium combustion plant be operated as a limited operting hours plant? (required information) | Annual operating hours. Please enter the hours the plant is intended to run. | Do you want to declare that your existing MCP will meet new MCP emission limit values (ELVs) from the medium combustion plant directive? | Annual load factor as a percentage | Background nitrogen dioxide (NO2) in ug/m3 | Stack height (meters) | What is the emission rate for the pollutants (g/s) | Is the plant in an Air Quality Management Area (AQMA) for a declared pollutant? | What is the name of the local authority who has declared th AQMA? | Closest human receptor (meters) | Human receptor details | Closest Ecological receptor (meters) | Ecological receptor details | Will secondary abatement be fitted to the plant | What type of secondary abatement will be fitted? | date of capacity market of balancing service agreement or FiT accreditation (DD/MM/YYYY)
Guidance | NACE code means Nomenclature of Economic Activities and is the European statistical classification of economic activities | Serial number or other unique identifier, name plate, manufacturer and or model |  |  |  | Enter the coordinates of the emission point of the plant (not the site). You should enter this as a National Grid Reference or as a Latitude and Longitude pair. You should enter the values using the same coordinate system that you collected the raw data in. |  |  |  |  | When the plant or generator was first put into operation or the commissioning date, leave blank if new and not yet operating | This is for each individual unit. You should calculate this using one of the methods in the Association of Manufacturers and suppliers of Power Systems and ancillary equipment (AMPS) technical note: "Determination of thermal input power of an engine driven generator". | This should be the total of all the individual units of any size | Boiler, Engine, Back up generator, turbine, boiler CHP, Engine CHP | Gas oil, Liquid fuels other than gas oil, Natural gas, Biogas, Other gaseous fuels, Solid biomass, Waste biomass, Woody solid biomass, Straw, Other solid fuels | Gas oil, Liquid fuels other than gas oil, Natural gas, Biogas, Other gaseous fuels, Solid biomass, Waste biomass, Woody solid biomass, Straw, Other solid fuels | Back up, co firing, both | Only required where co firing | Where the option of exemption under Article 6 (8) of the medium combustion plant directive is used the operator (as identified in Part A of the application form) can declare by indicating here that the MCP will not be operaterated more than the number of hours referred to in this paragraph. | This should be the total for the year and be to the nearest whole number | Applicable for existing MCP plant only. You may want to claim this to demonstrate low risk impacts to habitats as part of an air emissions risk assessment. If you do make this voluntary declaration we will include new MCP ELVs from the medium combustion plant directive in your permit. |  | Go to the Defra UK Air website and select the most recent background map data. Set the local authority to that of your site location and the pollutant to NO2 |  |  | AQMAs interactive map | [7 empty] | applicable to SG applications only
| Full Classification | [10 empty] | Microsoft Word - AMPS8704 - AMPS Technical Committee document template update 03.docx (environment-agency.gov.uk) | [10 empty] | Background Mapping data for local authorities - Defra, UK
Simple List
Plant 1 | C.11.05 | GEN1234DE0001 | Cummins | C12 D6T | stationary | ST 58132 72695 |  |  | 51.4517 | -2.6039 | 2016-05-23 | 2.1 | 12.4 | Engine | Gas oil | natural gas | co firing | 20 | yes | 7000 | yes | 90% | 12 | 3 |  | yes | Cheshire West and Chester | 100 | school | 500 | SSSI, SAC | Yes | SCR | 2018-12-01
Plant 1 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8092798438 | 480927.95 | 198438.36 |  |  |  | 6.18 | 356.22 | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 11 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 278.7418 | Residential façade | 315.4939 | Slough Hill LWS | No
Plant 2 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8092498442 | 480924.73 | 198442.95 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 11 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 273.1581 | Residential façade | 314.3918 | Slough Hill LWS | No
Plant 3 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8092198447 | 480921.69 | 198447.66 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 11 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 267.5603 | Residential façade | 313.6001 | Slough Hill LWS | No
Plant 4 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8091898452 | 480918.7 | 198452.37 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 11 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 261.9876 | Residential façade | 312.9517 | Slough Hill LWS | No
Plant 5 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8087498520 | 480874 | 198520.59 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 11 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 180.6559 | Residential façade | 313.6486 | Slough Hill LWS | No
Plant 6 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8087198525 | 480871.05 | 198525.19 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 11 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 175.2094 | Residential façade | 314.5052 | Slough Hill LWS | No
Plant 7 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8086798529 | 480867.87 | 198529.9 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 11 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 169.5597 | Residential façade | 315.3617 | Slough Hill LWS | No
Plant 8 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8086498534 | 480864.92 | 198534.56 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 11 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 164.0629 | Residential façade | 316.4481 | Slough Hill LWS | No
Plant 9 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8086698398 | 480866.83 | 198398.73 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 11 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 291.8395 | Residential façade | 244.013 | Slough Hill LWS | No
Plant 10 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8086498403 | 480864.03 | 198403.27 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 11 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 286.7211 | Residential façade | 243.0199 | Slough Hill LWS | No
Plant 11 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8086098407 | 480860.9 | 198407.81 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 11 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 281.5262 | Residential façade | 241.8362 | Slough Hill LWS | No
Plant 12 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8085798412 | 480857.92 | 198412.49 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 11 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 276.2455 | Residential façade | 240.967 | Slough Hill LWS | No
Plant 13 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8081398480 | 480813.23 | 198480.84 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 11 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 200.6285 | Residential façade | 241.9528 | Slough Hill LWS | No
Plant 14 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8081098485 | 480810.26 | 198485.42 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 11 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 195.738 | Residential façade | 243.0192 | Slough Hill LWS | No
Plant 15 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8080798490 | 480807.17 | 198490.07 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 11 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 190.7972 | Residential façade | 244.1703 | Slough Hill LWS | No
Plant 16 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8080498494 | 480804.08 | 198494.65 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 11 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 185.9624 | Residential façade | 245.3915 | Slough Hill LWS | No
Plant 17 | 35.11 | TBC | Moteurs Baudouin | 16M55G6D2/5 | Stationary | SU8085298555 | 480852 | 198555 |  |  |  | 7.86 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 11 | NOx: 7.25 PM10: 0.009 | No | Buckinghamshire | 139.9786 | Residential façade | 322.2996 | Slough Hill LWS | No
Plant 18 | 35.11 | TBC | Moteurs Baudouin | 12M55G10D2/5 | Stationary | SU8084898559 | 480848.44 | 198559.79 |  |  |  | 6.3 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 11 | NOx: 6.98 PM10: 0.008 | No | Buckinghamshire | 134.1028 | Residential façade | 323.5703 | Slough Hill LWS | No
Plant 19 | 35.11 | TBC | Moteurs Baudouin | 12M55G10D2/5 | Stationary | SU8084598564 | 480845.4 | 198564.46 |  |  |  | 6.3 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 11 | NOx: 6.98 PM10: 0.008 | No | Buckinghamshire | 128.5708 | Residential façade | 325.1845 | Slough Hill LWS | No
Plant 20 | 35.11 | TBC | Moteurs Baudouin | 12M55G10D2/5 | Stationary | SU8084298568 | 480842.31 | 198568.91 |  |  |  | 6.3 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 11 | NOx: 6.98 PM10: 0.008 | No | Buckinghamshire | 123.2191 | Residential façade | 326.6828 | Slough Hill LWS | No
Plant 21 | 35.11 | TBC | Moteurs Baudouin | 16M55G6D2/5 | Stationary | SU8079198515 | 480791 | 198515 |  |  |  | 7.86 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 11 | NOx: 7.25 PM10: 0.009 | No | Buckinghamshire | 165.0121 | Residential façade | 252.6064 | Slough Hill LWS | No
Plant 22 | 35.11 | TBC | Moteurs Baudouin | 12M55G10D2/5 | Stationary | SU8078798568 | 480787.76 | 198568.91 |  |  |  | 6.3 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 11 | NOx: 6.98 PM10: 0.008 | No | Buckinghamshire | 111.0969 | Residential façade | 295.647 | Slough Hill LWS | No
Plant 23 | 35.11 | TBC | Moteurs Baudouin | 12M55G10D2/5 | Stationary | SU8078498524 | 480784.63 | 198524.63 |  |  |  | 6.3 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 11 | NOx: 6.98 PM10: 0.008 | No | Buckinghamshire | 155.4314 | Residential façade | 256.6425 | Slough Hill LWS | No
Plant 24 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8074598485 | 480745.14 | 198485.6 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 11 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 157.2806 | Residential façade | 202.3006 | Slough Hill LWS | No
Plant 25 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8074298490 | 480742.1 | 198490.18 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 11 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 152.5166 | Residential façade | 204.6368 | Slough Hill LWS | No
Plant 26 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8073998494 | 480739.1 | 198494.76 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 11 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 147.8399 | Residential façade | 207.112 | Slough Hill LWS | No
Plant 27 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8070098554 | 480700.16 | 198554.23 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 11 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 95.2003 | Residential façade | 248.1417 | Slough Hill LWS | No
Plant 28 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8069798558 | 480697.24 | 198558.99 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 11 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 92.2615 | Residential façade | 252.0505 | Slough Hill LWS | No
Plant 29 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8069498563 | 480694.19 | 198563.56 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 11 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 89.4309 | Residential façade | 255.8076 | Slough Hill LWS | No
Plant 30 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8063398523 | 480633.3 | 198523.8 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 11 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 43.6249 | Residential façade | 209.8526 | Slough Hill LWS | No
Plant 31 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8063698519 | 480636.37 | 198519.11 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 11 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 49.1907 | Residential façade | 205.1165 | Slough Hill LWS | No
Plant 32 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8063998514 | 480639.43 | 198514.31 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 11 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 54.844 | Residential façade | 200.3151 | Slough Hill LWS | No
Plant 33 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8067898455 | 480678.26 | 198455.12 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 11 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 125.4853 | Residential façade | 146.7505 | Slough Hill LWS | No
Plant 34 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8068198450 | 480681.36 | 198450.36 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 11 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 131.16 | Residential façade | 143.0879 | Slough Hill LWS | No
Plant 35 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8068498445 | 480684.32 | 198445.67 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 11 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 136.6969 | Residential façade | 139.5798 | Slough Hill LWS | No
Plant 36 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8081898366 | 480818.98 | 198366.98 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 15.98 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 286.1731 | Residential façade | 188.5753 | Slough Hill LWS | No
Plant 37 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8081598371 | 480815.91 | 198371.77 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 15.98 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 280.7012 | Residential façade | 187.0544 | Slough Hill LWS | No
Plant 38 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8081298458 | 480812.89 | 198458.65 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 15.98 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 222.6355 | Residential façade | 226.9584 | Slough Hill LWS | No
Plant 39 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8075898458 | 480758.97 | 198458.65 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 15.98 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 182.7005 | Residential façade | 188.5666 | Slough Hill LWS | No
Plant 40 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8075598463 | 480755.84 | 198463.18 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 15.98 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 177.637 | Residential façade | 190.1077 | Slough Hill LWS | No
Plant 41 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8076398330 | 480763.41 | 198330.88 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 15.98 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 276.0869 | Residential façade | 126.5409 | Slough Hill LWS | No
Plant 42 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8076098335 | 480760.39 | 198335.48 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 15.98 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 270.5867 | Residential façade | 124.2606 | Slough Hill LWS | No
Plant 43 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8075798340 | 480757.2 | 198340.14 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 15.98 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 264.9398 | Residential façade | 122.0325 | Slough Hill LWS | No
Plant 44 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8070398422 | 480703.55 | 198422.25 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 15.98 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 166.9421 | Residential façade | 126.5499 | Slough Hill LWS | No
Plant 45 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8070098426 | 480700.68 | 198426.9 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 15.98 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 161.4951 | Residential façade | 129.1325 | Slough Hill LWS | No
Plant 46 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8076098329 | 480760.9 | 198329.04 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 15.98 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 276.1713 | Residential façade | 123.8168 | Slough Hill LWS | No
Plant 47 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8075798333 | 480757.58 | 198333.63 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 15.98 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 270.5084 | Residential façade | 121.1805 | Slough Hill LWS | No
Plant 48 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8075498338 | 480754.71 | 198338.42 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 15.98 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 264.9345 | Residential façade | 119.2374 | Slough Hill LWS | No
Plant 49 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8070098420 | 480700.74 | 198420.4 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 15.98 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 166.8104 | Residential façade | 123.5203 | Slough Hill LWS | No
Plant 50 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8069798425 | 480697.93 | 198425.18 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 15.98 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 161.2839 | Residential façade | 126.3036 | Slough Hill LWS | No
Plant 51 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8081698372 | 480816 | 198372 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 15.98 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 280.6172 | Residential façade | 187.2111 | Slough Hill LWS | No
Plant 52 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8081398376 | 480813 | 198376 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 15.98 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 275.7263 | Residential façade | 185.6583 | Slough Hill LWS | No
Plant 53 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8075998459 | 480759 | 198459 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 15.98 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 182.5377 | Residential façade | 188.8544 | Slough Hill LWS | No
Plant 54 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8076398331 | 480763 | 198331 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 15.98 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 275.7535 | Residential façade | 126.1507 | Slough Hill LWS | No
Plant 55 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8076098335 | 480760 | 198335 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 15.98 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 270.7563 | Residential façade | 123.7942 | Slough Hill LWS | No
Plant 56 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8075198343 | 480751.63 | 198343 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 15.98 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 259.4154 | Residential façade | 117.2722 | Slough Hill LWS | No
Plant 57 | 35.11 | TBC | Moteurs Baudouin | 16M55G3000/5 | Stationary | SU8081298382 | 480812.43 | 198382.73 |  |  |  | 6.18 |  | Back up generator | Gas oil |  |  |  | Yes | 5 |  | 90% | 6.2094 | 15.98 | NOx: 4.65 PM10: 0.083 | No | Buckinghamshire | 270.9192 | Residential façade | 187.4824 | Slough Hill LWS | No
Note
*Virtus can send this information if required once the 57 generators have been secured. The submitted AQA and other supporting reports have been submitted on the basis of diesel powered, stationery plant, optimised to 2.4MWe (55 generators) and 2.8MWe (2 generators), which will meet the US EPA Tier 2 emissions certification. Virtus will secure generators with the same specifications as above for the Saunderton Data Centre campus., and can send the above details if required once secured.
Note on C6: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C7: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C8: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C9: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C10: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C11: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C12: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C13: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C14: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C15: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C16: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C17: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C18: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C19: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C20: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C21: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C22: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C23: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C24: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C25: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C26: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C27: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C28: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C29: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C30: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C31: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C32: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C33: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C34: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C35: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C36: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C37: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C38: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C39: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C40: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C41: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C42: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C43: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C44: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C45: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C46: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C47: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C48: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C49: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C50: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C51: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C52: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C53: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C54: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C55: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C56: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C57: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C58: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C59: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C60: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C61: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN
Note on C62: Khary Cave: INSERT SERIAL NUMBERS IF KNOWN

## Resp_1 (hidden)
Plant Name | _1136 | _1333 | _1234 | Easting | Northing | Lat | Long | _1224 | _1137 | _1118 | _1125 | _1152 | _1230 | _1138 | _1328 | _1062 | _1326 | _1021 | _1015 | _1140 | _1121 | _1117 | _1124 | _2005 | _1016 | _2006 | _1150 | _1040 | _1225 | _2017 | Release Point NGR | Mobile Plant | NACE Code
Plant 1 | TBC | Moteurs Baudouin | 16M55G3000/5 | 480927.95 | 198438.36 | 0 | 0 | 0 | 6.18 | Back up generator | Gas oil | 0 | 0 | 0 | Yes | 5 | 0 | 0.9 | 6.2094 | 11 | No | Buckinghamshire | 278.7418 | Residential façade | 315.4939 | Slough Hill LWS | No | 0 | 0 | NOx: 4.65 PM10: 0.083 | SU8092798438 | No | 35.11
Plant 2 | TBC | Moteurs Baudouin | 16M55G3000/5 | 480924.73 | 198442.95 | 0 | 0 | 0 | 6.18 | Back up generator | Gas oil | 0 | 0 | 0 | Yes | 5 | 0 | 0.9 | 6.2094 | 11 | No | Buckinghamshire | 273.1581 | Residential façade | 314.3918 | Slough Hill LWS | No | 0 | 0 | NOx: 4.65 PM10: 0.083 | SU8092498442 | No | 35.11
Plant 3 | TBC | Moteurs Baudouin | 16M55G3000/5 | 480921.69 | 198447.66 | 0 | 0 | 0 | 6.18 | Back up generator | Gas oil | 0 | 0 | 0 | Yes | 5 | 0 | 0.9 | 6.2094 | 11 | No | Buckinghamshire | 267.5603 | Residential façade | 313.6001 | Slough Hill LWS | No | 0 | 0 | NOx: 4.65 PM10: 0.083 | SU8092198447 | No | 35.11
Plant 4 | TBC | Moteurs Baudouin | 16M55G3000/5 | 480918.7 | 198452.37 | 0 | 0 | 0 | 6.18 | Back up generator | Gas oil | 0 | 0 | 0 | Yes | 5 | 0 | 0.9 | 6.2094 | 11 | No | Buckinghamshire | 261.9876 | Residential façade | 312.9517 | Slough Hill LWS | No | 0 | 0 | NOx: 4.65 PM10: 0.083 | SU8091898452 | No | 35.11
Plant 5 | TBC | Moteurs Baudouin | 16M55G3000/5 | 480874 | 198520.59 | 0 | 0 | 0 | 6.18 | Back up generator | Gas oil | 0 | 0 | 0 | Yes | 5 | 0 | 0.9 | 6.2094 | 11 | No | Buckinghamshire | 180.6559 | Residential façade | 313.6486 | Slough Hill LWS | No | 0 | 0 | NOx: 4.65 PM10: 0.083 | SU8087498520 | No | 35.11
Plant 6 | TBC | Moteurs Baudouin | 16M55G3000/5 | 480871.05 | 198525.19 | 0 | 0 | 0 | 6.18 | Back up generator | Gas oil | 0 | 0 | 0 | Yes | 5 | 0 | 0.9 | 6.2094 | 11 | No | Buckinghamshire | 175.2094 | Residential façade | 314.5052 | Slough Hill LWS | No | 0 | 0 | NOx: 4.65 PM10: 0.083 | SU8087198525 | No | 35.11
Plant 7 | TBC | Moteurs Baudouin | 16M55G3000/5 | 480867.87 | 198529.9 | 0 | 0 | 0 | 6.18 | Back up generator | Gas oil | 0 | 0 | 0 | Yes | 5 | 0 | 0.9 | 6.2094 | 11 | No | Buckinghamshire | 169.5597 | Residential façade | 315.3617 | Slough Hill LWS | No | 0 | 0 | NOx: 4.65 PM10: 0.083 | SU8086798529 | No | 35.11
Plant 8 | TBC | Moteurs Baudouin | 16M55G3000/5 | 480864.92 | 198534.56 | 0 | 0 | 0 | 6.18 | Back up generator | Gas oil | 0 | 0 | 0 | Yes | 5 | 0 | 0.9 | 6.2094 | 11 | No | Buckinghamshire | 164.0629 | Residential façade | 316.4481 | Slough Hill LWS | No | 0 | 0 | NOx: 4.65 PM10: 0.083 | SU8086498534 | No | 35.11
Plant 9 | TBC | Moteurs Baudouin | 16M55G3000/5 | 480866.83 | 198398.73 | 0 | 0 | 0 | 6.18 | Back up generator | Gas oil | 0 | 0 | 0 | Yes | 5 | 0 | 0.9 | 6.2094 | 11 | No | Buckinghamshire | 291.8395 | Residential façade | 244.013 | Slough Hill LWS | No | 0 | 0 | NOx: 4.65 PM10: 0.083 | SU8086698398 | No | 35.11
Plant 10 | TBC | Moteurs Baudouin | 16M55G3000/5 | 480864.03 | 198403.27 | 0 | 0 | 0 | 6.18 | Back up generator | Gas oil | 0 | 0 | 0 | Yes | 5 | 0 | 0.9 | 6.2094 | 11 | No | Buckinghamshire | 286.7211 | Residential façade | 243.0199 | Slough Hill LWS | No | 0 | 0 | NOx: 4.65 PM10: 0.083 | SU8086498403 | No | 35.11
Plant 11 | TBC | Moteurs Baudouin | 16M55G3000/5 | 480860.9 | 198407.81 | 0 | 0 | 0 | 6.18 | Back up generator | Gas oil | 0 | #REF! | 0 | Yes | 5 | 0 | 0.9 | 6.2094 | 11 | No | Buckinghamshire | 281.5262 | Residential façade | 241.8362 | Slough Hill LWS | No | 0 | 0 | NOx: 4.65 PM10: 0.083 | SU8086098407 | No | 35.11
Plant 12 | TBC | Moteurs Baudouin | 16M55G3000/5 | 480857.92 | 198412.49 | 0 | 0 | 0 | 6.18 | Back up generator | Gas oil | 0 | #REF! | 0 | Yes | 5 | 0 | 0.9 | 6.2094 | 11 | No | Buckinghamshire | 276.2455 | Residential façade | 240.967 | Slough Hill LWS | No | 0 | 0 | NOx: 4.65 PM10: 0.083 | SU8085798412 | No | 35.11
Plant 13 | TBC | Moteurs Baudouin | 16M55G3000/5 | 480813.23 | 198480.84 | 0 | 0 | 0 | 6.18 | Back up generator | Gas oil | 0 | 0 | 0 | Yes | 5 | 0 | 0.9 | 6.2094 | 11 | No | Buckinghamshire | 200.6285 | Residential façade | 241.9528 | Slough Hill LWS | No | 0 | 0 | NOx: 4.65 PM10: 0.083 | SU8081398480 | No | 35.11
Plant 31 | TBC | Moteurs Baudouin | 16M55G3000/5 | 480636.37 | 198519.11 | 0 | 0 | 0 | 6.18 | Back up generator | Gas oil | 0 | 0 | 0 | Yes | 5 | 0 | 0.9 | 6.2094 | 11 | No | Buckinghamshire | 49.1907 | Residential façade | 205.1165 | Slough Hill LWS | No | 0 | 0 | NOx: 4.65 PM10: 0.083 | SU8063698519 | No | 35.11
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | 0
Named Range | Value | [6 empty] | MCP-DateCommissioned | ThermalInput | MCP-CombustionTechnology | MCP-FuelMain | MCP-FuelSec | MCP-FuelSecWhen | MCP-FuelUsageSec | MCP-Limitedhrs |  | MeetnewELV | MCP-Loadas% | MCP-BackgroundNO2 | MCP-StackHeight | AQMA | AQMA LA | HumanReceptor | MCP_HumanReceptorDetails | EcoReceptor | MCP_EcoReceptorDetails | MCP-Abated | MCP-AbateType | MCP-CapBalAgree
MobilePlant | No
NaceCode | 35.11
Plant Name | Plant Name
_1136 | Serial No. of Plant (If already purchased)
_1333 | Plant Manufacturer
_1234 | Model Name
Easting | Easting
Northing | Northing
Lat | Lat
Long | Long
_1224 | Commissioning Date
_1137 | Size (MWth)
_1118 | Technology
_1125 | Fuel/Main Fuel
IF an individual plant uses more than one fuel, give the proportions | IF an individual plant uses more than one fuel, give the proportions
0 | 0
02 | 0
03 | 0
04 | 0
Stack Height (metres) | Stack Height (metres)
_1027 | If new plant does the flue share a common windshield?
_1062 | Annual Hours
_1328 | Limited Operating Hours
_1021 | Annual Load (%)
_1121 | In AQMA
_1117 | AQMA Local Authority
_1124 | Closest Human Receptor (metres)
_2005 | Human Receptor Details
_1016 | Closest Ecological Receptor (metres)
_2006 | Ecological Receptor Details
_1015 | Background NO2 (μg/m3)
_1150 | Will secondary abatement be fitted to the plant?
_1040 | Abatement Type
_1326 | Will Meet New ELVs

## Sheet1
Compatibility Report for 6. MCP-generator-list-v3 (1).xls
Run on 29/05/2025 17:01
If the workbook is saved in an earlier file format or opened in an earlier version of Microsoft Excel, the listed features will not be available.
Minor loss of fidelity | # of occurrences | Version
Some cells or styles in this workbook contain formatting that is not supported by the selected file format. These formats will be converted to the closest format available. | 24 | Excel 97-2003