## 1.Risk assessment
1.1 | Source
For the purposes of the ABDA Assessment, assets containing sludge have been listed only
| Name | Number | Physical properties | Maximum quantity | units | Storage | Flammability | Corrosive | Ecotoxicity (based on LD and quantity) | Hazard rating
| Digesters | 2 | Digested Sludge | 2354 | m3 | Glass Fused Steel above ground tank | Methane produced is flammable Digestate isn't flammable | Low | Organic heavy - Nitrogen, Phosphorous, Ammonia, BOD, TSS, COD - Environmental hazard (algae blooms and death of organisms) | M
| Digester Feed Tank/Thickening sludge tank | 1 | Raw Sludge | 478 | m3 | GRP above ground tank | Low | Low | Organic heavy - Nitrogen, Phosphorous, Ammonia, BOD, TSS, COD - Environmental hazard (algae blooms and death of organisms) | M
| Screened sludge tank | 2 | Raw Sludge | 1000 | m3 | Concrete above ground tank | Low | Low | Organic heavy - Nitrogen, Phosphorous, Ammonia, BOD, TSS, COD - Environmental hazard (algae blooms and death of organisms) | M
| Digestate/ Digested sludge tank | 1 | Digested Sludge | 1564 | m3 | Steel above ground tank | Methane produced is flammable Digestate isn't flammable | Low | Organic heavy - Nitrogen, Phosphorous, Ammonia, BOD, TSS, COD - Environmental hazard (algae blooms and death of organisms) | M
| Sludge import tank | 1 | Raw Sludge | 45 | m3 | Steel above ground tank | Low | Low | Organic heavy - Nitrogen, Phosphorous, Ammonia, BOD, TSS, COD - Environmental hazard (algae blooms and death of organisms) | M
| Sequential Batch Reactor (SBR) Balance Tank | 1 | Digested Sludge | 783 | m3 | Steel above ground tank | Low | Low | Organic heavy - Nitrogen, Phosphorous, Ammonia, BOD, TSS, COD - Environmental hazard (algae blooms and death of organisms) | M
| SBR Tank | 2 | Digested Sludge | 1172 | m3 | Steel above ground tank | Low | Low | Organic heavy - Nitrogen, Phosphorous, Ammonia, BOD, TSS, COD - Environmental hazard (algae blooms and death of organisms) | M
| Cake silo | 1 | Raw Cake | 240 | m3 | Steel bay | Low | Low | Organic heavy - Nitrogen, Phosphorous, Ammonia, BOD, TSS, COD - Environmental hazard (algae blooms and death of organisms) Pathogens - Human hazard (E.coli etc.) | M
| Emergency cake silo | 1 | Raw Cake/Treated Cake | 200 | m3 | Brick bay | Low | Low | Organic heavy - Nitrogen, Phosphorous, Ammonia, BOD, TSS, COD - Environmental hazard (algae blooms and death of organisms) Pathogens - Human hazard (E.coli etc.) | M
[8 empty] | Overall | M
|  |  | Total Volume | 11922 | m3
|  |  | 25% Volume | 2980.5 | m3 | 25% volume to be taken forward.
|  |  | 110% Largest Tank (Digestor) | 2589.4 | m3
1.2 | Pathway and Receptor
Figure 1.1 - Source
Figure 1.2 - Pathway
Figure 1.3 Receptor
| Pathway - the route from primary containment to receptor (extent of loss of containment) |  | Time of concentration/ duration of source outside containment |  | Hazard - Transport potential |  |  | Receptor | Hazard - Damage potential
| Tanks are surrounded by, grass, permeable stone and impermeable concrete Based on available ground information, soil is permeable and will act as a pathway |  | Direct contamination but over an extended period of time |  | L |  |  | Watercourse and bodies
| If permeable area gets saturated (high groundwater or due to the area flooding as the treatment works is in Flood Zone 3) or becomes blocked with sludge, areas will act as impermeable and transport sludge downstream and towards the River Wye which is a SSSI. |  | Direct contamination but over an extended period of time |  | M |  |  | Groundwater - contaminated through percolation through soil or through fluctuating tidal groundwater level Site is not located within 250m of a Source Protection Zone (SPZ), however the entire site and locality lie in a drinking water protected area (surface water) and within a Secondary A aquifer. Over a very long period, can contaminate river through groundwater base flow underground | M
| Seasonally fluctuating groundwater |  | Direct contamination but over an extended period of time |  | M |  |  | Sludge storage within 50m of the River Wye, which is designated as a Site of Special Scientific Interest (SSSI) and Special Area of Conservation (SAC). The area is also in a Nitrate Vulnerable Zone (NVZ) | H
| Existing underground services - ductwork, troughs, pipework. |  | Direct contamination but over an extended period of time |  | L |  |  | Local environment including grassy area - through overland flow from uncontrolled spill. <5m away | M
| There is impermeable concrete surfacing on site If inventory is cascaded onto road, sludge will be transported along the road surface into the road gullies and into the site drainage system. |  | Minutes - hours |  | M |  |  | WWTW - internal drainage system returns effluent to the head of the works prior to discharge into the River Wye | M
| If the drainage channel were to get blocked, it may overflow locally to the permeable surrounding area. |  | Minutes - hours |  | M |  |  | Habitation
|  |  | Overall |  | M |  |  | No dwelling or workplace within 250m of the site | L
Other
[8 empty] | River Wye SSSI within 50m of the site | H
[8 empty] | Overall | H
| Combination of Hazards | MMH
| Overall risk rating for zone (Ciria 736) | High
1.3 | Frequency of loss of containment
In terms of likelihood of a loss of containment, CIRIA 736 provides these guidelines on quantifying the likelihood...
To derive the likelihood for your site, firstly, using the completed risk descriptions and any additional risks identified at your site ask yourself how often will the risk occur and cause a loss of primary containment.
Secondly, consider any mitigation (see the examples provided in the table starting below row 50 for guidance) and apply the reduced likelihood.
Finally, select the likelihood by applying the fact that the highest likelihood gives the site's overall likelihood.
| Failure mode | Description | Existing consequence and mitigation measure | [6 empty] | Annual probability of loss of containment | Rating
| Operational failure - tank (partial) | Overfilling/overflow of tank Foaming | All tanks have high level overflows which connect to a gravity pipe feeding the digested sludge holding tanks in both the digester and screening stages when levels within the tanks are too high. Sludge supplied to the digesters displace the existing digestate and sludge overflows. The digestor tanks are all covered. In the unlikely event when there is an overflow (overflows blocked and non working volume is filled), the volume lost would be minimal as the pumps can be inhibited by operators present onsite. Foaming is a very general failure mode for digesters. Foaming could occupy up to 2m of height within the digesters. Otherwise, automated and operator safeguards are in place to control or inhibit the process if there is a foaming risk. Total loss of containment is not credible when considering overflowing or foaming of the tank (partial loss of containment would be more likely to occur but is still very unlikely). | [6 empty] | 1 in 100 to 1 in 1 Million | M
| Structural failure - tank (catastrophic) | Catastrophic failure due to significant external damage Potential to lose total volume if mixer pipework fails/break off of tank - has been a failure mode for digesters in the past | Tanks are located above ground. In the case of significant damage above ground during operation or maintenance, the total volume contained above ground could be lost. It is not credible for the tanks to fail catastrophically structurally as the tank is fit for purpose. The tanks were originally designed and constructed to hold hydrolysed sludge and have been operating with no notable concerns. The tanks could lose their full inventory if the pipe connections to the tank fail/break off and fail catastrophically, causing a rupture/hole in the tank, through which the total inventory is lost as mixer pipework is located near the bottom of the digester tanks. This pipework is supported and the connections in the tank wall are cast in with puddle flanges and hydrophilic water bars so this type of failure is not a credible scenario. The tanks are not hydraulically linked so failure of one tank would not result in the loss of containment of additional tanks. | [6 empty] | > 1 in 1 Million | L
| Structural failure - tank (partial) | Most likely through cracks formed in concrete Most critical cracks would be large cracks at low level along the side of the tank walls or tank base. Cracks would need to be large >6mm to allow for sludge to pass through the crack freely. General screens at WwTW are 6-10mm, thus cracks would need to be in the same range to allow for sludge to pass freely. Roof failure | Tanks are located above ground. Any significant loss of containment, would spill above ground. Structural failure of tanks would mainly be through cracks. In the case of significant cracks forming above ground, the volume contained above ground would seep through the cracks . If the cracks are significant (>6mm), the tank could potentially lose the above ground volume over a long period of time. This would be identified promptly by operators and the process inhibited immediately. The tanks have been designed as double skinned tanks and constructed to the appropriate code for water retaining concrete structures or steel structures so this could only reasonably be assumed to occur if the tanks were operated well in excess of their design life without appropriate maintenance or any refurbishment. As the site is manned, large drops in levels in the tanks and significant leaks above ground would be noticed. Significant cracks below/above ground would also be easily spotted if tanks are inspected throughout their design life. Partial loss of containment from cracks is still highly unlikely and safeguards are in place to mitigate the impact of such a leak. | [6 empty] | > 1 in 1 Million | L
| Structural failure - pipework (catastrophic) | Loss of containment due to failure of above ground connecting pipework and rising mains | In the extremely unlikely event where the above ground pipework or valves fail completely, the total above ground volume could be lost, if the valves are not closed by operational staff or tanks are not drained down to limit loss of containment. As the site is manned, valves can be closed and operated by operational staff if the pipes were to fail and automated safeguards did not function as intended. Due to the makeup of some of the tanks (glass reinforced steel), total loss of containment is considered a rare but credible scenario. Partial loss of containment is however more likely but still considered an unlikely occurance. | [6 empty] | > 1 in 1 Million | L
| Structural failure - pipework (partial) | Loss of containment most likely to occur where there are weak points in the pipework - Most likely through failures where pipe connects with the structure, bolts/sealant at pipe flanges/valves or along any pipe pitting. Weak point could be created through either human damage (during maintenance/operation), erosion (high velocities and silt content within the pipe) or environmental (corrosion) Valve failure/seizure | All pipework above ground is carbon or stainless steel. If loss of containment occurs above ground through leaks or damage to pipework, it will cascade onto road and concrete hardstanding. Due to the impermeable external surfacing around the concrete bunds, the majority of the sludge from leaks at valves/mixers would be contained within the hardstanding area within the bund and, if significant, cascade into the gullies within the chambers and ultimately to the head of the works. The quantities of sludge involved is not expected to have an adverse impact on the wastewater treatment process. Any significant leaks/damage to above ground pipes would be noticed by staff on site and loss of containment would be mitigated through operational measures (closing of valves and isolation of tanks/pipework - as detailed in the accident managment plan). This can be achieved quickly due to the manned presence and daily inspection regime. Due to the makeup of some of the tanks (glass reinforced steel), total loss of containment is considered a rare but credible scenario. Partial loss of containment is however more likely but still considered an unlikely occurance. | [6 empty] | 1 in 100 to 1 in 1 Million | M
| Vehicular impact (partial to catastrophic) | Impact from vehicles - damage to pipes or tank causing loss of containment | No known vehicle impacts. No visible protection in the form of guard rails. | [6 empty] | 1 in 100 to 1 in 1 Million | M
| Vandalism | Vandalism of infrastructure - damage to pipes or tank causing loss of containment | No known vandalism to tanks or pipework - CCTV cameras and gates on site. Boundary protected by temporary fencing in places. If vandalism damage were to occur, total loss of containment is unlikely due to type of inventory. Partial loss of containment would be more likely to occur if slight damage was done. | [6 empty] | 1 in 100 to 1 in 1 Million | M
| Flooding | River flooding - Flood zone 3 - damage to pipes or tank causing loss of containment | The site is located within Flood Zone 3 for the River Wye which is a SSSI. The area according to the government long term flood risk website (https://check-long-term-flood-risk.service.gov.uk/map?easting=352884&northing=238182&map=RiversOrSea) is at high risk of flooding, which a chance of flooding of greater than 3.3% each year. There are no areas of the proposed permit boundary indicated as being affected by groundwater flooding. | [6 empty] | Greater than 1% (1 in 100) | H
*Site is manned. Probability and frequency thus reduced
| Frequency of loss of containment (Ciria 736) | M
1.4 | Overall zone hazard rating
| Overall zone hazard rating (Ciria 736) | High
1.5 | Containment required
| Containment required | Class 3
Digesters (2No 2,354 m3)
Digestate/ Digested sludge tank (1,564 m3)
Screened Sludge Tank (2No 1,000 m3)
Thickening Sludge Tank (478 m3 / 750m3)
SBR Balance Tank (783 m3)
SBR Tanks (2No 1,172 m3)
Cake Silo (240 m3)
Emergency Cake Silo (200 m3)
Sludge Import Tank (45 m3)
Permeable ground
Impermeable ground
River
50m
Grassy area & trees - potential ecology
Grassy area & trees - potential ecology
Grassy area & trees - potential ecology
55m
120m

## 2.Total vol. - Mitigation
2.1 | Catastrophic failure - modes (loss of containment)
| Risk | Cause | Existing consequence and mitigation measure | Existing zone risk rating | Proposed Mitigation | Risk rating after mitigation
|  | Operational failure - tank (partial) | All tanks have high level overflows which connect to a gravity pipe feeding the digested sludge holding tanks in both the digester and screening stages when levels within the tanks are too high. Sludge supplied to the digesters displace the existing digestate and sludge overflows. The digestor tanks are all covered. In the unlikely event when there is an overflow (overflows blocked and non working volume is filled), the volume lost would be minimal as the pumps can be inhibited by operators present onsite. Foaming is a very general failure mode for digesters. Foaming could occupy up to 2m of height within the digesters. Otherwise, automated and operator safeguards are in place to control or inhibit the process if there is a foaming risk. Total loss of containment is not credible when considering overflowing or foaming of the tank (partial loss of containment would be more likely to occur but is still very unlikely). | M | Due to the high level overflows in place overfilling is not a risk. There have been no cases of overflow/overfilling reported by the operational team. Foaming could occur, if a mixer fails or the digestate composition is different. As foaming cannot be completely mitigated through anti-foaming measures, secondary containment should be provided for a proportion of digester volume. Possible foaming volume to be accommodated is assumed to be 1m of each digester. In the unlikely event that tank loses significant containment above ground sludge will cascade towards the access road and eventually into the drainage system, based on the site topography. Only competent and trained staff operate the site. The zone is robust and safe provided the permeable areas around the digesters (gravel/stone) is replaced with impermeable hardstanding to remove the pathway to the ground and containment is provided to contain the foaming volume within the site. | L
|  | Structural failure - tank (catastrophic) | Tanks are located above ground. In the case of significant damage above ground during operation or maintenance, the total volume contained above ground could be lost. It is not credible for the tanks to fail catastrophically structurally as the tank is fit for purpose. The tanks were originally designed and constructed to hold hydrolysed sludge and have been operating with no notable concerns. The tanks could lose their full inventory if the pipe connections to the tank fail/break off and fail catastrophically, causing a rupture/hole in the tank, through which the total inventory is lost as mixer pipework is located near the bottom of the digester tanks. This pipework is supported and the connections in the tank wall are cast in with puddle flanges and hydrophilic water bars so this type of failure is not a credible scenario. The tanks are not hydraulically linked so failure of one tank would not result in the loss of containment of additional tanks. | L | Original tank construction was reinforced concrete (2010). The construction is fit for purpose and there are no credible scenarios identified that could lead to catastrophic failure. If severe damage does occur, operational staff can isolate the tank and drain it down as an emergency response, reducing the loss of containment as they will be in the vicinity of the tank. To reduce the likelihood of loss of containment, the tanks should be structurally inspected on an annual basis by a competent engineer. The tanks should then be refurbished if necessary. Ultrasonic meters in tanks should be alarmed if there is a significant and unanticipated drop in level to mitigate any significant loss of containment. To allow for some loss of containment due to catastrophic failure or significant mixer connection leakage (pre-failure), secondary containment to allow for minimum of 500mm of digester height volume loss until tank is drained down by operational staff. In the case of valve seizure (double jeopardy) - Allow for an additional 250mm of volume loss (750mm in total). The zone is robust and safe provided the permeable areas around the digesters (gravel/stone) is replaced with impermeable hardstanding to remove the pathway to the ground and secondary containment is provided to contain the potential volume loss of the digester within the site. | L
|  | Structural failure - tank (partial) | Tanks are located above ground. Any significant loss of containment, would spill above ground. Structural failure of tanks would mainly be through cracks. In the case of significant cracks forming above ground, the volume contained above ground would seep through the cracks . If the cracks are significant (>6mm), the tank could potentially lose the above ground volume over a long period of time. This would be identified promptly by operators and the process inhibited immediately. The tanks have been designed as double skinned tanks and constructed to the appropriate code for water retaining concrete structures or steel structures so this could only reasonably be assumed to occur if the tanks were operated well in excess of their design life without appropriate maintenance or any refurbishment. As the site is manned, large drops in levels in the tanks and significant leaks above ground would be noticed. Significant cracks below/above ground would also be easily spotted if tanks are inspected throughout their design life. Partial loss of containment from cracks is still highly unlikely and safeguards are in place to mitigate the impact of such a leak. | L | In the event that tank loses containment above ground, through structural failure (cracks), sludge would weep through the cracks at a very slow rate. The volume would slowly flow down the side of the tank and gather around the tank. To reduce the likelihood of loss of containment, the tanks should be structurally inspected on an annual basis by a competent engineer. The tanks should then be refurbished if necessary. Ultrasonic meters in tanks should be alarmed if there is a significant and unanticipated drop in level to mitigate any significant loss of containment. The zone is robust and safe provided the permeable areas around the tanks are replaced with impermeable hardstanding to remove the pathway to the ground. Associated drainage would connect to the inlet works. The tanks should be inspected on at least an annual basis by a competent engineer in addition to the current maintenance strategy. This can be undertaken during the sludge plant's annual maintenance and inspection shutdown. No further mitigation is considered to be necessary. | L
|  | Structural failure - pipework (catastrophic) | In the extremely unlikely event where the above ground pipework or valves fail completely, the total above ground volume could be lost, if the valves are not closed by operational staff or tanks are not drained down to limit loss of containment. As the site is manned, valves can be closed and operated by operational staff if the pipes were to fail and automated safeguards did not function as intended. Due to the makeup of some of the tanks (glass reinforced steel), total loss of containment is considered a rare but credible scenario. Partial loss of containment is however more likely but still considered an unlikely occurance. | L | If catastrophic failure of the above ground pipework occurs (i.e. rising main pipe failure), the pumps have the necessary pressure controls to switch off the pumps to minimise the loss of containment. The volume contained in the pipe length should still be contained. Additional secondary containment is not proposed and volume is assumed will be able to be accommodated in the new hardstanding area around the tank and pipework within the drainage system. The zone is robust and safe provided the permeable areas around the tanks are replaced with impermeable hardstanding to remove the pathway to the ground. Associated drainage would connect to the inlet works. The above ground pipework should continue to be regularly inspected during daily and weekly inspections to enable proactive maintenance when required. Below ground pipework and chambers should be inspected on an annual basis to check their integrity. | L
|  | Structural failure - pipework (partial) | All pipework above ground is carbon or stainless steel. If loss of containment occurs above ground through leaks or damage to pipework, it will cascade onto road and concrete hardstanding. Due to the impermeable external surfacing around the concrete bunds, the majority of the sludge from leaks at valves/mixers would be contained within the hardstanding area within the bund and, if significant, cascade into the gullies within the chambers and ultimately to the head of the works. The quantities of sludge involved is not expected to have an adverse impact on the wastewater treatment process. Any significant leaks/damage to above ground pipes would be noticed by staff on site and loss of containment would be mitigated through operational measures (closing of valves and isolation of tanks/pipework - as detailed in the accident managment plan). This can be achieved quickly due to the manned presence and daily inspection regime. Due to the makeup of some of the tanks (glass reinforced steel), total loss of containment is considered a rare but credible scenario. Partial loss of containment is however more likely but still considered an unlikely occurance. | M | The above ground pipework is located within the bunded area so will have secondary containment. Based on experience the volume that could be lost due to above ground pipework leaks is minimal. Significant leaks would be spotted by operational staff during their daily inspection (site is also manned) and repaired and any loss of containment mitigated. The volume lost to leaks would be able to be contained in the new hardstanding area around the tanks (replacing the permeable stone) and drainage pipework. No secondary containment required. Sludge would seep through the leaks at a very slow rate. The volume would slowly flow down the side of the pipe and gather around the pipework. The actual volume lost would be minimal. In the unlikely event that there is significant loss of containment through pipework above ground, based on topography and the type of inventory, loss of containment would be limited to the hardstanding area around the pipework and the stone area around the digesters. Jetting from leaks in the pipework shall be contained within the bunded area. The zone is robust and safe provided the permeable areas around the tanks is replaced with impermeable hardstanding to remove the pathway to the ground. Associated drainage would connect to the inlet works. The above ground pipework should continue to be regularly inspected during daily and weekly inspections to enable proactive maintenance when required. Below ground pipework and chambers should be inspected on an annual basis to check their integrity. | L
|  | Vehicular impact (partial to catastrophic) | No known vehicle impacts. No visible protection in the form of guard rails. | M | The existing measures mitigate any potential impacts from vehicles within the site and potential damage which could lead to loss of containment. There is however a risk of vehicles impacting the digesters from the road adjacent to the site. Additional vehicular impact protection is recommended to be installed and temporary fencing replaced with permanent fencing. | L
|  | Vandalism | No known vandalism to tanks or pipework - CCTV cameras and gates on site. Boundary protected by temporary fencing in places. If vandalism damage were to occur, total loss of containment is unlikely due to type of inventory. Partial loss of containment would be more likely to occur if slight damage was done. | M | If pipes and the tank get damaged, because it is operated on a daily basis with operational staff present, the risk of loss of containment is low. If there are any signs of damage due to vandalism operators will fix any damage first. No mitigation measures proposed, existing measures deemed adequate. | L
|  | Flooding | The site is located within Flood Zone 3 for the River Wye which is a SSSI. The area according to the government long term flood risk website (https://check-long-term-flood-risk.service.gov.uk/map?easting=352884&northing=238182&map=RiversOrSea) is at high risk of flooding, which a chance of flooding of greater than 3.3% each year. There are no areas of the proposed permit boundary indicated as being affected by groundwater flooding. | H | The containment that will be constructed to comply with IED regulations will also likely reduce the flood risk of the treatment works site from the River Wye. During optioneering, the risk of negatively impacting flood risk elsewhere needs to be mitigated. If the treatment works site is still classified as a flood zone following containment construction, procedures need to be agreed and adopted in the event of the treatment works site flooding to minimise pollutants from the site returning into the River Wye when the flood waters recede. | L
Implementing the above measures will significantly reduce the probability and risk of failure from the concrete tanks and significantly reduce the amount of secondary containment. As per CIRIA 736, the above will need to be implemented in conjunction with a good maintenance strategy as mentioned in Box 5.2,Page 60.

## 3.Containment volume-Total vol.
3.1 | Secondary containment volume requirement - Inventory volume (above ground)
| All Tanks | 11922 | m3 | (Inventory volume - above ground below overflow)
| Total volume | 11922 | m3
25% rule (CIRIA 736)
| *25% of all tanks | 2980.5 | m3
| Secondary storage to be provided | 2980.5 | m3
*Note that 10% includes for rainfall and is the minimum allowable storage that can be provided
3.2 | Loss of containment - Time to empty fully
Quick estimation of rate of loss of containment. Modelling will, however, simulate an instantaneous failure of the full volume
Rate of flow from tank:
| Tank volume |  |  | 2980.5 | m3
| Diameter of pipe (d) |  |  | 0.25 | m
| Area |  |  | 0.049087 | m2
| Discharge coefficient (Cd) |  |  | 0.61
| Gravitational acceleration (g) |  |  | 9.81 | m/s2
| Height within tank (H),m | Flow rate (Q) m3/s | Diameter of Tank(m) | Volume in tank (m3) - above ground | % volume lost | Time to drop in level (min) | Time to empty (cumulative) - min
| 12 | 0.45945 | 15.02 | 2126.2337 | 28.66% |  | 0
| 11 | 0.43989 | 15.02 | 1949.0475 | 34.61% | 6.4274 | 6.4274 |  | Height of tank taken from largest tank (digester) within the site
| 10 | 0.41942 | 15.02 | 1771.8614 | 40.55% | 6.7133 | 13.1407
| 9 | 0.3979 | 15.02 | 1594.6753 | 46.5% | 7.0409 | 20.1816
| 8.5 | 0.38669 | 15.02 | 1506.0822 | 49.47% | 3.7109 | 23.8925
| 8 | 0.37514 | 15.02 | 1417.4891 | 52.44% | 3.8185 | 27.711
| 7.5 | 0.36323 | 15.02 | 1328.896 | 55.41% | 3.936 | 31.647
| 7 | 0.35091 | 15.02 | 1240.303 | 58.39% | 4.0651 | 35.712
| 6.5 | 0.33815 | 15.02 | 1151.7099 | 61.36% | 4.2078 | 39.9198
| 6 | 0.32488 | 15.02 | 1063.1168 | 64.33% | 4.3666 | 44.2864
| 5.5 | 0.31105 | 15.02 | 974.5238 | 67.3% | 4.5449 | 48.8313
| 5 | 0.29657 | 15.02 | 885.9307 | 70.28% | 4.747 | 53.5783
| 4.5 | 0.28136 | 15.02 | 797.3376 | 73.25% | 4.9787 | 58.557
| 4 | 0.26526 | 15.02 | 708.7446 | 76.22% | 5.248 | 63.8049
| 3.5 | 0.24813 | 15.02 | 620.1515 | 79.19% | 5.5663 | 69.3713
| 3 | 0.22973 | 15.02 | 531.5584 | 82.17% | 5.9507 | 75.3219
| 2.5 | 0.20971 | 15.02 | 442.9653 | 85.14% | 6.4274 | 81.7494
| 2 | 0.18757 | 15.02 | 354.3723 | 88.11% | 7.0409 | 88.7903
| 1.5 | 0.16244 | 15.02 | 265.7792 | 91.08% | 7.872 | 96.6623
| 1 | 0.13263 | 15.02 | 177.1861 | 94.06% | 9.0898 | 105.7521
| 0.5 | 0.093785 | 15.02 | 88.5931 | 97.03% | 11.1327 | 116.8847
| 0 | 0 | 15.02 | 0 | 100% | 15.744 | 132.6287 | Minutes to empty to ground level

## 4.Current asset evaluation
4.1 | Current Asset Evaluation | Digester 01
| Description | Digesters
| Number of tanks | 2
| Volume of tank | 2,354m3 - total volume
| Material of tank | Glass Reinforced Steel
| Above/below ground? | Above ground
| Pipe material | Above ground - Stainless steel
| Drainage for zone | Infiltration through grass around tanks
| Year of construction | 2010
| Surrounding area | grass -permeable Access road is tarmac - impermeable Some areas are concrete - impermeable
| Is asset fit for purpose? | The tanks were originally designed and constructed to hold hydrolysed sludge and has been operating with no notable concerns. The tank has not undergone a change of use.
| Condition of the tank Any tank failures - cracks, flaking, corrosion, overflows, overfilling? | The tank is in good condition with no structural or serviceability cracks or other signs of deterioration.
| Condition of pipework Pipe leaks, corrosion? | The pipework is in good condition with no structural or serviceability cracks or other signs of deterioration.
| Protection of assets - bollards? | None visible
| Control/monitoring/alarming measures in place? | Flow controlled to digesters - level and temperature in digester, failure of recirculation or mixing pumps. Level and temperature sensors within each digester. Automated inhibits if the process falls outside normal operating parameters.
| Secondary containment provided? | Tanks are all double skinned. Containment to be provided as part of this scheme
| Secondary containment condition? | Good condition

## 5.Containment type-Total vol.
5.1 | Containment to be provided
Based on a Medium site risk rating for the zone, Class 2 containment is required. Bunds, as shown below, or concrete walls will be used
Typical Bund section view
Typical reinforced concrete wall section view
5.2 | Catastrophic failure
Catastrophic failure assumes the tank loses all its above ground volume and that the total volume would need to be contained.
Location
Suitability of containment to be provided
| Type |  | Applicability
| Reinforced concrete/masonry flooring and bund |  | Due to relatively large volume from loss of containment, use of a masonry/concrete bund is generally not appropriate for local containment in this scenario. Due to the limited space available around the area, the use of masonry/concrete bunds is however applicable
| Earth banked basins, bunds and flooring |  | Soil within site is of permeable nature - Clay or impermeable soil type not plentiful Potential for stabilised soil (lime and cement used to make it impermeable) for bund construction. Area of which bunding can be provided is however limited - assuming for example a bund height of 300mm, crest width of 100m, side slopes of 1:3 - a base width of the bund of at least 2000mm is required. Dependant on area required and nature of surrounding area, might be applicable Not applicable within the digester area.
| Containment tank |  | Nature of catastrophic failure and type of primary containment makes use of a containment tank not appropriate
5.3 | Catastrophic failure in existing situation (Do Nothing) - Visualisation
Figure 5.3.1 Visualisation of Do Nothing Option
5.4 | Type of containment to be provided
Proposed Option: Local containment
Volume is proposed to be contained within the site and will be constructed within the treatment works site boundary. Where currently permeable (stone and grass), to be made impermeable with either converting this to a concrete surface or via lining. Mobile pumps to be used to remove volume from bund from the low point. Daily operational inspection to ensure any rainfall runoff within the bund is removed.
Walls to be constructed ranging up to 2.8 m with the addition of freeboard. This would limit flow throughout the entire site and contain it to the site boundary. To enable access into the walled area, 2No. floodgates are proposed to be constructed at road crossing points. The floodgates shall be designed to meet British Standard BS 851188 for flood defense systems and shall be finshed with a coating with a minimum C3 rating (ISO 12944).
Figure 5.4.1. Proposed Option - Bunded Zone
Figure 5.4.2. Proposed Option - Impermeable Zone
Figure 5.4.3. Visualisation of Proposed Option
| Advantages | Bunded wall heigt follow Ciria 736 guidelines for secondary containment. Bund shall maintain failure volume even during a flood event by preventing flood water entering the zone. Sludge is kept on-site and out of the identified receptors outside the site boundary. Spills from any tanks registered in the IED permit are contained in case of failure. This option protects key receptors
| Disadvantages | Bunded zone will require revised operation and maintenance processes. Flood gates are required for vehicle (skip, tanker, maintenance) access, must remain closed in the event of a catastrophic failure. Sludge is contained over a large area