DAF Daily Report – Date:  28.08.26

| Balance Tank Level | 76% >75% TO DAF |
| --- | --- |
| Flow Through DAF (meter from Balance tank to DAF) | 240m3 |
| Flow to Wetlands(Slip Inn meter) All wastewater not gone through MBR | 165m3 |
| Final Pond 7 depth Pond with emergency spillway to stream-aim not to allow over spillway. Water also used for irrigation to orchards | Below Board >75cms |
| Flow to Reed Bed from MBR Maximum throughput of MBR 300m3 | 234m3 >150-300 |
| Flow to Reed bed from Pond 7 | 0 m3 |
| Flow to Pond 4 recirculation | 0 m3 |
| Flow to Orchards | 0 m3 |
| Dosing rate and type | Urea dose @ 8 L/hr Phosphoric acid @ 0.8 L/hr |
| Discharge to Brook via V notch Max. Flow 2.35l/s or 200m3 per day is consent limit with the E.A | Daily Total: 152 m3 100-200m3 |
| MLSS Normal Working -Limits 6000-12000 | 9192 6000 - 12000 |
| Total from Site (Slip Inn plus MBR discharge) | 441m3 |
| RAINFALL | NRmm |
| AS Tank Temperature If seen to be increasing suggest bugs working generating heat | Falling oC – 35.3c |
| Any other comments | Temperature fallen – 0.1c |