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DAF Daily Report – Date:  28.08.26
	                       Balance Tank Level

	76%

>75% TO DAF

	Flow Through DAF
(meter from Balance tank to DAF)
	240m3

	Flow to Wetlands(Slip Inn meter)
All wastewater not gone through MBR
	165m3


	Final Pond 7 depth
Pond with emergency spillway to stream-aim not to allow over spillway. Water also used for irrigation to orchards
	                               Below Board     
                                       
>75cms

	Flow to Reed Bed from MBR
Maximum throughput of MBR 300m3

	234m3
                                                                
>150-300

	Flow to Reed bed from Pond 7
	0 m3 

	Flow to Pond 4 recirculation
	0 m3

	Flow to Orchards 
	 	       0 m3 

	 Dosing rate and type
	Urea dose @   8 L/hr
Phosphoric acid @ 0.8   L/hr 

	Discharge to Brook via V notch
Max. Flow 2.35l/s or 200m3 per day is consent limit with the E.A

	Daily Total:  152  m3
                                                       
100-200m3

	MLSS
Normal Working -Limits 6000-12000 
	9192
 [image: ] 6000 - 12000

	Total from Site (Slip Inn plus MBR discharge)
	441m3

	RAINFALL
	NRmm

	AS Tank Temperature
If seen to be increasing suggest bugs working generating heat
	         [image: ]Falling  oC – 35.3c

	Any other comments
	Temperature fallen – 0.1c 
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