## Flare
INPUT Data
| Total Gas Flow Rate at STANDARD Temperature (m3/s): | 14.9744 | Standard temperature is the feed gas, not the flare exit temperature
| STANDARD Temperature of Feed Gas (K): | 273.15 | Standard temperature is the feed gas, not the flare exit temperature
| Actual Stack Diameter (m) | 4 | This is the flare chamber diameter
| Stack Height (m): | 10 | This is the physical stack height
| Heat Radiation Loss (%) | 25 | Leave as default (25%), unless site specific data provided otherwise
| Conversion Efficiency for SO2 (%) | 98 | Leave as default (98%), unless site specific data provided otherwise
| Ambient Temperature (K): | 283.4272 | Obtain from meteorological data for site
| Flare combustion temperature (K): | 1273 | Leave as defaul 1273 unless specific temperatuer known
| Gas Component | Gas fraction (%Volume)
| CH4 | 0.032033
| C2H6 | 0
| C3H8 | 0
| C4H10 | 0
| C5+ | 0
| H2 | 0.96797
| H2S | 0
| Non-combustible fraction (N, H2O, CO2 etc.) | 0
| Total | 1 | This value must equal '1'
OUTPUT Data
| Emission Temperature (K) | 1273
| Exit Velocity (m/s): | 5.7625
| Effective Stack Height (m) | 29.4884
| Equivalent Stack Diameter (m): | 9.9821
|  |  | g/y | 1 event per year, taking 1 hr
| Emission Rate of SO2 (g/s): | 0 | 0
| Emission Rate of H2S (g/s): | 0 | 0
| Emission Rate of Hydrocarbons (g/s): | 9.9205 | 35713.8485
| Emission Rate of CO (g/s): | 26.2185 | 94386.5995
| Emission Rate of NOx (g/s): | 4.8185 | 17346.7264
| Emission Rate of PM non-smoking flares (g/s): | 0
| Emission Rate of PM light-smoking flares (g/s): | 0.59898
| Emission Rate of PM average-smoking flares (g/s): | 2.6505
| Emission Rate of PM heavy-smoking flares (g/s): | 4.103
CALCULATION DATA
CALCULATION SHEET FOR FLARES |  |  |  |  | VER. 3.0
Source: Alberta Environmental Sustainable Resource Development (ESRD) https://static.aer.ca/prd/documents/directives/Directive060.pdf
USER SUPPLIED INPUTS (GREY CELLS)
at flame temp
| Total Gas Flow Rate at Reference Temperature (m3/s): | 14.9744 | 69.7875
| Actual Stack Diameter (m) | 4
| Stack Height (m): | 10
| Heat Radiation Loss (%) | 25
| Conversion Efficiency for SO2 (%) | 98
| Ambient Temperature (K): | 283.4272
| Standard Temperature (K): | 273.15
| Gas Component | Gas Fraction | Gas Flow Rate | Low Heat Value at 15.6C and 101.3kPa | Heat Release
|  |  | m3/s | MJ/m3 | MJ/s
| CH4 | 0.032033 | 0.47968 | 34 | 16.309
| C2H6 | 0 | 0 | 61.1 | 0
| C3H8 | 0 | 0 | 88.8 | 0
| C4H10 | 0 | 0 | 116.2 | 0
| C5+ | 0 | 0 | 138.2 | 0
| H2 | 0.96797 | 14.4948 | 10.246 | 148.5134 | Fuel Gases - Heating Values (engineeringtoolbox.com)
| H2S | 0 | 0 | 22.2 | 0
| Non-combustibles | 0 | 0 | 0 | 0
|  |  | 0 |  | 0
|  |  | 0 |  | 0
|  |  | 0 | 0 | 0
|  |  |  | Total Heat Release Rate (MJ/s) | 164.8224
|  |  |  | Total Heating Value (MJ/m3) | 11.0069
|  |  |  | Total Heat Release Rate (cal/s) | 39431196.7732
|  |  |  | Buoyancy Flux (m4/s3) | 1094.2157
ADDITIONAL NUMBERS FOR INPUT INTO ISC3 MODEL OR SCREEN3 AS POINT SOURCE OPTION
| Equivalent Stack temperature (K): |  |  | 1273
| Actual Exit Velocity (m/s): |  |  | 5.7625
| Effective Stack Height (m) |  |  | 29.4884
| Equivalent Stack Diameter (m): |  |  | 9.9821
| Emission Rate of SO2 (g/s): |  |  | 0
Emissiosn Data from USEPA AP-42
13.5_industrial_flares.pdf
|  | lb/million BTU | g/MJ
| Total hydrocarbons | 0.14 | 0.060189
| Carbon monoxide | 0.37 | 0.15907
| Nitrogen oxides | 0.068 | 0.029235
| Soot | 0 - 274
| 1millionBTU = | 1055.056 | MJ
| 1 lb = | 453.592 | grams
| Soot in concentration values: | micrograms per liter (μg/L) | g/m3 | g/s
| nonsmoking flares | 0 | 0 | 0
| lightly smoking flares | 40 | 0.04 | 0.59898
| average smoking flares | 177 | 0.177 | 2.6505
| heavily smoking flares | 274 | 0.274 | 4.103
Flare Location
| Zone | 30 U
| Easting | 692194
| Northing | 5966314

## mass to volume conversion H2
Calculation of volume flow rate from mass emission rate for a gas turbine operating on conventional fuels
Input Data | Mass emission | kg/s | 0.46837
| Emission Temperature | Celsius | 0
| Site Altitude | m | 0
Output data | Total Volume Flow | Am3/s | 4.2849 | at actual temp, wet, actual oxygen
| Total Volume Flow | Nm3/s | 14.9744 | Normalised to 15% O2, 273K, dry
Calculate volume | Exhaust gas composition (approximate) |  | upper | Source
| Hydrogen (H2) | % by volume | 96.8%
| CH4 | % by volume | 3.203%
| Carbon dioxide (CO2) | % by volume
| Water vapour (H2O) | % by volume
| Total | % by volume | 100%
| 1 litre of gas contains |  |  |  | Section | Description | Gas | Peak Depressurisation Rate (kg/h) | Flare System | Depressurisation Time (min) | vol from B&V report Am3? | kg based on B&V report Vol
| Hydrogen (H2) | g of gas | 0.086426 |  | 1 | Electrolyser train 1/2 | H2 | 1591 | LP | 5 |  | 0
| CH4 | g of gas | 0.022881 |  | 2 | LP Buffer tank | H2 | 1591 | LP | 5 | 100 | 3.87
| Carbon dioxide (CO2) | g of gas | 0 |  | 3 | LP Comp | H2 | 682.5 | HP | 15 | 48.4 | 83.38
| Water vapour (H2O) | g of gas | 0 |  | 4 | Deoxo & Dehydration | H2 | 1275 | HP | 15 | 96.6 | 166.41
| Therefore, 1 litre of gas weighs | g | 0.10931 |  | 5 | IP Buffer | H2 | 296.9 | HP | 15 | 33.7 | 76.25
[5 empty] | 6 | HP Comp | H2 | 8298 | HP | 15 | 49 | 871.66
| Molecular mass |  |  |  | 7 | Filter Separator | H2 | 3433 | HP | 15 | 20.1 | 357.56
| Hydrogen (H2) | g/mole | 2 |  | 8 | OCGT Feed System | H2 | 666.5 | HP | 15 | 23.8 | 74.87
| CH4 | g/mole | 16 |  | 9 | OCGT Mixing Skid | H3 | 85 | HP | 15 | 3.1 | 9.93
| Carbon dioxide (CO2) | g/mole | 44 |  | 10 | NG Supply to Mixing Skid | NG | 3758 | HP | 15 | 12.4 | 42.21
| Water vapour (H2O) | g/mole | 18
[5 empty] | Time (min) | Systems flared | Peak depressurisation rate (kg/hr) |  |  | total H2 | 374.7 | 1643.93
| Percentage by mass |  |  |  | 15 | LP Flare: 1,2 | LP Flare: 3,182.00 |  |  | Total NG | 12.4 | 42.21
| Hydrogen (H2) | %mass | 0.79067 |  |  | HP Flare: 3, 4, 5, 7, 8, 9 | HP Flare: 6,438.90 |  |  | NG, % | 3.203% | 2.503%
| CH4 | %mass | 0.20933 |  | 30 | HP Flare: 6 | HP Flare: 8,298.00 |  |  | H2, % | 96.8% | 97.5%
| Carbon dioxide (CO2) | %mass | 0 |  | 45 | HP Flare: 10 | HP Flare: 3,758.00
| Water vapour (H2O) | %mass | 0
| Mass emission | g/hr | 1686140
| Hydrogen (H2) | g/hr | 1333185.6046
| CH4 | g/hr | 352954.3954
| Carbon dioxide (CO2) | g/hr | 0
| Water vapour (H2O) | g/hr | 0
| Hydrogen (H2) | mol/hr | 666592.8023
| CH4 | mol/hr | 22059.6497
| Carbon dioxide (CO2) | mol/hr | 0
| Water vapour (H2O) | mol/hr | 0
| Hydrogen (H2) | litre/hr | 14931678.771 | 1 mol = 22.4 litres
| CH4 | litre/hr | 494136.1536
| Carbon dioxide (CO2) | litre/hr | 0
| Water vapour (H2O) | litre/hr | 0
| Vol flow | Alitre/hr | 15425814.9247
| Vol flow | Am3/s | 4.2849 | actual moisture, O2 and pressure, @273.15K
| Vol flow | Am3/s | 4.2849 | actual everything
Calculate Normalised |  |  | Method 1: Actual oxygen presented in WET gas
| Actual volume flow rate | Am3/s | 4.2849 | As measured in stack
| Actual emission temperature | Celsius | 0 | As measured in stack
| Actual flue gas oxygen | %v/v | 3.203% | As measured in stack WET gas basis
| Actual flue gas moisture | %v/v | 0% | As measured in stack
| Emission temperature - normalised | Celsius | 0
| Moisture - normalised | %v/v | 0
| Oxygen - normalised | %v/v | 15 | In dry gas
| Site altitude (above sea level) | m | 0
| Normalised volume flow rate | Nm3/s | 14.9744 | 101.3kPa; 273K; ref O2 (in dry gas); 0% moisture
Calculation of correction factors
| Correct for temperature |  | 1
| Corerct for moisture |  | 1
Correct for oxygen
| Correct for oxygen (dry) |  | 3.4947
| atmospheric pressure at site |  | 101.325
| Correct for atmosperic pressure (altitude) |  | 1