## Front Cover
Aldbrough Hydrogen Pathfinder H1 Assessment to Water Workbook
Project Number | 653313
Date | 2025-10-24
Version | V1.6
Author | Taraka Rhodes, Liam Fernand
Client Name | SSE Hornsea Limited
Version | Revision | Author | Reviewed by | Name | Date | Comments
V1 | 1 | Taraka Rhodes, Liam Fernand | Kate Riley | Russell Cullen | 2024-03-09 | Draft for Client Review
V1 | 2 | Taraka Rhodes, Liam Fernand | Kate Riley | Russell Cullen | 13/11/2024 | Draft for Client Review
V1 | 3 | Taraka Rhodes, Liam Fernand | Kate Riley | Russell Cullen | 2025-01-31 | Final for Client Review
V1 | 4 | Taraka Rhodes, Liam Fernand | Kate Riley | Russell Cullen | 2025-03-20 | Final for Client Review
V1 | 5 | Taraka Rhodes, Liam Fernand | Kate Riley | Russell Cullen | 2025-04-10 | Final for Issue
V1 | 6 | Taraka Rhodes | Kate Riley | Russell Cullen | 2025-10-24 | Final for Issue
This document has been prepared by Environmental Resources Management Limited (ERM) for SSE Hornsea Limited. The document provides the H1 screening assessment to water calculations for the proposed new Aldbrough Hydrogen Pathfinder (AHP) Project. The following document is intended to be used by SSE Hornsea Limited to support the new bespoke permit application.

## Contents
CONTENTS
Sheet | Description
1. Sample Analysis | This tab provides an summary of borehole samples used to derive concentrations of substances used in the H1 assessment. Those substances that had associated Environmental Quality Standards (EQS) were taken through to the H1 screening assessment in Tab 4 & 5.
2. Ammonia Calculations | This tab provides calculations of ammonia concentrations that were separately used in the H1 screening assessment in Tab 4 & 5.
3. Background | This tab provides a summary of background concentrations used in the H1 screening assessment in Tab 4 & 5
4. H1 Test_TRaC Riverine Phase 1 | H1 screening methodology and results for Phase 1 (cavern + demin plant discharge)
5. H1 Test_TRaC Riverine Phase 2 | H1 screening methodology and results for Phase 2 (demin plant discharge only)

## 1.Sample Analysis
Parameters with EQSs that have been taken forward to H1 assessment
Sample result equal to or less than limit of detection
|  |  | red text | Added/updated since previous version | [5 empty] | *increase in concentration by factor of 2.7
Parameter | Units | Method | Sample Analysis |  |  |  |  | Stream A (Cavern dewatering) Concentration (ug/l) |  | Steam B (1) (Demin plant effluent) Concentration (ug/l) |  | Phase 1 Concentration (Stream A + Stream B) (ug/l) |  | Coastal Waters EQS (ug/l) |  | Comments
|  |  | 2019-09-05 | 2019-09-09 | 2019-09-16 | Average | Max | Average | Max | Average | Max | Average | Max | AA | MAC
|  |  | 1308876 | 1311550 | 1317266 | (ug/l) | (ug/l) | (ug/l) | (ug/l) | (ug/l) | (ug/l) | (ug/l) | (ug/l) | (ug/l) | (ug/l)
Aluminium (dissolved) | mg/l |  | 4.5 | 3.2 | 1 | 2900 | 4500 | 2900 | 4500 | 7830 | 12150 | 3020.2439 | 4686.5854 | N/A | N/A
Ammonia (unionised) | mg/l | Calc* | NA | NA | NA | NA | NA | See Tab 2 | See Tab 2 | See Tab 2 | See Tab 2 | See Tab 2 | See Tab 2 | 21 | N/A | Derived property dependant upon on the discharge temperature, pH and salinity. See Tab 2 for values calculated and used in H1 assessment instead of these sample results.
Ammonium | mg/l |  | 1.3 | 1.2 | 1.4 | 1300 | 1400 | 1300 | 1400 | 3510 | 3780 | 1353.9024 | 1458.0488 | N/A | N/A
Arsenic (dissolved) | ug/l | CBA118* | 1.02 | 0.7 | 0.54 | 0.75333 | 1.02 | 0.75333 | 1.02 | 2.034 | 2.754 | 0.78457 | 1.0623 | 25 | N/A
Barium (dissolved) | mg/l |  | 0.01 | 0.01 | 0.01 | 10 | 10 | 10 | 10 | 27 | 27 | 10.4146 | 10.4146 | N/A | N/A
Bicarbonate | mg/l | APIRP45-81 | 10 | 10 | 10 | 10000 | 10000 | 10000 | 10000 | 27000 | 27000 | 10414.6341 | 10414.6341 | N/A | N/A
Boron (dissolved) | mg/l |  | 0.5 | 0.51 | 0.52 | 510 | 520 | 510 | 520 | 1377 | 1404 | 531.1463 | 541.561 | 7000 | N/A
Cadmium (dissolved) | ug/l |  | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.054 | 0.054 | 0.020829 | 0.020829 | 0.2 | N/A
Calcium (dissolved) | mg/l |  | 150 | 190 | 140 | 160000 | 190000 | 160000 | 190000 | 432000 | 513000 | 166634.1463 | 197878.0488 | N/A | N/A
Chloride | mg/l | CBA56 | 820 | 830 | 840 | 830000 | 840000 | 830000 | 840000 | 2241000 | 2268000 | 864414.6341 | 874829.2683 | N/A | N/A
Chromium (dissolved) | ug/l |  | 0.2 | 0.3 | 0.2 | 0.23333 | 0.3 | 0.23333 | 0.3 | 0.63 | 0.81 | 0.24301 | 0.31244 | N/A | N/A | Not taken through to modelling as this is Cr Dissolved whereas EQS is for Cr VI
Conductivity | mS.cm | CML-LAB-TP-18* | 3.8 | 3.9 | 3.9 | 3.8667 | 3.9 | 3.8667 | 3.9 | 10.44 | 10.53 | 4.027 | 4.0617 | N/A | N/A
Copper (dissolved) | ug/l | LOD | 8.1 | 6.4 | 2.4 | 5.6333 | 8.1 | 5.6333 | 8.1 | 15.21 | 21.87 | 5.8669 | 8.4359 | 3.76 | N/A
Dissolved Organic Carbon | mg/l | Combustion and NDIR Detection*^ | 2.61 | 1.86 | 1.85 | 2106.6667 | 2610 | 2106.6667 | 2610 | 5688 | 7047 | 2194.0163 | 2718.2195 | N/A | N/A
Iron (dissolved) | mg/l |  | 1 | 0.09 | 0.02 | 370 | 1000 | 370 | 1000 | 999 | 2700 | 385.3415 | 1041.4634 | 1000 | N/A
Lead (dissolved) | ug/l |  | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.54 | 0.54 | 0.20829 | 0.20829 | 1.3 | 14
Lithium (dissolved) | mg/l |  | 0.02 | 0.02 | 0.02 | 20 | 20 | 20 | 20 | 54 | 54 | 20.8293 | 20.8293 | N/A | N/A
Magnesium (dissolved) | mg/l |  | 82 | 95 | 86 | 87666.6667 | 95000 | 87666.6667 | 95000 | 236700 | 256500 | 91301.626 | 98939.0244 | N/A | N/A
Manganese (dissolved) | mg/l |  | 0.02 | 0.03 | 0.02 | 23.3333 | 30 | 23.3333 | 30 | 63 | 81 | 24.3008 | 31.2439 | N/A | N/A
Mercury (dissolved) | ug/l |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.135 | 0.135 | 0.052073 | 0.052073 | N/A | 0.07 | Not taken through to modelling as not expected in background
Molybdenum (dissolved) | ug/l |  | 1.4 | 1.1 | 1.2 | 1.2333 | 1.4 | 1.2333 | 1.4 | 3.33 | 3.78 | 1.2845 | 1.458 | N/A | N/A
Nickel (dissolved) | ug/l |  | 0.7 | 1.4 | 1.1 | 1.0667 | 1.4 | 1.0667 | 1.4 | 2.88 | 3.78 | 1.1109 | 1.458 | 8.6 | 34
Nitrate | mg/l |  | 0.51 | 0.43 | 0.48 | 473.3333 | 510 | 473.3333 | 510 | 1278 | 1377 | 492.9593 | 531.1463 | N/A | N/A
pH |  | ASTMD1293B | 7.2 | 7.2 | 7.4 | 7.2667 | 7.4 | 7.2667 | 7.4 | 7.2667 | 7.4 | 7.2667 | 7.4 | N/A | N/A | Median pH taken, as there is a significant outlier. In addition the demin process shouldn't affect pH (or only slightly).
Potassium (dissolved) | mg/l |  | 32 | 32 | 30 | 31333.3333 | 32000 | 31333.3333 | 32000 | 84600 | 86400 | 32632.5203 | 33326.8293 | N/A | N/A
Sodium (dissolved) | mg/l | CBA67 | 550 | 550 | 570 | 556666.6667 | 570000 | 556666.6667 | 570000 | 1503000 | 1539000 | 579747.9675 | 593634.1463 | N/A | N/A
Strontium (dissolved) | mg/l |  | 6.9 | 8.3 | 10 | 8400 | 10000 | 8400 | 10000 | 22680 | 27000 | 8748.2927 | 10414.6341 | N/A | N/A
Sulphate | mg/l |  | 640 | 575 | 703 | 639333.3333 | 703000 | 639333.3333 | 703000 | 1726200 | 1898100 | 665842.2764 | 732148.7805 | N/A | N/A
Total Cyanide | ug/l | HACH*^ | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 27 | 27 | 10.4146 | 10.4146 | 1 | 5 | Not taken through to modelling as not expected in background
Total Organic Carbon | mg/l |  | 2.45 | 3 | 2.37 | 2606.6667 | 3000 | 2606.6667 | 3000 | 7038 | 8100 | 2714.748 | 3124.3902 | N/A | N/A
Selenium | ug/l |  | 10 | 16 | 16 | 14 | 16 | 14 | 16 | 37.8 | 43.2 | 14.5805 | 16.6634 | N/A | N/A
Tin | ug/l |  | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.54 | 0.54 | 0.20829 | 0.20829 | 10 | N/A
Zinc | ug/l |  | 44 | 62 | 51 | 52.3333 | 62 | 52.3333 | 62 | 141.3 | 167.4 | 54.5033 | 64.5707 | 6.8 | N/A
Flowrate | m3/d | [6 empty] | 3744 |  | 93.6 |  | 3837.6
| m3/s | [6 empty] | 0.043333 |  | 0.0010833 |  | 0.044417
Notes:
1. Demin plant effluent assumed to increase concentrations by a factor of 2.7, based on Demin plant feed rate of 10.5 m3/h and reject rate 3.9 m3/h.
2. Substances with EQS are taken forward to H1 assessment

## 2.Ammonia Calculations
1.Input Values used in Calculations
|  | Stream A + B conditions (Cavern dewatering + demin plant discharge) | Steam B conditions (Demin plant effluent) | Sea water conditions at Aldbrough
| Temperature (oC) | 26 | 10 | 15.9
| Average pH | 7.2667 | 7.6 | 8.1
| Average salinity (ppt) | 111 | 5.4 | 34.25
| Ammonium, ug/l | 1353.9024 | 3510
Calculations in Section 3 below have been performed for the un-ionised ammonia concentration in the fresh water as it is discharged and also considering the discharge into the sea water.
2. Methodology
The equation provide by Florida Dept has been used to calculate un-ionised ammonia concentrations (see screenshot below of methodology)
| Available online at: | https://floridadep.gov/sites/default/files/5-Unionized-Ammonia-SOP_1.pdf
3. Results
FLORIDA DEPARTMENT OF ENVIRONMENTAL PROTECTION CHEMISTRY LABORATORY METHODS MANUAL, TALLAHASSEE CALCULATION OF UN-IONIZED AMMONIA IN FRESH WATER STORET Parameter Code 006
|  |  |  | Stream A + B conditions (Cavern dewatering + demin plant discharge) | At point of discharge | Steam B conditions (Demin plant effluent) | At point of discharge
|  | Temperature, T | oC | 26 | 15.9 | 10 | 15.9
|  | Salinity, S | ppt | 111 | 34.25 | 5.4 | 34.25
|  | pH | - | 7.2667 | 8.1 | 7.6 | 8.1
|  | Molal ionic strength, I |  | 2.5579 | 0.71341 | 0.10856 | 0.71341
|  | Ionisation constant , pKa,s |  | 9.5919 | 9.6418 | 9.7479 | 9.6418
|  | Fraction of ammonia which is unionised, fs = | - | 0.0047072 | 0.027919 | 0.0070629 | 0.027919
|  | Ammonium conc | ug/l | 1353.9024 | 1353.9024 | 3510 | 3510
|  | Unionised Ammonia conc | ug/l | 6.3731 | 37.8002 | 24.7907 | 97.9973
|  | Max ammonium conc | ug/l | 1458.0488 | 1458.0488 | 3780 | 3780
|  | Max ammonia conc | ug/l | 6.8633 | 40.7079 | 26.6977 | 105.5356

## 3.Background Concentrations
| Average | Maximum | Source | Where the background is below the detection limit, 1/2 of the detection limit has been used
Ammonia | 11 | 11 | Table 1 - EA Data Set
Arsenic | 1.75 | 2 | Table 2 - 2023
Boron | 3500 | 3500 | 50% of EQS
Cadmium | 0.1 | 0.1 | Table 2 - 2023 1/2 Detection limit
Chromium | 0.5 | 0.5 | Table 2 - 2023 1/2 Detection limit
Copper - dissolved | 0.5 | 0.5 | Table 2 - 2023 1/2 Detection limit
Iron | 100 | 100 | Table 1 - EA Data Set
Lead | 0.5 | 0.5 | Table 2 - 2023 1/2 Detection limit
Mercury | 0.01 | 0.01 | Table 1 - EA Data Set
Nickel | 0.5 | 0.5 | Table 2 - 2023 1/2 Detection limit
Cyanide | 0.5 | 2.5 | 50% of EQS
Zinc | 3.4 | 4 | Table 2 - 2023
Tin | 5 | n/a | 50% of EQS
Table 1 - EA Water Quality Archive
Table 2 - Summary Data from 12 stations at Aldbrough Oct 2023
Parameter | Average Concentration | Maximum Concentration | Units
THC | 5.08 | 9.66 | μg.l-1
Total Alkanes | 0.051 | 0.51 | μg.l-1
Total PAHs | 0.14 | 0.48 | μg.l-1
Dissolved Heavy and Trace Metals | - | <0.0001
Arsenic | 0.00175 | 0.002 | mg.l-1
Cadmium | <0.0001 | <0.0001 | mg.l-1
Chromium | <0.001 | <0.001 | mg.l-1
Copper | <0.001 | <0.001 | mg.l-1
Lead | <0.001 | <0.001 | mg.l-1
Mercury | <0.0001 | <0.0001 | mg.l-1
Nickel | <0.001 | <0.001 | mg.l-1
Zinc | 0.0034 | 0.004 | mg.l-1
Aluminium | 0.12 | 0.25 | mg.l-1
Barium | <0.01 | <0.0001 | mg.l-1
Lithium | 0.146 | 0.26 | mg.l-1
Silicon | 0.233 | 0.4 | mg.l-1
Sulphur | 2825 | 2930 | mg.l-1
Nutrients, Minerals and Suspended Solids
Nitrate (NO3) | <0.2 | <0.2 | mg.l-1
Nitrite (NO2) | <0.01 | <0.01 | mg.l-1
Orthophosphate (PO4) | 0.068 | 0.12 | mg.l-1
Total Nitrogen (N) | <1 | <0.01 | mg.l-1
Total Suspended Solids (TSS) | 113 | 527 | mg.l-1
pH | 8.1 | 8.11

## 4.H1 Test_TRaC Riverine Phase 1
H1 - Freshwater Rivers
PHASE 1 - STREAM A (Cavern dewatering) + STREAM B (demin plant effluent) | [14 empty] | H1 Screening Tests
Input Data | [14 empty] | Test 1 |  | Test 3 |  | Test 4 |  |  |  | Test 5 |  |  | Significance Load Test
Substance | Release Concentration (ug/l) (AA) | Release Concentration (ug/l) (MAC) | EFR (m3/s) (average) | EFR (m3/s) (max) | EFR x RC (Average) | EFR x RC (Max) | Average BC (ug/l) | Max BC (ug/l) | EVF (AA) | EVF (Max) | Water depth (m) | Estuaries & Coastal Waters EQS (ug/l) (Long term/AA) | Estuaries & Coastal Waters EQS (ug/l) (Short term/MAC) | Comments/ Source (EQS or other) | Substance < AA EQS?) | Substance < MAC EQS? | Restricted dilution? | Modelling required? | Is discharge<50m offshore from where the sea bed is at chart datum? | Is the sea bed at the discharge location less than 1m below chart datum? | Modelling required? |  | Is depth <3.5m? | Where depth >3.5m, is AA EVF <=3.5 m3/s? | Where depth >3.5, is MAX EVF <=3.5 m3/s? | SL | Step 1+2 mg/day ((RC x AA EFR)/1000) | Step 3 kg/day (Step 2/1000) | Step 4 kg/year (Step 3*365) | Results <SL?
Unionised Ammonia | 37.8002 | 40.7079 | 0.044421 | 0.044421 | 1.6791 | 1.8083 | 11 | N/A | 0.16791 | N/A | 9.5 | 21 | N/A | EQS | Fail | N/A | No | No model | No | No | No Model | No model | No | Yes | N/A
Arsenic | 0.78457 | 1.0623 | 0.044421 | 0.044421 | 0.034852 | 0.047188 | 1.75 | N/A | 0.001499 | N/A | 9.5 | 25 | N/A | EQS | Pass | N/A | No | No model | No | No | No Model | No model | No | Yes | N/A
Boron | 531.1463 | 541.561 | 0.044421 | 0.044421 | 23.5942 | 24.0568 | 3500 | N/A | 0.0067412 | N/A | 9.5 | 7000 | N/A | EQS | Pass | N/A | No | No model | No | No | No Model | No model | No | Yes | N/A
Cadmium | 0.020829 | 0.020829 | 0.044421 | 0.044421 | 0.00092526 | 0.00092526 | 0.1 | N/A | 0.0092526 | N/A | 9.5 | 0.2 | N/A | EQS | Pass | N/A | No | No model | No | No | No Model | No model | No | Yes | N/A | 5 | 9.2526e-07 | 9.2526e-10 | 3.3772e-07 | Yes
Copper - dissolved | 5.8669 | 8.4359 | 0.044421 | 0.044421 | 0.26062 | 0.37473 | 0.5 | N/A | 0.079943 | N/A | 9.5 | 3.76 | N/A | EQS | Fail | N/A | No | No model | No | No | No Model | No model | No | Yes | N/A
Iron | 385.3415 | 1041.4634 | 0.044421 | 0.044421 | 17.1174 | 46.2632 | 100 | N/A | 0.019019 | N/A | 9.5 | 1000 | N/A | EQS | Pass | N/A | No | No model | No | No | No Model | No model | No | Yes | N/A
Lead | 0.20829 | 0.20829 | 0.044421 | 0.044421 | 0.0092526 | 0.0092526 | 0.5 | 0.5 | 0.011566 | 0.00068538 | 9.5 | 1.3 | 14 | EQS | Pass | Pass | No | No model | No | No | No Model | No model | No | Yes | Yes
Nickel | 1.1109 | 1.458 | 0.044421 | 0.044421 | 0.049347 | 0.064768 | 0.5 | 0.5 | 0.0060923 | 0.0019334 | 9.5 | 8.6 | 34 | EQS | Pass | Pass | No | No model | No | No | No Model | No model | No | Yes | Yes
Zinc | 54.5033 | 64.5707 | 0.044421 | 0.044421 | 2.4211 | 2.8683 | 3.4 | N/A | 0.71209 | N/A | 9.5 | 6.8 | N/A | EQS | Fail | N/A | No | No model | No | No | No Model | No model | No | Yes | N/A
Tin | 0.20829 | 0.20829 | 0.044421 | 0.044421 | 0.0092526 | 0.0092526 | 5 | N/A | 0.0018505 | N/A | 9.5 | 10 | N/A | EQS | Pass | N/A | No | No model | No | No | No Model | No model | No | Yes | N/A
NOTE 1 - Ammonia, Copper and Zinc do not screen out at Test 1 and therefore require modelling due to the discharge being in a protected area. Cyanide has not been considered any further as detailed in the H1 report.
|  |  |  | Flow rate | 3838 | m3/day | [9 empty] | N/A (screened out or no EQS)
[5 empty] | 0.044421 | m3/s
Abbreviations
|  |  |  | AA | Annual Average
|  |  |  | BC | Background Concentration
|  |  |  | EFR | Effluent Flow Rate
|  |  |  | EQS | Environmental Quality Standard
|  |  |  | EVF | Effective Volume Flux
|  |  |  | MAC | Maximum Allowable Concentration
|  |  |  | m | Metres
|  |  |  | m3 | Cubic Metres
|  |  |  | RC | Release Concentration
|  |  |  | RFR | River Flow Rate
|  |  |  | s | Second
|  |  |  | SL | Significance Load
|  |  |  | ug/l | Micrograms per litre

## 5.H1 Test_TRaC Riverine Phase 2
H1 - Freshwater Rivers
PHASE 2 - STREAM B ONLY | [14 empty] | H1 Screening Tests
Input Data | [14 empty] | Test 1 |  | Test 3 |  | Test 4 |  |  |  | Test 5 |  |  | Significance Load Test
Substance | Release Concentration (ug/l) (AA) | Release Concentration (ug/l) (MAC) | EFR (m3/s) (average) | EFR (m3/s) (max) | EFR x RC (Average) | EFR x RC (Max) | Average BC (ug/l) | Max BC (ug/l) | EVF (AA) | EVF (Max) | Water depth (m) | Estuaries & Coastal Waters EQS (ug/l) (Long term/AA) | Estuaries & Coastal Waters EQS (ug/l) (Short term/MAC) | Comments/ Source (EQS or other) | Substance < AA EQS?) | Substance < MAC EQS? | Restricted dilution? If Yes = Model | Modelling required (No = False)? | Is discharge<50m offshore from where the sea bed is at chart datum? | Is the sea bed at the discharge location less than 1m below chart datum? | Modelling required (No = False)? |  | Is depth <3.5m? | Where depth >3.5m, is AA EVF <=3.5 m3/s? | Where depth >3.5, is MAX EVF <=3.5 m3/s? | SL | Step 1+2 mg/day ((RC x AA EFR)/1000) | Step 3 kg/day (Step 2/1000) | Step 4 kg/year (Step 3*365) | Results <SL?
Unionised Ammonia | 97.9973 | 105.5356 | 0.0010833 | 0.0010833 | 0.10616 | 0.11433 | 11 | N/A | 0.010616 | N/A | 9.5 | 21 | N/A | EQS | Fail | N/A | No | No model | No | No | No Model | No model | No | Yes | N/A
Arsenic | 2.034 | 2.754 | 0.0010833 | 0.0010833 | 0.0022035 | 0.0029835 | 1.75 | N/A | 9.4774e-05 | N/A | 9.5 | 25 | N/A | EQS | Pass | N/A | No | No model | No | No | No Model | No model | No | Yes | N/A
Boron | 1377 | 1404 | 0.0010833 | 0.0010833 | 1.4917 | 1.521 | 3500 | N/A | 0.00042621 | N/A | 9.5 | 7000 | N/A | EQS | Pass | N/A | No | No model | No | No | No Model | No model | No | Yes | N/A
Cadmium | 0.054 | 0.054 | 0.0010833 | 0.0010833 | 5.85e-05 | 5.85e-05 | 0.1 | N/A | 0.000585 | N/A | 9.5 | 0.2 | N/A | EQS | Pass | N/A | No | No model | No | No | No Model | No model | No | Yes | N/A | 5 | 5.85e-08 | 5.85e-11 | 2.1353e-08 | Yes
Copper - dissolved | 15.21 | 21.87 | 0.0010833 | 0.0010833 | 0.016477 | 0.023692 | 0.5 | N/A | 0.0050544 | N/A | 9.5 | 3.76 | N/A | EQS | Fail | N/A | No | No model | No | No | No Model | No model | No | Yes | N/A
Iron | 999 | 2700 | 0.0010833 | 0.0010833 | 1.0823 | 2.925 | 100 | N/A | 0.0012025 | N/A | 9.5 | 1000 | N/A | EQS | Pass | N/A | No | No model | No | No | No Model | No model | No | Yes | N/A
Lead | 0.54 | 0.54 | 0.0010833 | 0.0010833 | 0.000585 | 0.000585 | 0.5 | 1 | 0.00073125 | 4.5e-05 | 9.5 | 1.3 | 14 | EQS | Pass | Pass | No | No model | No | No | No Model | No model | No | Yes | Yes
Nickel | 2.88 | 3.78 | 0.0010833 | 0.0010833 | 0.00312 | 0.004095 | 0.5 | 0.5 | 0.00038519 | 0.00012224 | 9.5 | 8.6 | 34 | EQS | Pass | Pass | No | No model | No | No | No Model | No model | No | Yes | Yes
Zinc | 141.3 | 167.4 | 0.0010833 | 0.0010833 | 0.15308 | 0.18135 | 3.4 | N/A | 0.045022 | N/A | 9.5 | 6.8 | N/A | EQS | Fail | N/A | No | No model | No | No | No Model | No model | No | Yes | N/A
Tin | 0.54 | 0.54 | 0.0010833 | 0.0010833 | 0.000585 | 0.000585 | 5 | N/A | 0.000117 | N/A | 9.5 | 10 | N/A | EQS | Pass | N/A | No | No model | No | No | No Model | No model | No | Yes | N/A
NOTE 1 - Ammonia, Copper and Zinc do not screen out at Test 1 and therefore require modelling due to the discharge being in a protected area. Chromium, Mercury and Cyanide has not been considered any further as detailed in the H1 report.
|  |  |  | Flow rate | 93.6 | m3/day | [9 empty] | N/A (screened out or no EQS)
[5 empty] | 0.0010833 | m3/s
Abbreviations
|  |  |  | AA | Annual Average
|  |  |  | BC | Background Concentration
|  |  |  | EFR | Effluent Flow Rate
|  |  |  | EQS | Environmental Quality Standard
|  |  |  | EVF | Effective Volume Flux
|  |  |  | MAC | Maximum Allowable Concentration
|  |  |  | m | Metres
|  |  |  | m3 | Cubic Metres
|  |  |  | RC | Release Concentration
|  |  |  | RFR | River Flow Rate
|  |  |  | s | Second
|  |  |  | SL | Significance Load
|  |  |  | ug/l | Micrograms per litre