## Trial Results
C 2620245 Perenco UK: Dimlington Terminal
Laboratory Number |  |  | 23754909 | 23754910 | 23754908 | 23789209 | 23789210 | 23789208 | 23858607 | 23858608 | 23858609 | 23858610 | 23858611 | 23858612 | 23916509 | 23916510 | 23916511 | 23916512 | 23916513 | 23916514 | 24093289 | 24093290 | 24093291 | 24093292 | 24093293 | 24093294
Customer Sample Ref. |  |  | Day 1 Inlet 1st filter | Day 1 Outlet 1st filter | Day 1 Outlet 2nd filter | Day 10 Inlet 1st filter | Day 10 Outlet 1 st filter | Day 10 Outlet 2nd filter | Day 20 Inlet 1st filter | Day 20 Outlet 1st filter | Day 20 Outlet 2nd filter | Day 30 Inlet 1st filter | Day 30 Outlet 1st filter | Day 30 Outlet 2nd filter | Day 40 Inlet 1st Filter | Day 40 Outlet 1st Filter | Day 40 Outlet 2nd Filter | Day 50 Inlet 1st Filter | Day 50 Outlet 1st Filter | Day 50 Outlet 2nd Filter | Day 60 Inlet 1st Filter | Day 60 Outlet 1st Filter | Day 60 Outlet 2nd Filter | Day 70 Inlet 1st Filter | Day 70 Outlet 1st Filter | Day 70 Outlet 2nd Filter
Sample Matrix |  |  | Not Specified | Not Specified | Not Specified | Surface Water | Surface Water | Surface Water | Not Specified | Not Specified | Not Specified | Not Specified | Not Specified | Not Specified | Not Specified | Not Specified | Not Specified | Not Specified | Not Specified | Not Specified | Not Specified | Not Specified | Not Specified | Not Specified | Not Specified | Not Specified
Sample Date |  |  | 2024-02-18 | 2024-02-18 | 2024-02-18 | 2024-02-28 | 2024-02-28 | 2024-02-28 | 2024-03-08 | 2024-03-08 | 2024-03-08 | 2024-03-18 | 2024-03-18 | 2024-03-18 | 2024-03-28 | 2024-03-28 | 2024-03-28 | 2024-04-07 | 2024-04-07 | 2024-04-07 | 2024-04-17 | 2024-04-17 | 2024-04-17 | 2024-04-27 | 2024-04-27 | 2024-04-27
Sample Time |  |  | 21:00 | 21:00 | 21:00 | 21:00 | 21:00 | 21:00 | 21:00 | 21:00 | 21:00 | 21:00 | 21:00 | 21:00 | 21:00 | 21:00 | 21:00 | 21:00 | 21:00 | 21:00 | 21:00 | 21:00 | 21:00 | 21:00 | 21:00 | 21:00
Point Code
Analyte | Method | Units
3:3 FTCA (356-02-5) | TM434 | ng/l | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | 6.29 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2
4:2 FTSA (757124-72-4) | TM434 | ng/l | 1.2 | <1 | <1 | 1.05 | <1 | <1 | 1.24 | <1 | <1 | 1.25 | <1 | <1 | 1.22 | <1 | <1 | 1.31 | <1 | <1 | 1.21 | <1 | <1 | 1.3 | <1 | <1
5:3 FTCA (914637-49-3) | TM434 | ng/l | 78 | <5 | <5 | 27.2 | <5 | <5 | 17.9 | <5 | <5 | 66.1 | <5 | <5 | 13.7 | <5 | <5 | 44.1 | <5 | <5 | 60.4 | <5 | <5 | 21.2 | <5 | <5
6:2 Cl-PFESA (756426-58-1) | TM434 | ng/l | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1
6:2 FTSA (27619-97-2) | TM434 | ng/l | 3670 | <1 | <1 | 2590 | 29.7 | 28.5 | 3380 | 2.26 | 1.41 | 3790 | 1.05 | <1 | 2040 | 1.9 | <1 | 2130 | 60.1 | 1.23 | 4910 | <1 | <1 | 5560 | <1 | <1
7:3 FTCA (812-70-4) | TM434 | ng/l | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5
8:2 Cl-PFESA (763051-92-9) | TM434 | ng/l | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2
8:2 FTSA (39108-34-4) | TM434 | ng/l | 54.6 | <2 | <2 | 38 | <2 | <2 | 30.3 | <2 | <2 | 33.1 | <2 | <2 | 29 | <2 | <2 | 33.5 | <2 | <2 | 22.6 | <2 | <2 | 24.7 | <2 | <2
DONA (919005-14-4) | TM434 | ng/l | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1
EtFOSA (4151-50-2) | TM434 | ng/l | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1
EtFOSE (1691-99-2) | TM434 | ng/l | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10
FBSA (30334-69-1) | TM434 | ng/l | 12 | <1 | <1 | 7.78 | <1 | <1 | 10.7 | <1 | <1 | 13 | <1 | <1 | 9.86 | <1 | <1 | 13.1 | <1 | <1 | 22.3 | <1 | <1 | 20.9 | <1 | <1
FHxSA (41997-13-1) | TM434 | ng/l | 122 | <1 | <1 | 89 | 1.74 | 1.7 | 87.4 | 1.17 | <1 | 99.5 | <1 | <1 | 102 | <1 | <1 | 118 | 1.11 | <1 | 135 | <1 | <1 | 134 | <1 | <1
FOSA (754-91-6) | TM434 | ng/l | 6.94 | <1 | <1 | 4.88 | <1 | <1 | 6.97 | <1 | <1 | 7.29 | <1 | <1 | 7.67 | <1 | <1 | 8.79 | <1 | <1 | 6.76 | <1 | <1 | 7.05 | <1 | <1
HFPO-DA (Gen X) (13252-13-6) | TM434 | ng/l | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2
HFPO-TA (13252-14-7) | TM434 | ng/l | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5
MeFOSA (31506-32-8) | TM434 | ng/l | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1
MeFOSE (24448-09-7) | TM434 | ng/l | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10
NEtFOSAA (2991-50-6) | TM434 | ng/l | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2
NFDHA (151772-58-6) | TM434 | ng/l | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1
NMeFOSAA (2355-31-9) | TM434 | ng/l | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2
PFBA (375-22-4) | TM434 | ng/l | 117 | <2 | <2 | 100 | <2 | <2 | 95.7 | 2.14 | <2 | 122 | <2 | <2 | 170 | <2 | <2 | 196 | 5.25 | <2 | 267 | 4.14 | <2 | 318 | 5.29 | <2
PFBS (375-73-5) | TM434 | ng/l | 14.2 | <1 | <1 | 9.56 | <1 | <1 | 10.4 | <1 | 1.13 | 12 | <1 | <1 | 13.4 | <1 | <1 | 15.3 | <1 | <1 | 16.5 | <1 | <1 | 16.8 | <1 | <1
PFDA (335-76-2) | TM434 | ng/l | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2
PFDoA (307-55-1) | TM434 | ng/l | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2
PFDoS (79780-39-5) | TM434 | ng/l | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | 3.96 | <2 | <2 | <2 | <2 | <2 | 5.13 | <2 | <2
PFDS (335-77-3) | TM434 | ng/l | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | 2.54 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2
PFecHS (133201-07-7) | TM434 | ng/l | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1
PFEESA (113507-82-7) | TM434 | ng/l | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1
PFHpA (375-85-9) | TM434 | ng/l | 182 | <1 | <1 | 157 | 2.61 | 2.56 | 177 | 1.03 | 1.16 | 214 | <1 | <1 | 256 | <1 | <1 | 280 | 5.25 | <1 | 427 | 1.6 | <1 | 544 | 1.37 | <1
PFHpS (375-92-8) | TM434 | ng/l | 17.2 | <1 | <1 | 11.9 | <1 | <1 | 9.93 | <1 | <1 | 12.1 | <1 | <1 | 9.44 | <1 | <1 | 9.01 | <1 | <1 | 12.8 | <1 | <1 | 12.4 | <1 | <1
PFHxA (307-24-4) | TM434 | ng/l | 429 | <1 | <1 | 358 | 5.13 | 4.78 | 443 | <1 | <1 | 517 | <1 | <1 | 621 | <1 | <1 | 690 | 13.2 | <1 | 913 | 6.21 | <1 | 981 | 4.8 | <1
PFHxDA (67905-19-5) | TM434 | ng/l | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1
PFHxS (355-46-4) | TM434 | ng/l | 242 | <1 | 1.13 | 178 | 1.23 | 1.24 | 183 | <1 | 1.05 | 195 | <1 | <1 | 195 | <1 | <1 | 241 | 2 | <1 | 243 | <1 | <1 | 279 | <1 | <1
PFMOBA (863090-89-5) | TM434 | ng/l | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1
PFMOPrA (377-73-1) | TM434 | ng/l | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1
PFNA (375-95-1) | TM434 | ng/l | 3.21 | <1 | <1 | 2.64 | <1 | <1 | 2.78 | <1 | <1 | 2.58 | <1 | <1 | 2.64 | <1 | <1 | 2.83 | <1 | <1 | 4.19 | <1 | <1 | 4.09 | <1 | <1
PFNS (68259-12-1) | TM434 | ng/l | 1.48 | <1 | <1 | 1.41 | <1 | <1 | 1.34 | <1 | <1 | 1.5 | <1 | <1 | <1 | <1 | <1 | 1.65 | <1 | <1 | 1.49 | <1 | <1 | 1.41 | <1 | <1
PFOA (335-67-1) | TM434 | ng/l | 28.6 | <1 | <1 | 20.4 | <1 | <1 | 20.7 | <1 | 1.19 | 23.9 | <1 | <1 | 25.9 | <1 | <1 | 29 | 1.1 | <1 | 35.6 | <1 | <1 | 37.1 | <1 | <1
PFODA (16517-11-6) | TM434 | ng/l | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1
PFPA (2706-90-3) | TM434 | ng/l | 509 | <1 | <1 | 510 | 5.75 | 5.68 | 599 | 1.49 | 1.25 | 730 | 1.14 | <1 | 807 | 1 | <1 | 935 | 16.4 | <1 | 1330 | 8.79 | <1 | 1450 | 7.28 | <1
PFPeS (2706-91-4) | TM434 | ng/l | 17.7 | <1 | <1 | 13.9 | <1 | <1 | 15.3 | <1 | <1 | 17.2 | <1 | <1 | 17.9 | <1 | <1 | 19.6 | <1 | <1 | 22.1 | <1 | <1 | 22 | <1 | <1
PFTeA (376-06-7) | TM434 | ng/l | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1
PFTrDA (72629-94-8) | TM434 | ng/l | <3 | <3 | <3 | <3 | <3 | <3 | <3 | <3 | <3 | <3 | <3 | <3 | <3 | <3 | <3 | <3 | <3 | <3 | <3 | <3 | <3 | <3 | <3 | <3
PFUnA (2058-94-8) | TM434 | ng/l | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2
PFUnDS (749786-16-1) | TM434 | ng/l | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2
Total PFOS (1763-23-1) | TM434 | ng/l | 1130 | <1 | 1.2 | 767 | 5.24 | 5.22 | 743 | 1.03 | 1.23 | 762 | 1.27 | <1 | 734 | 10.2 | <1 | 864 | 7.76 | <1 | 764 | <1 | <1 | 891 | <1 | <1
PFOA | GEO82 | ug/l | 0.0314 | <0.00013 | <0.00013 | 0.0229 | 0.00041 | <0.00013 | 0.0248 | <0.00013 | <0.00013 | 0.0275 | <0.00013 | <0.00013 | 0.869 | 0.00019 | <0.00013 | 0.858 | 0.00603 | 0.00018 | 0.0356 | <0.00013 | <0.00013 | 0.0325 | 0.00016 | <0.00013
PFOS | GEO82 | ug/l | 0.826 | 0.00018 | 0.00303 | 0.896 | 0.0076 | 0.00013 | 0.776 | <0.00260 | <0.00260 | 0.797 | <0.00260 | <0.00260 | [6 empty] | 0.649 | 0.00042 | <0.00013 | 0.811 | 0.00056 | <0.00013
6:2 FTAB | TM434 | ng/l | 764 | <10 | <10 | 529 | <10 | <10 | 689 | <10 | <10 | 622 | <10 | <10 | 470 | <10 | <10 | 492 | <10 | <10 | 633 | <10 | <10 | 643 | <10 | <10

## LEP results
C 2857609 Perenco UK: Dimlington Terminal | [20 empty] | New Result for H1 starts here
Laboratory Number |  |  | 25445191 | 25445192 | 25445193 | 25445194 | 25445195 | 25445196 | 25526197 | 25526199 | 25526198 | 25526200 | 25526201 | 25526202 | 25597263 | 25597264 | 25597265 | 25619497 | 25619498 | 25619499 | 25656303 | 25656305 | 25656304 | 25698565 | 25698566 | 25698567 | 25730662 | 25730663 | 25730664 | 25780342 | 25780344 | 25780343 | 25806507 | 25806508 | 25806509 | 25823388 | 25823389 | 25823390 | 25854309 | 25854310 | 25854311 | 25878473 | 25878474 | 25878475 | 25892207 | 25892208 | 25892209
Customer Sample Ref. |  |  | 1 Inlet - 1 | Outlet - 1st Filter | Outlet - 2nd Filter | 1 Inlet - 2 | 1 Outlet - 1st Filter | Outlet - 2nd Filter | Filter 1 Inlet - 1 | Filter 2 Outlet - 1 | Filter 1 Outlet -1 | Filter 1 Inlet - 2 | Filter 1 Outlet - 2 | Filter 2 Outlet - 2 | Filter 1 Inlet - 1 | Filter 1 Outlet - 1 | Filter 2 Outlet - 1 | Filter 1 Inlet | Filter 1 OUTLET | Filter 2 OUTLET | Filter 1 Inlet | Filter 2 Outlet | Filter 1 Outlet | Filter 1 INLET | Filter 1 OUTLET | Filetr 2 OUTLET | Filter 1 INLET | Filter 1 OUTLET | Filter 2 OUTLET | Filter 1 INLET | Filter 2 OUTLET | Filter 1 OUTLET | Filter 1 INLET | Filter 1 OUTLET | Filter 2 OUTLET | Filter 1 INLET | Filter 1 OUTLET | Filter 2 OUTLET | Filter 1 INLET | Filter 1 OUTLET | Filter 2 OUTLET | Filter 1 INLET | Filter 1 OUTLET | Filter 2 OUTLET | Filter 1 Inlet | Filter 2 Inlet | Filter 2 Outlet
Sample Matrix |  |  | Not Specified | Not Specified | Not Specified | Not Specified | Not Specified | Not Specified | Not Specified | Not Specified | Not Specified | Not Specified | Not Specified | Not Specified | Not Specified | Not Specified | Not Specified | Surface Water | Surface Water | Surface Water | Surface Water | Surface Water | Surface Water | Surface Water | Surface Water | Surface Water | Surface Water | Surface Water | Surface Water | Surface Water | Surface Water | Surface Water | Surface Water | Surface Water | Surface Water | Surface Water | Surface Water | Surface Water | Surface Water | Surface Water | Surface Water | Surface Water | Surface Water | Surface Water | Surface Water | Surface Water | Surface Water
Sample Date |  |  | 15/06/2025 00:00:00 | 15/06/2025 00:00:00 | 15/06/2025 00:00:00 | 05/07/2025 00:00:00 | 05/07/2025 00:00:00 | 05/07/2025 00:00:00 | 05/08/2025 00:00:00 | 05/08/2025 00:00:00 | 05/08/2025 00:00:00 | 06/08/2025 00:00:00 | 06/08/2025 00:00:00 | 06/08/2025 00:00:00 | 02/09/2025 00:00:00 | 02/09/2025 00:00:00 | 02/09/2025 00:00:00 | 12/09/2025 11:00:00 | 12/09/2025 11:00:00 | 12/09/2025 11:00:00 | 2025-09-25 | 2025-09-25 | 2025-09-25 | 2025-10-10 | 2025-10-10 | 2025-10-10 | 2025-10-28 | 2025-10-28 | 2025-10-28 | 2025-11-10 | 2025-11-10 | 2025-11-10 | 2025-11-17 | 2025-11-17 | 2025-11-17 | 27/11/25 | 27/11/25 | 27/11/25 | 07/12/25 | 07/12/25 | 07/12/25 | 2025-12-17 | 2025-12-17 | 2025-12-17 | 2025-12-27 | 2025-12-27 | 2025-12-27
[45 empty] | 09:00 | 09:00 | 09:00
Point Code
Analyte | Method | Units
11Cl-PF3OUdS (763051-92-9) | TM434 | ng/l | <100 | <2 | <2 | <100 | <2 | <2 | I/S | <2 | <2 | I/S | <2 | <2 | I/S | <2 | I/S | <50 | <2 | <2 | <10 | <2 | <2 | <2 | <2 | <2 | <100 | <2 | <2 | <100 | <2 | <2 | <100 | <2 | <2 | <100 | <2 | <2 | <50 | <2 | <2 | <50 | <2 | <2 | <50 | <2 | <2
3:3 FTCA (356-02-5) | TM434 | ng/l | <100 | <2 | <2 | <100 | <2 | <2 | I/S | <5 | <5 | <125 | <5 | <5 | I/S | <5 | I/S | <125 | <5 | <5 | <25 | <5 | <5 | 51.3 | <5 | <5 | <250 | <5 | <5 | <250 | <5 | <5 | <250 | <5 | <5 | <250 | <5 | <5 | <125 | <5 | <5 | <125 | <5 | <5 | <125 | <5 | <5
4:2 FTS (757124-72-4) | TM434 | ng/l | <50 | <1 | <1 | <50 | <1 | <1 | I/S | <1 | <1 | <25 | <1 | <1 | I/S | <1 | I/S | <25 | <1 | <1 | <5 | <1 | <1 | 1.65 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <25 | <1 | <1 | <25 | <1 | <1 | <25 | <1 | <1
5:3 FTCA (914637-49-3) | TM434 | ng/l | <250 | <5 | <5 | <250 | <5 | <5 | I/S | <5 | <5 | <125 | <5 | <5 | I/S | <5 | I/S | 140 | <5 | <5 | 204 | <5 | <5 | 129 | <5 | <5 | <250 | <5 | <5 | <250 | <5 | <5 | <250 | <5 | <5 | <250 | <5 | <5 | <125 | 7.75 | <5 | <125 | <5 | <5 | <125 | 27.2 | <5
6:2 FTS (27619-97-2) | TM434 | ng/l | 8960 | <1 | <1 | 9030 | 5.81 | 12.4 | I/S | 155 | 3.46 | 292 | 266 | 2.92 | I/S | <1 | I/S | Incomplete | 4.9 | 3.57 | 5660 | <1 | <1 | 8500 | 1.8 | 1.88 | 8180 | <1 | 1.95 | 7380 | <1 | I/S | 6440 | 7.53 | 7.14 | 4330 | 2.83 | 1.55 | 3920 | 868 | 13.3 | 4450 | 48.2 | 2.46 | 4620 | 910 | 30.3
7:3 FTCA (812-70-4) | TM434 | ng/l | <250 | <5 | <5 | <250 | <5 | <5 | I/S | <5 | <5 | <125 | <5 | <5 | I/S | <5 | I/S | <125 | <5 | <5 | <25 | <5 | <5 | <5 | <5 | <5 | <250 | <5 | <5 | <250 | <5 | <5 | <250 | <5 | <5 | <250 | <5 | <5 | <125 | <5 | <5 | <125 | <5 | <5 | <125 | <5 | <5
8:2 FTS (39108-34-4) | TM434 | ng/l | <100 | <2 | <2 | <100 | <2 | <2 | I/S | 6.78 | <2 | <50 | 6.91 | <2 | I/S | <2 | I/S | <50 | <2 | <2 | 59.1 | <2 | <2 | 83.9 | <2 | <2 | <100 | <2 | <2 | <100 | <2 | <2 | <100 | <2 | <2 | <100 | <2 | <2 | <50 | 13.8 | <2 | <50 | <2 | <2 | <50 | 17.7 | <2
9Cl-PF3ONS (756426-58-1) | TM434 | ng/l | <50 | <1 | <1 | <50 | <1 | <1 | I/S | <1 | <1 | <25 | <1 | <1 | I/S | <1 | I/S | <25 | <1 | <1 | <5 | <1 | <1 | <1 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <25 | <1 | <1 | <25 | <1 | <1 | <25 | <1 | <1
ADONA (919005-14-4) | TM434 | ng/l | <50 | <1 | <1 | <50 | <1 | <1 | I/S | <1 | <1 | <25 | <1 | <1 | I/S | <1 | I/S | <25 | <1 | <1 | <5 | <1 | <1 | <1 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <25 | <1 | <1 | <25 | <1 | <1 | <25 | <1 | <1
Branched PFOS | TM434 | ng/l | 384 | <0.65 | <0.65 | 364 | <0.65 | <0.65 | I/S | 20.1 | <0.65 | 57 | 32.1 | <0.65 | I/S | <0.65 | I/S | 282 | <0.65 | <0.65 | 370 | 0.857 | <0.65 | 340 | 1.72 | <0.65 | 348 | <0.65 | <0.65 | 427 | <0.65 | <0.65 | 289 | <0.65 | <0.65 | 276 | <0.65 | <0.65 | 289 | 73.8 | 1.57 | 283 | 4.66 | 1.03 | 234 | 133 | 2.94
EtFOSAA (2991-50-6) | TM434 | ng/l | <100 | <2 | <2 | <100 | <2 | <2 | I/S | <2 | <2 | <50 | <2 | <2 | I/S | <2 | I/S | <50 | <2 | <2 | <10 | <2 | <2 | <2 | <2 | <2 | <100 | <2 | <2 | <100 | <2 | <2 | <100 | <2 | <2 | <100 | <2 | <2 | <50 | <2 | <2 | <50 | <2 | <2 | <50 | <2 | <2
EtFOSE (1691-99-2) | TM434 | ng/l | <500 | <10 | <10 | <500 | <10 | <10 | I/S | <10 | <10 | I/S | <10 | <10 | I/S | <10 | I/S | <250 | <10 | <10 | <50 | <10 | <10 | <10 | <10 | <10 | <500 | <10 | <10 | <500 | <10 | <10 | <500 | <10 | <10 | <500 | <10 | <10 | <250 | <10 | <10 | <250 | <10 | <10 | <250 | <10 | <10
FBSA (30334-69-1) | TM434 | ng/l | <50 | <1 | <1 | <50 | <1 | <1 | I/S | <1 | <1 | <25 | <1 | <1 | I/S | <1 | I/S | <25 | <1 | <1 | 23.5 | <1 | <1 | 39.6 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <25 | 3.09 | <1 | <25 | <1 | <1 | <25 | 3.6 | <1
FHxSA (41997-13-1) | TM434 | ng/l | 272 | <1 | <1 | 266 | <1 | <1 | I/S | 1.25 | <1 | <25 | 5.39 | <1 | I/S | <1 | I/S | 166 | <1 | <1 | 206 | <1 | <1 | 188 | <1 | <1 | 274 | <1 | <1 | 229 | <1 | <1 | 178 | <1 | <1 | 132 | <1 | <1 | 164 | 26 | <1 | 160 | 3.72 | <1 | 116 | 39.8 | <1
HFPO-DA (13252-13-6) | TM434 | ng/l | <100 | <2 | <2 | <100 | <2 | <2 | I/S | <2 | <2 | <50 | <2 | <2 | I/S | <2 | I/S | <50 | <2 | <2 | <10 | <2 | <2 | <2 | <2 | <2 | <100 | <2 | <2 | <100 | <2 | <2 | <100 | <2 | <2 | <100 | <2 | <2 | <50 | <2 | <2 | <50 | <2 | <2 | <50 | <2 | <2
HFPO-TA (13252-14-7) | TM434 | ng/l | <250 | <5 | <5 | <250 | <5 | <5 | I/S | <5 | <5 | <125 | <5 | <5 | I/S | <5 | I/S | <125 | <5 | <5 | <25 | <5 | <5 | <5 | <5 | <5 | <250 | <5 | <5 | <250 | <5 | <5 | <250 | <5 | <5 | <250 | <5 | <5 | <125 | 5.02 | <5 | <125 | <5 | <5 | <125 | <5 | <5
Linear PFOS (1763-23-1) | TM434 | ng/l | 1020 | <0.65 | <0.65 | 934 | 1.27 | <0.65 | I/S | 64.3 | <0.65 | 82.5 | 83.8 | <0.65 | I/S | <0.65 | I/S | 678 | 1.51 | 0.918 | 941 | 1.14 | 0.716 | 843 | 1.76 | <0.65 | 673 | <0.65 | <0.65 | 914 | 1.09 | <0.65 | 826 | 4.19 | 2.67 | 761 | 0.945 | <0.65 | 794 | 120 | 1.33 | 796 | 3.24 | 1.1 | 470 | 192 | 3.05
MeFOSAA (2355-31-9) | TM434 | ng/l | <100 | <2 | <2 | <100 | <2 | <2 | I/S | <2 | <2 | <50 | <2 | <2 | I/S | <2 | I/S | <50 | <2 | <2 | <10 | <2 | <2 | <2 | <2 | <2 | <100 | <2 | <2 | <100 | <2 | <2 | <100 | <2 | <2 | <100 | <2 | <2 | <50 | <2 | <2 | <50 | <2 | <2 | <50 | <2 | <2
MeFOSE (24448-09-7) | TM434 | ng/l | <500 | <10 | <10 | <500 | <10 | <10 | I/S | <10 | <10 | <250 | <10 | <10 | I/S | <10 | I/S | <250 | <10 | <10 | <50 | <10 | <10 | <10 | <10 | <10 | <500 | <10 | <10 | <500 | <10 | <10 | <500 | <10 | <10 | <500 | <10 | <10 | <250 | <10 | <10 | <250 | <10 | <10 | <250 | <10 | <10
N-EtFOSA (4151-50-2) | TM434 | ng/l | <50 | <1 | <1 | <50 | <1 | <1 | I/S | <1 | <1 | <25 | <1 | <1 | I/S | <1 | I/S | <25 | <1 | <1 | <5 | <1 | <1 | <1 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <25 | <1 | <1 | <25 | <1 | <1 | <25 | <1 | <1
NFDHA (151772-58-6) | TM434 | ng/l | <150 | <3 | <3 | <150 | <3 | <3 | I/S | <3 | <3 | <75 | <3 | <3 | I/S | <3 | I/S | <75 | <3 | <3 | <15 | <3 | <3 | <3 | <3 | <3 | <150 | <3 | <3 | <150 | <3 | <3 | <150 | <3 | <3 | <150 | <3 | <3 | <75 | <3 | <3 | <75 | <3 | <3 | <75 | <3 | <3
N-MeFOSA (31506-32-8) | TM434 | ng/l | <50 | <1 | <1 | <50 | <1 | <1 | I/S | <1 | <1 | I/S | <1 | <1 | I/S | <1 | I/S | <25 | <1 | <1 | <5 | <1 | <1 | <1 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <25 | <1 | <1 | <25 | <1 | <1 | <25 | <1 | <1
PFBA (375-22-4) | TM434 | ng/l | 524 | <2 | <2 | 420 | <2 | <2 | I/S | 2 | 5.04 | <50 | 9.7 | <2 | I/S | 2.38 | I/S | 330 | 22.3 | <2 | 296 | <2 | <2 | 383 | <2 | <2 | 407 | <2 | <2 | 515 | 24.4 | <2 | 228 | <2 | <2 | <100 | <2 | <2 | 116 | 47.6 | <2 | 115 | 6.71 | <2 | <50 | 67.5 | <2
PFBS (375-73-5) | TM434 | ng/l | <50 | <1 | <1 | <50 | <1 | <1 | I/S | <1 | <1 | <25 | <1 | <1 | I/S | <1 | I/S | <25 | <1 | <1 | 19.4 | <1 | <1 | 28.7 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <25 | 2.94 | <1 | <25 | <1 | <1 | <25 | 3.52 | <1
PFDA (335-76-2) | TM434 | ng/l | <100 | <2 | <2 | <100 | <2 | <2 | I/S | <2 | <2 | <50 | <2 | <2 | I/S | <2 | I/S | <50 | <2 | <2 | <10 | <2 | <2 | <2 | <2 | <2 | <100 | <2 | <2 | <100 | <2 | <2 | <100 | <2 | <2 | <100 | <2 | <2 | <50 | <2 | <2 | <50 | <2 | <2 | <50 | <2 | <2
PFDoA (307-55-1) | TM434 | ng/l | <100 | <2 | <2 | <100 | <2 | <2 | I/S | <2 | <2 | <50 | <2 | <2 | I/S | <2 | I/S | <50 | <2 | <2 | <10 | <2 | <2 | <2 | <2 | <2 | <100 | <2 | <2 | <100 | <2 | <2 | <100 | <2 | <2 | <100 | <2 | <2 | <50 | <2 | <2 | <50 | <2 | <2 | <50 | <2 | <2
PFDoS (79780-39-5) | TM434 | ng/l | 137 | <2 | <2 | <100 | 6.22 | 6.24 | I/S | 5.54 | 4.27 | <50 | 5.76 | 5.25 | I/S | 2.79 | I/S | <50 | 5.66 | 4.17 | <10 | 2.01 | 3.1 | 20.7 | 2.95 | <2 | <100 | <2 | 2.44 | <100 | <2 | <2 | <100 | 2.28 | <2 | <100 | <2 | <2 | <50 | 5.26 | <2 | <50 | <2 | <2 | <50 | 2.7 | <2
PFDS (335-77-3) | TM434 | ng/l | <100 | <2 | <2 | <100 | <2 | <2 | I/S | <2 | <2 | <50 | <2 | <2 | I/S | <2 | I/S | <50 | <2 | <2 | <10 | <2 | <2 | 6.33 | <2 | <2 | <100 | <2 | <2 | <100 | <2 | <2 | <100 | <2 | <2 | <100 | <2 | <2 | <50 | <2 | <2 | <50 | <2 | <2 | <50 | <2 | <2
PFecHS (133201-07-7) | TM434 | ng/l | <50 | <1 | <1 | <50 | <1 | <1 | I/S | <1 | <1 | <25 | <1 | <1 | I/S | SEE A/C | I/S | <25 | <1 | <1 | <5 | <1 | <1 | <1 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <25 | <1 | <1 | <25 | <1 | <1 | <25 | <1 | <1
PFEESA (113507-82-7) | TM434 | ng/l | <50 | <1 | <1 | <50 | <1 | <1 | I/S | <1 | <1 | <25 | <1 | <1 | I/S | <1 | I/S | <25 | <1 | <1 | <5 | <1 | <1 | <1 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <25 | <1 | <1 | <25 | <1 | <1 | <25 | <1 | <1
PFHpA (375-85-9) | TM434 | ng/l | 521 | <1 | <1 | 312 | <1 | 1.29 | I/S | 1.83 | <1 | <25 | 5.46 | <1 | I/S | <1 | I/S | 208 | <1 | <1 | 234 | <1 | <1 | 283 | <1 | <1 | 270 | <1 | <1 | 386 | <1 | <1 | 185 | <1 | <1 | 147 | <1 | <1 | 142 | 34 | 1.49 | 136 | 3.06 | <1 | 109 | 52.9 | 2.23
PFHpS (375-92-8) | TM434 | ng/l | <50 | <1 | <1 | <50 | <1 | <1 | I/S | <1 | <1 | <25 | <1 | <1 | I/S | SEE A/C | I/S | <25 | <1 | <1 | 14.7 | <1 | <1 | 21.6 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <25 | 2.38 | <1 | <25 | <1 | <1 | <25 | 3.1 | <1
PFHxA (307-24-4) | TM434 | ng/l | 1490 | <1 | <1 | 1370 | 1.36 | 1.48 | I/S | 6.28 | 1.95 | 28.7 | 20.9 | 1.29 | I/S | <1 | I/S | 1010 | 1.7 | <1 | 964 | <1 | <1 | 1370 | 1.38 | <1 | 1170 | <1 | 1.23 | 1410 | <1 | <1 | 860 | <1 | <1 | 597 | <1 | <1 | 487 | 140 | 3.05 | 506 | 11.3 | <1 | 391 | 218 | 7.99
PFHxDA (67905-19-5) | TM434 | ng/l | <50 | <1 | <1 | <50 | <1 | <1 | I/S | <1 | <1 | <25 | <1 | <1 | I/S | <1 | I/S | <25 | <1 | <1 | <5 | <1 | <1 | <1 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <25 | <1 | <1 | <25 | <1 | <1 | <25 | <1 | <1
PFHxS (355-46-4) | TM434 | ng/l | 461 | <1 | <1 | 444 | <1 | <1 | I/S | 4.58 | <1 | <25 | 11.1 | <1 | I/S | <1 | I/S | 273 | <1 | <1 | 336 | <1 | <1 | 389 | 2.44 | <1 | 375 | <1 | <1 | 447 | <1 | <1 | 365 | <1 | <1 | 320 | <1 | <1 | 313 | 41.6 | <1 | 314 | 2.26 | <1 | 243 | 81 | 1.28
PFMOBA (863090-89-5) | TM434 | ng/l | <50 | <1 | <1 | <50 | <1 | <1 | I/S | <1 | <1 | <25 | <1 | <1 | I/S | <1 | I/S | <25 | <1 | <1 | <5 | <1 | <1 | <1 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <25 | <1 | <1 | <25 | <1 | <1 | <25 | <1 | <1
PFMOPrA (377-73-1) | TM434 | ng/l | <50 | <1 | <1 | <50 | <1 | <1 | I/S | <1 | <1 | <25 | <1 | <1 | I/S | <1 | I/S | <25 | <1 | <1 | <5 | <1 | <1 | <1 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <25 | <1 | <1 | <25 | <1 | <1 | <25 | <1 | <1
PFNA (375-95-1) | TM434 | ng/l | <50 | <1 | <1 | <50 | <1 | <1 | I/S | <1 | <1 | <25 | <1 | <1 | I/S | <1 | I/S | <25 | <1 | <1 | 6.63 | <1 | <1 | 7.28 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <25 | <1 | <1 | <25 | <1 | <1 | <25 | 1.3 | <1
PFNS (68259-12-1) | TM434 | ng/l | <50 | <1 | <1 | <50 | <1 | <1 | I/S | <1 | <1 | I/S | <1 | <1 | I/S | <1 | I/S | <25 | <1 | <1 | <5 | <1 | <1 | 2.82 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <25 | <1 | <1 | <25 | <1 | <1 | <25 | <1 | <1
PFOA (335-67-1) | TM434 | ng/l | 66.2 | <0.65 | <0.65 | 80.4 | <0.65 | <0.65 | I/S | <0.65 | <0.65 | <16.3 | 2.98 | <0.65 | I/S | <0.65 | I/S | 54.1 | <0.65 | <0.65 | 61.8 | <0.65 | <0.65 | 85.3 | <0.65 | <0.65 | <32.5 | <0.65 | <0.65 | 98.5 | <0.65 | <0.65 | 75.1 | <0.65 | <0.65 | 58.5 | <0.65 | <0.65 | 43.7 | 11.2 | <0.65 | 43.5 | 1.2 | <0.65 | 25.9 | 12.3 | <0.65
PFODA (16517-11-6) | TM434 | ng/l | <50 | <1 | <1 | <50 | <1 | <1 | I/S | <1 | <1 | <25 | <1 | <1 | I/S | <1 | I/S | <25 | <1 | <1 | <5 | <1 | <1 | <1 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <25 | <1 | <1 | <25 | <1 | <1 | <25 | <1 | <1
PFOSA (754-91-6) | TM434 | ng/l | <100 | <2 | <2 | <100 | <2 | <2 | I/S | <2 | <2 | <50 | <2 | <2 | I/S | <2 | I/S | <50 | <2 | <2 | 12.6 | <2 | <2 | 13.5 | <2 | <2 | <100 | <2 | <2 | <100 | <2 | <2 | <100 | <2 | <2 | <100 | <2 | <2 | <50 | <2 | <2 | <50 | <2 | <2 | <50 | <2 | <2
PFPA (2706-90-3) | TM434 | ng/l | 2190 | <1 | 1.21 | 1600 | 1.59 | 1.59 | I/S | 5.77 | 2.6 | 37.6 | 26.6 | 2.04 | I/S | <1 | I/S | 1090 | 11.9 | <1 | 995 | <1 | <1 | 1900 | 1.11 | <1 | 1660 | <1 | 1.42 | 2100 | 1.44 | <1 | 870 | <1 | <1 | 844 | <1 | <1 | 571 | 142 | 4.43 | 591 | 12.8 | <1 | 429 | 258 | 8.95
PFPeS (2706-91-4) | TM434 | ng/l | <50 | <1 | <1 | 52.6 | <1 | <1 | I/S | <1 | <1 | <25 | <1 | <1 | I/S | <1 | I/S | 31.4 | <1 | <1 | 26.8 | <1 | <1 | 39.5 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | 27.6 | 2.72 | <1 | 33.2 | <1 | <1 | <25 | 5.88 | <1
PFTeA (376-06-7) | TM434 | ng/l | <50 | <1 | <1 | <50 | <1 | <1 | I/S | <1 | <1 | <25 | <1 | <1 | I/S | <1 | I/S | <25 | <1 | <1 | <5 | <1 | <1 | <1 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <25 | <1 | <1 | <25 | <1 | <1 | <25 | <1 | <1
PFTrDA (72629-94-8) | TM434 | ng/l | <150 | <3 | <3 | <150 | <3 | <3 | I/S | <3 | <3 | I/S | <3 | <3 | I/S | SEE A/C | I/S | <75 | <3 | <3 | <15 | <3 | <3 | <3 | <3 | <3 | <150 | <3 | <3 | <150 | <3 | <3 | <150 | <3 | <3 | <150 | <3 | <3 | <75 | <3 | <3 | <75 | <3 | <3 | <75 | <3 | <3
PFTrDS (174675-49-1) | TM434 | ng/l | 63 | <1 | <1 | <50 | 1.24 | <1 | I/S | <1 | <1 | <25 | <1 | <1 | I/S | <1 | I/S | <25 | 1.37 | 1.1 | <5 | <1 | <1 | 4.28 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <50 | <1 | <1 | <25 | <1 | <1 | <25 | <1 | <1 | <25 | 0 | <1
PFUnA (2058-94-8) | TM434 | ng/l | <100 | <2 | <2 | <100 | <2 | <2 | I/S | <2 | <2 | <50 | <2 | <2 | I/S | <2 | I/S | <50 | <2 | <2 | <10 | <2 | <2 | <2 | <2 | <2 | <100 | <2 | <2 | <100 | <2 | <2 | <100 | <2 | <2 | <100 | <2 | <2 | <50 | <2 | <2 | <50 | <2 | <2 | <50 | <2 | <2
PFUnDS (749786-16-1) | TM434 | ng/l | <100 | <2 | <2 | <100 | <2 | <2 | I/S | <2 | <2 | <50 | <2 | <2 | I/S | <2 | I/S | <50 | <2 | <2 | <10 | <2 | <2 | 4.55 | <2 | <2 | <100 | <2 | <2 | <100 | <2 | <2 | <100 | <2 | <2 | <100 | <2 | <2 | <50 | <2 | <2 | <50 | <2 | <2 | <50 | <2 | <2
Total PFOS (1763-23-1) | TM434 | ng/l | 1400 | <0.65 | <0.65 | 1300 | 1.27 | <0.65 | I/S | 84.4 | <0.65 | 140 | 116 | <0.65 | I/S | <0.65 | I/S | 960 | 1.51 | 0.918 | 1310 | 2 | 0.716 | 1180 | 3.49 | <0.65 | 1020 | <0.65 | <0.65 | 1340 | 1.09 | <0.65 | 1110 | 4.19 | 2.67 | 1040 | 0.945 | <0.65 | 1080 | 194 | 2.9 | 1080 | 7.9 | 2.13 | 704 | 325 | 5.99
PFOA | GEO82 | ug/l | 0.0826 | <0.00013 | <0.00013 | 0.0815 | 0.00019 | <0.00013 | 0.0876 | <0.0130 | <0.0130 | 0.0868 | <0.0130 | <0.0130 | 0.0986 | <0.0130 | <0.0130
PFOS | GEO82 | ug/l | 1.89 | 0.00088 | 0.00039 | 1.53 | 0.00143 | 0.00071 | 2.09 | 0.0808 | <0.0130 | 1.76 | 0.116 | <0.0130 | To Follow | <0.0130 | <0.0130
6:2 FTAB | TM434 | ng/l | 1150 | <10 | <10 | 1100 | <10 | <10 | I/S | 49.4 | <10 | <250 | 62 | <10 | I/S | <10 | I/S | 1270 | <10 | <10 | 1150 | <10 | <10 | 992 | <10 | <10 | 1010 | <10 | <10 | 1500 | <10 | <10 | 926 | <10 | <10 | 816 | <10 | <10 | 1040 | 78.5 | <10 | 894 | <10 | <10 | 640 | 125 | <10
[10 empty] | 25526199 should be the outlet of the 1st filter and not the outlet of the 2nd filter as labelled; technically, the concentration in the final discharge following flow through the second filter would be less than the outlet from the first filter, | [12 empty] | 25656304 should be the outlet of the 2nd filter and not the outlet of the 1st filter as labelled; technically, the concentration in the final discharge following flow through the second filter would be less than the outlet from the first filter | [7 empty] | 25780344 should be the outlet of the 1st filter and not the outlet of the 2nd filter as it is not logical to get higher PFAS concentration post treatment from the 2nd filter.
Note on K2: ABRAHAM Nicholas:
Note on X3: ABRAHAM Nicholas: Should be filter 2 outlet and not 1 as erroneously labelled