## note
SZC LVSE calculation data for spp099 v3
AWAC data at SZC intakes - measurement height lower than model outputs (2.04 to 2.09m off bed re model at 2.5m off bed)
2 ADCP data files SZ1 Northern, SZ2 southern. The instrument was an AWAC with 10 minute measurements.
ADCP measurement locations in centre of 3 possible SZC intake head locations on northern and southern intake tunnel routes.
Only difference between these calculations and those made with the SZ GETM model in SPP099 v1 is to substitute ADCP data for model data for the SZC calculations

## SZC results summary
Results summary for SPP099 v3
SZC intercept areas (m2) - data source Sizewell C intake AWAC deployment 10 minute interval data | [13 empty] | Sensitivity analyses
|  | slack velocity= |  | 0.3 | m/s | Sensitivity analyses | slk threshold 0.2 m/s | [6 empty] | slk threshold 0.3 m/s | [6 empty] | 0.25
|  | slk threshold m/s |  |  |  | Misalignment degrees | [6 empty] | Misalignment degrees | [6 empty] | slk threshold m/2
|  | 0.1 | 0.2 | 0.3 |  | -3 | -2 | -1.85 | 0 | 1.85 | 2 | 3 | -3 | -2 | -1.85 | 0 | 1.85 | 2 | 3 | 0.1 | 0.2 | 0.3
| Northern | 33.1901 | 41.6071 | 50.2327 |  | 45.27 | 43.39 | 43.2 | 41.6071 | 42.25 | 42.35 | 43.66 | 53.85 | 52 | 51.81 | 50.2327 | 50.84 | 50.94 | 52.21 | 32.39 | 38.99
| Southern | 33.6081 | 43.0418 | 53.3013 |  | 46.77 | 44.89 | 44.7 | 43.0418 | 43.8 | 43.86 | 45.28 | 57 | 55.15 | 54.97 | 53.3013 | 53.95 | 54.04 | 55.4 | 32.52 | 40.1
| SZB area m2 | 118.4 | 118.4 | 123.5 | [15 empty] | 115.25
Ratio SZC/SZB intercept areas
| Northern | 0.28032 | 0.35141 | 0.40674 |  | 0.38235 | 0.36647 | 0.36486 | 0.35141 | 0.35684 | 0.35769 | 0.36875 | 0.43603 | 0.42105 | 0.41951 | 0.40674 | 0.41166 | 0.41247 | 0.42275 | #DIV/0! | #DIV/0!
| Southern | 0.28385 | 0.36353 | 0.43159 |  | 0.39502 | 0.37914 | 0.37753 | 0.36353 | 0.36993 | 0.37044 | 0.38243 | 0.46154 | 0.44656 | 0.4451 | 0.43159 | 0.43684 | 0.43757 | 0.44858 | #DIV/0! | #DIV/0!
| mean ratio | 0.28209 | 0.35747 | 0.41917 |  | 0.38868 | 0.3728 | 0.3712 | 0.35747 | 0.36339 | 0.36406 | 0.37559 | 0.44879 | 0.43381 | 0.43231 | 0.41917 | 0.42425 | 0.42502 | 0.43567 | 0.43381 | 0.42502
118.9%
|  |  | AWAC data |  |  |  | mean |  |  |  | range
|  |  | SZC/SZB ratio |  |  | slk threshold =0.2m/s | 0.35747 |  |  |  | 0.3712 | 0.36339 | (not uniformly distributed - see spp099 v3) | [7 empty] | 111% | of tr406
[6 empty] | vslack 0.3 | 0.41917 |  |  |  | 0.43231 | 0.42425 | (not uniformly distributed - see spp099 v3)
1.7783
GETM model result from SPP099 v1 | [5 empty] | slk threshold =0.2m/s | 0.237
[6 empty] | slk threshold =0.3m/s | 0.295
Ratio of intercept areas AwAC/Model data | [5 empty] | slk threshold =0.2m/s | 1.5083
[6 empty] | slk threshold =0.3m/s | 1.4209

## northern slk 0.1
SZC northern slk 0.1 |  |  | SZC intake alignment: |  |  | 4.5
SZC AWAC data 10 minute intervals
Count of Direction at 2.04m above bed (deg) | Column Labels | [13 empty] | 284
Row Labels | 0-0.1 | 0.1-0.2 | 0.2-0.3 | 0.3-0.4 | 0.4-0.5 | 0.5-0.6 | 0.6-0.7 | 0.7-0.8 | 0.8-0.9 | 0.9-1 | 1-1.1 | Grand Total |  | mid bin | area m2
0-1 | 3 | 4 | 4 | 11 | 9 | 9 | 12 | 12 | 3 |  |  | 67 | 67 | 0.5 | 19.8108
1-2 |  | 1 | 5 | 7 | 18 | 13 | 10 | 15 | 5 |  |  | 74 | 74 | 1.5 | 14.8634
2-3 | 1 | 4 |  | 13 | 16 | 10 | 10 | 15 | 17 | 4 |  | 90 | 90 | 2.5 | 9.9115
3-4 | 2 |  | 6 | 12 | 17 | 18 | 18 | 28 | 20 | 1 |  | 122 | 122 | 3.5 | 4.9565
4-5 |  | 3 | 2 | 11 | 17 | 14 | 19 | 34 | 20 | 3 | 1 | 124 | 124 | 4.5 | 0
5-6 | 1 | 1 | 5 | 8 | 8 | 25 | 26 | 24 | 19 | 2 | 1 | 120 | 120 | 5.5 | 4.9565
6-7 |  |  | 5 | 6 | 25 | 24 | 26 | 39 | 23 | 9 |  | 157 | 157 | 6.5 | 9.9115
7-8 |  | 1 | 11 | 6 | 14 | 21 | 24 | 43 | 27 | 2 |  | 149 | 149 | 7.5 | 14.8634
8-9 | 1 | 1 | 3 | 7 | 17 | 22 | 28 | 17 | 15 | 5 | 2 | 118 | 118 | 8.5 | 19.8108
9-10 | 1 |  | 10 | 6 | 18 | 16 | 21 | 31 | 18 | 6 | 2 | 129 | 129 | 9.5 | 24.7522
10-11 |  | 3 | 3 | 7 | 12 | 19 | 23 | 8 | 19 | 5 |  | 99 | 99 | 10.5 | 29.6861
11-12 |  | 2 | 4 | 18 | 14 | 12 | 12 | 9 | 9 | 1 |  | 81 | 81 | 11.5 | 34.6109
12-13 |  | 2 | 4 | 12 | 12 | 11 | 2 | 1 | 2 |  |  | 46 | 46 | 12.5 | 39.5252
13-14 | 1 | 2 | 3 | 4 | 9 | 10 | 9 | 5 | 7 | 1 |  | 51 | 51 | 13.5 | 44.4274
14-15 |  | 4 | 6 | 12 | 11 | 10 | 5 | 7 | 2 |  |  | 57 | 57 | 14.5 | 49.3161
15-16 |  |  | 4 | 4 | 6 | 6 | 3 | 1 |  |  |  | 24 | 24 | 15.5 | 54.1898
16-17 | 2 | 3 | 1 | 5 | 1 | 5 | 1 |  |  |  |  | 18 | 18 | 16.5 | 59.0469
17-18 |  | 5 | 2 | 4 | 13 | 5 | [5 empty] | 29 | 29 | 17.5 | 63.8861
18-19 | 2 |  | 3 | 8 | 9 | 8 | 2 |  |  |  |  | 32 | 32 | 18.5 | 68.7058
19-20 |  | 4 | 3 | 8 | 2 | 4 | [5 empty] | 21 | 21 | 19.5 | 73.5046
20-21 |  |  | 2 | 4 | 3 | [6 empty] | 9 | 9 | 20.5 | 78.281
21-22 |  |  | 3 | 3 | 3 | [6 empty] | 9 | 9 | 21.5 | 83.0336
22-23 | 1 | 2 | 3 | 3 | 5 | 1 | [5 empty] | 15 | 15 | 22.5 | 87.7608
23-24 | 1 | 3 | 6 | 3 | 3 | [6 empty] | 16 | 16 | 23.5 | 92.4614
24-25 |  | 2 | 5 | 3 | 1 | [6 empty] | 11 | 11 | 24.5 | 97.1337
25-26 |  | 3 | 1 |  | 3 | [6 empty] | 7 | 7 | 25.5 | 101.7765
26-27 | 3 | 2 | 1 | 3 | [7 empty] | 9 | 9 | 26.5 | 106.3883
27-28 | 1 | 1 | 5 | 4 | [7 empty] | 11 | 11 | 27.5 | 110.9676
28-29 |  |  | 1 | 3 | [7 empty] | 4 | 4 | 28.5 | 115.5132
29-30 |  |  | 2 | 4 | [7 empty] | 6 | 6 | 29.5 | 120.0236
30-31 |  | 2 | 1 | [8 empty] | 3 | 3 | 30.5 | 124.4974
31-32 |  |  | 1 | 2 | [7 empty] | 3 | 3 | 31.5 | 128.9333
32-33 |  | 2 | [9 empty] | 2 | 2 | 32.5 | 133.3299
33-34 |  |  |  | 2 | 1 | [6 empty] | 3 | 3 | 33.5 | 137.6859
34-35 |  | 3 |  | 1 | [7 empty] | 4 | 4 | 34.5 | 142
35-36 |  | 3 | 2 | [8 empty] | 5 | 5 | 35.5 | 146.2708
36-37 | 3 | 2 | 2 | [8 empty] | 7 | 7 | 36.5 | 150.4971
37-38 | 1 | 1 | 1 | [8 empty] | 3 | 3 | 37.5 | 154.6775
38-39 |  | 2 | 1 | [8 empty] | 3 | 3 | 38.5 | 158.8108
39-40 |  | 1 | 1 | [8 empty] | 2 | 2 | 39.5 | 162.8957
40-41 | 3 | 1 |  | 2 | [7 empty] | 6 | 6 | 40.5 | 166.931
41-42 | 1 | 1 | [9 empty] | 2 | 2 | 41.5 | 170.9155
42-43 | 3 | 2 | 3 | [8 empty] | 8 | 8 | 42.5 | 174.8479
43-44 | 1 | 2 | [9 empty] | 3 | 3 | 43.5 | 178.727
44-45 |  | 4 | 1 | [8 empty] | 5 | 5 | 44.5 | 182.5517
46-47 |  | 3 | [9 empty] | 3 | 3 | 46.5 | 190.0331
47-48 |  | 4 | [9 empty] | 4 | 4 | 47.5 | 193.6875
48-49 |  | 1 | [9 empty] | 1 | 1 | 48.5 | 197.283
49-50 | 1 | 3 | [9 empty] | 4 | 4 | 49.5 | 200.8183
50-51 |  | 3 | [9 empty] | 3 | 3 | 50.5 | 204.2925
51-52 |  | 3 | 1 | [8 empty] | 4 | 4 | 51.5 | 207.7045
52-53 | 4 | [10 empty] | 4 | 4 | 52.5 | 211.0531
54-55 |  | 1 | 1 | [8 empty] | 2 | 2 | 54.5 | 217.5566
55-56 | 1 |  | 2 | [8 empty] | 3 | 3 | 55.5 | 220.7095
56-57 |  | 5 | [9 empty] | 5 | 5 | 56.5 | 223.7951
58-59 |  | 1 | [9 empty] | 1 | 1 | 58.5 | 229.7608
59-60 |  | 1 | [9 empty] | 1 | 1 | 59.5 | 232.6392
60-61 | 1 | [10 empty] | 1 | 1 | 60.5 | 235.4467
63-64 |  | 2 | [9 empty] | 2 | 2 | 63.5 | 243.4355
64-65 |  | 2 | [9 empty] | 2 | 2 | 64.5 | 245.9512
66-67 |  | 1 | [9 empty] | 1 | 1 | 66.5 | 250.7571
67-68 | 1 | 1 | [9 empty] | 2 | 2 | 67.5 | 253.0459
69-70 | 1 | 1 | [9 empty] | 2 | 2 | 69.5 | 257.3914
71-72 |  | 1 | [9 empty] | 1 | 1 | 71.5 | 261.4234
72-73 | 2 | [10 empty] | 2 | 2 | 72.5 | 263.3202
73-74 |  | 1 | [9 empty] | 1 | 1 | 73.5 | 265.1368
75-76 |  | 1 | [9 empty] | 1 | 1 | 75.5 | 268.5273
77-78 | 1 | [10 empty] | 1 | 1 | 77.5 | 271.5906
78-79 | 1 | 2 | [9 empty] | 3 | 3 | 78.5 | 272.9983
79-80 | 1 | 1 | [9 empty] | 2 | 2 | 79.5 | 274.3229
80-81 | 2 | [10 empty] | 2 | 2 | 80.5 | 275.564
81-82 |  | 2 | [9 empty] | 2 | 2 | 81.5 | 276.7211
82-83 |  | 1 | [9 empty] | 1 | 1 | 82.5 | 277.7939
83-84 |  | 1 | [9 empty] | 1 | 1 | 83.5 | 278.7821
84-85 | 1 | [10 empty] | 1 | 1 | 84.5 | 279.6854
87-88 |  | 1 | [9 empty] | 1 | 1 | 87.5 | 281.8831
89-90 | 1 | [10 empty] | 1 | 1 | 89.5 | 282.9193
90-91 | 3 | 1 | [9 empty] | 4 | 4 | 90.5 | 283.3082
91-92 |  | 1 | [9 empty] | 1 | 1 | 91.5 | 283.6108
92-93 | 2 | [10 empty] | 2 | 2 | 92.5 | 283.827
95-96 |  | 1 | [9 empty] | 1 | 1 | 95.5 | 283.9567
99-100 | 2 | [10 empty] | 2 | 2 | 99.5 | 282.9193
101-102 | 1 | [10 empty] | 1 | 1 | 101.5 | 281.8831
102-103 |  | 1 | [9 empty] | 1 | 1 | 102.5 | 281.2361
103-104 | 1 | [10 empty] | 1 | 1 | 103.5 | 280.5035
104-105 | 2 | [10 empty] | 2 | 2 | 104.5 | 279.6854
105-106 | 1 | [10 empty] | 1 | 1 | 105.5 | 278.7821
107-108 | 1 | [10 empty] | 1 | 1 | 107.5 | 276.7211
108-109 | 1 | 2 | [9 empty] | 3 | 3 | 108.5 | 275.564
109-110 | 2 | [10 empty] | 2 | 2 | 109.5 | 274.3229
110-111 |  | 1 | [9 empty] | 1 | 1 | 110.5 | 272.9983
111-112 |  | 2 | [9 empty] | 2 | 2 | 111.5 | 271.5906
113-114 | 1 | [10 empty] | 1 | 1 | 113.5 | 268.5273
114-115 |  | 1 | [9 empty] | 1 | 1 | 114.5 | 266.8727
115-116 |  | 1 | [9 empty] | 1 | 1 | 115.5 | 265.1368
117-118 | 1 | [10 empty] | 1 | 1 | 117.5 | 261.4234
118-119 |  |  | 1 | [8 empty] | 1 | 1 | 118.5 | 259.4469
119-120 | 3 | [10 empty] | 3 | 3 | 119.5 | 257.3914
122-123 | 2 | 1 | [9 empty] | 3 | 3 | 122.5 | 250.7571
123-124 |  | 2 | [9 empty] | 2 | 2 | 123.5 | 248.392
125-126 |  | 1 | [9 empty] | 1 | 1 | 125.5 | 243.4355
126-127 |  | 1 | [9 empty] | 1 | 1 | 126.5 | 240.8457
127-128 |  | 2 | [9 empty] | 2 | 2 | 127.5 | 238.1824
128-129 |  | 1 | 2 | [8 empty] | 3 | 3 | 128.5 | 235.4467
129-130 |  |  | 1 | [8 empty] | 1 | 1 | 129.5 | 232.6392
132-133 |  | 2 | [9 empty] | 2 | 2 | 132.5 | 223.7951
133-134 |  | 1 | [9 empty] | 1 | 1 | 133.5 | 220.7095
134-135 |  | 2 | [9 empty] | 2 | 2 | 134.5 | 217.5566
135-136 | 2 | [10 empty] | 2 | 2 | 135.5 | 214.3375
137-138 | 1 | [10 empty] | 1 | 1 | 137.5 | 207.7045
138-139 | 2 | [10 empty] | 2 | 2 | 138.5 | 204.2925
139-140 |  | 2 | [9 empty] | 2 | 2 | 139.5 | 200.8183
141-142 |  |  | 1 | [8 empty] | 1 | 1 | 141.5 | 193.6875
143-144 |  | 2 | [9 empty] | 2 | 2 | 143.5 | 186.3208
144-145 | 2 | 1 | [9 empty] | 3 | 3 | 144.5 | 182.5517
145-146 |  | 1 | [9 empty] | 1 | 1 | 145.5 | 178.727
147-148 | 2 | 1 | 2 | [8 empty] | 5 | 5 | 147.5 | 170.9155
148-149 |  | 2 | [9 empty] | 2 | 2 | 148.5 | 166.931
149-150 |  | 2 | [9 empty] | 2 | 2 | 149.5 | 162.8957
150-151 | 2 | 2 | [9 empty] | 4 | 4 | 150.5 | 158.8108
151-152 |  | 3 | [9 empty] | 3 | 3 | 151.5 | 154.6775
152-153 |  |  | 5 | [8 empty] | 5 | 5 | 152.5 | 150.4971
153-154 | 2 | 8 | [9 empty] | 10 | 10 | 153.5 | 146.2708
154-155 | 1 | 2 | 2 | 2 | [7 empty] | 7 | 7 | 154.5 | 142
155-156 |  | 1 | [9 empty] | 1 | 1 | 155.5 | 137.6859
156-157 |  | 3 | 1 | [8 empty] | 4 | 4 | 156.5 | 133.3299
157-158 |  |  | 1 | [8 empty] | 1 | 1 | 157.5 | 128.9333
158-159 |  | 4 | 1 | [8 empty] | 5 | 5 | 158.5 | 124.4974
159-160 |  | 4 | 1 | [8 empty] | 5 | 5 | 159.5 | 120.0236
160-161 | 1 | 4 | 1 | 2 | [7 empty] | 8 | 8 | 160.5 | 115.5132
161-162 | 1 | 4 | 3 | 1 | [7 empty] | 9 | 9 | 161.5 | 110.9676
162-163 |  | 5 | 3 | [8 empty] | 8 | 8 | 162.5 | 106.3883
163-164 | 2 | 2 | 3 | 1 | [7 empty] | 8 | 8 | 163.5 | 101.7765
164-165 | 1 | 1 | 1 | 3 | [7 empty] | 6 | 6 | 164.5 | 97.1337
165-166 |  | 4 | 6 |  |  | 1 | [5 empty] | 11 | 11 | 165.5 | 92.4614
166-167 |  | 2 | 1 | 3 | [7 empty] | 6 | 6 | 166.5 | 87.7608
167-168 | 2 | 4 | 2 | 1 | 2 | [6 empty] | 11 | 11 | 167.5 | 83.0336
168-169 |  | 6 | 1 | 1 | 4 | [6 empty] | 12 | 12 | 168.5 | 78.281
169-170 |  | 1 | 4 | 1 | 5 | [6 empty] | 11 | 11 | 169.5 | 73.5046
170-171 | 1 | 5 | 4 | 3 | 6 | 7 | [5 empty] | 26 | 26 | 170.5 | 68.7058
171-172 |  |  | 6 | 3 | 6 |  |  | 2 |  |  |  | 17 | 17 | 171.5 | 63.8861
172-173 | 1 | 1 | 8 | 10 | 5 | 3 | 2 | 1 |  |  |  | 31 | 31 | 172.5 | 59.0469
173-174 |  | 1 | 2 | 7 | 5 | 4 | 1 | 1 |  |  |  | 21 | 21 | 173.5 | 54.1898
174-175 |  | 1 | 6 | 5 | 6 | 2 | 4 | 3 |  |  |  | 27 | 27 | 174.5 | 49.3161
175-176 |  | 2 | 4 | 1 | 19 | 18 | 6 | 6 | 1 |  |  | 57 | 57 | 175.5 | 44.4274
176-177 |  | 2 | 5 | 6 | 12 | 9 | 12 | 7 | 3 |  |  | 56 | 56 | 176.5 | 39.5252
177-178 |  | 1 | 4 | 6 | 9 | 19 | 14 | 18 | 1 |  |  | 72 | 72 | 177.5 | 34.6109
178-179 |  | 2 | 2 | 12 | 20 | 19 | 14 | 13 | 2 |  |  | 84 | 84 | 178.5 | 29.6861
179-180 |  | 1 | 4 | 7 | 13 | 27 | 19 | 20 | 10 |  |  | 101 | 101 | 179.5 | 24.7522
180-181 | 1 | 3 | 5 | 12 | 23 | 24 | 32 | 25 | 14 | 1 |  | 140 | 140 | 180.5 | 19.8108
181-182 | 1 | 1 | 9 | 7 | 21 | 22 | 28 | 22 | 8 | 1 |  | 120 | 120 | 181.5 | 14.8634
182-183 |  | 3 | 2 | 6 | 16 | 32 | 31 | 25 | 25 |  |  | 140 | 140 | 182.5 | 9.9115
183-184 |  |  | 4 | 11 | 25 | 35 | 30 | 30 | 11 | 5 |  | 151 | 151 | 183.5 | 4.9565
184-185 |  | 1 | 6 | 4 | 20 | 21 | 27 | 15 | 6 |  |  | 100 | 100 | 184.5 | 3.4794e-14
185-186 |  | 5 | 2 | 4 | 21 | 32 | 24 | 16 | 3 |  |  | 107 | 107 | 185.5 | 4.9565
186-187 | 1 | 2 | 2 | 5 | 15 | 19 | 18 | 10 | 4 |  |  | 76 | 76 | 186.5 | 9.9115
187-188 |  | 1 | 2 | 10 | 37 | 12 | 13 | 19 | 3 | 2 |  | 99 | 99 | 187.5 | 14.8634
188-189 | 1 | 1 | 2 | 5 | 14 | 14 | 9 | 4 | 1 |  |  | 51 | 51 | 188.5 | 19.8108
189-190 | 2 | 2 | 3 | 5 | 11 | 11 | 4 | 5 |  |  |  | 43 | 43 | 189.5 | 24.7522
190-191 |  | 2 | 5 | 4 | 11 | 14 | 6 | 1 | 1 |  |  | 44 | 44 | 190.5 | 29.6861
191-192 |  | 3 | 1 | 3 | 17 | 7 | 2 | 1 |  |  |  | 34 | 34 | 191.5 | 34.6109
192-193 |  |  |  | 4 | 8 | 13 | 3 |  |  |  |  | 28 | 28 | 192.5 | 39.5252
193-194 | 2 |  | 2 | 9 | 6 | 2 | 1 | 2 |  |  |  | 24 | 24 | 193.5 | 44.4274
194-195 |  | 1 | 5 | 7 | 5 | 2 | 3 |  |  |  |  | 23 | 23 | 194.5 | 49.3161
195-196 |  | 1 | 3 | 2 | 6 | 1 | [5 empty] | 13 | 13 | 195.5 | 54.1898
196-197 |  | 1 | 1 | 4 | 10 | [6 empty] | 16 | 16 | 196.5 | 59.0469
197-198 |  |  | 3 | 3 | 3 | [6 empty] | 9 | 9 | 197.5 | 63.8861
198-199 |  |  | 1 | 3 | 2 | [6 empty] | 6 | 6 | 198.5 | 68.7058
199-200 |  | 2 | 1 | 2 | 3 | [6 empty] | 8 | 8 | 199.5 | 73.5046
200-201 |  | 1 | 2 | 7 | 4 | 1 | [5 empty] | 15 | 15 | 200.5 | 78.281
201-202 | 2 | 4 | 4 | 1 | 2 | [6 empty] | 13 | 13 | 201.5 | 83.0336
202-203 |  | 1 | 2 | 3 | 2 | [6 empty] | 8 | 8 | 202.5 | 87.7608
203-204 |  | 1 | 2 | 2 | [7 empty] | 5 | 5 | 203.5 | 92.4614
204-205 | 2 | 4 | 1 | [8 empty] | 7 | 7 | 204.5 | 97.1337
205-206 |  |  | 1 | 4 | [7 empty] | 5 | 5 | 205.5 | 101.7765
206-207 |  | 5 | 2 | 1 | 2 | [6 empty] | 10 | 10 | 206.5 | 106.3883
207-208 | 1 | 3 | 4 | 1 | [7 empty] | 9 | 9 | 207.5 | 110.9676
208-209 | 2 | 1 | 5 | [8 empty] | 8 | 8 | 208.5 | 115.5132
209-210 |  |  | 3 | [8 empty] | 3 | 3 | 209.5 | 120.0236
210-211 |  | 4 | [9 empty] | 4 | 4 | 210.5 | 124.4974
211-212 | 1 |  |  | 2 | [7 empty] | 3 | 3 | 211.5 | 128.9333
212-213 |  | 2 | 2 | 1 | [7 empty] | 5 | 5 | 212.5 | 133.3299
213-214 |  | 2 | 1 | [8 empty] | 3 | 3 | 213.5 | 137.6859
214-215 |  | 1 | 2 | 1 | [7 empty] | 4 | 4 | 214.5 | 142
215-216 |  | 6 | 1 | 1 | [7 empty] | 8 | 8 | 215.5 | 146.2708
216-217 |  | 2 | 2 | 3 | [7 empty] | 7 | 7 | 216.5 | 150.4971
217-218 |  | 2 | [9 empty] | 2 | 2 | 217.5 | 154.6775
218-219 |  | 1 | [9 empty] | 1 | 1 | 218.5 | 158.8108
219-220 |  | 2 | [9 empty] | 2 | 2 | 219.5 | 162.8957
220-221 |  | 2 | [9 empty] | 2 | 2 | 220.5 | 166.931
221-222 |  | 2 | 2 | [8 empty] | 4 | 4 | 221.5 | 170.9155
222-223 |  | 1 | [9 empty] | 1 | 1 | 222.5 | 174.8479
223-224 |  | 1 | [9 empty] | 1 | 1 | 223.5 | 178.727
224-225 |  | 1 | [9 empty] | 1 | 1 | 224.5 | 182.5517
225-226 |  | 1 | [9 empty] | 1 | 1 | 225.5 | 186.3208
226-227 | 1 | 4 | [9 empty] | 5 | 5 | 226.5 | 190.0331
227-228 |  | 3 | 1 | [8 empty] | 4 | 4 | 227.5 | 193.6875
228-229 | 1 |  | 1 | [8 empty] | 2 | 2 | 228.5 | 197.283
229-230 | 1 | 1 | [9 empty] | 2 | 2 | 229.5 | 200.8183
230-231 | 1 | 4 | [9 empty] | 5 | 5 | 230.5 | 204.2925
231-232 | 1 | 3 | 2 | [8 empty] | 6 | 6 | 231.5 | 207.7045
232-233 |  | 1 | [9 empty] | 1 | 1 | 232.5 | 211.0531
234-235 |  | 2 | [9 empty] | 2 | 2 | 234.5 | 217.5566
235-236 | 1 | 2 | [9 empty] | 3 | 3 | 235.5 | 220.7095
236-237 | 1 | [10 empty] | 1 | 1 | 236.5 | 223.7951
237-238 |  | 1 | [9 empty] | 1 | 1 | 237.5 | 226.8125
240-241 |  | 1 | [9 empty] | 1 | 1 | 240.5 | 235.4467
242-243 | 3 | [10 empty] | 3 | 3 | 242.5 | 240.8457
243-244 | 1 | 1 | [9 empty] | 2 | 2 | 243.5 | 243.4355
247-248 |  | 1 | [9 empty] | 1 | 1 | 247.5 | 253.0459
251-252 |  | 2 | [9 empty] | 2 | 2 | 251.5 | 261.4234
252-253 |  | 1 | [9 empty] | 1 | 1 | 252.5 | 263.3202
253-254 |  | 1 | [9 empty] | 1 | 1 | 253.5 | 265.1368
255-256 |  | 2 | [9 empty] | 2 | 2 | 255.5 | 268.5273
257-258 |  | 1 | [9 empty] | 1 | 1 | 257.5 | 271.5906
258-259 | 1 | [10 empty] | 1 | 1 | 258.5 | 272.9983
260-261 | 1 | [10 empty] | 1 | 1 | 260.5 | 275.564
262-263 | 1 | [10 empty] | 1 | 1 | 262.5 | 277.7939
263-264 | 2 | [10 empty] | 2 | 2 | 263.5 | 278.7821
265-266 |  | 1 | [9 empty] | 1 | 1 | 265.5 | 280.5035
267-268 | 4 | 1 | [9 empty] | 5 | 5 | 267.5 | 281.8831
268-269 |  | 1 | [9 empty] | 1 | 1 | 268.5 | 282.4442
270-271 | 1 | 2 | [9 empty] | 3 | 3 | 270.5 | 283.3082
271-272 | 1 | [10 empty] | 1 | 1 | 271.5 | 283.6108
273-274 |  | 3 | [9 empty] | 3 | 3 | 273.5 | 283.9567
274-275 |  | 1 | [9 empty] | 1 | 1 | 274.5 | 284
276-277 | 1 | [10 empty] | 1 | 1 | 276.5 | 283.827
277-278 | 1 | [10 empty] | 1 | 1 | 277.5 | 283.6108
279-280 |  | 1 | [9 empty] | 1 | 1 | 279.5 | 282.9193
282-283 |  | 1 | [9 empty] | 1 | 1 | 282.5 | 281.2361
284-285 | 1 | [10 empty] | 1 | 1 | 284.5 | 279.6854
285-286 |  | 1 | [9 empty] | 1 | 1 | 285.5 | 278.7821
286-287 | 1 | [10 empty] | 1 | 1 | 286.5 | 277.7939
289-290 | 3 | [10 empty] | 3 | 3 | 289.5 | 274.3229
291-292 |  | 1 | [9 empty] | 1 | 1 | 291.5 | 271.5906
293-294 | 1 | [10 empty] | 1 | 1 | 293.5 | 268.5273
296-297 |  | 1 | [9 empty] | 1 | 1 | 296.5 | 263.3202
297-298 | 1 | [10 empty] | 1 | 1 | 297.5 | 261.4234
298-299 |  | 1 | [9 empty] | 1 | 1 | 298.5 | 259.4469
299-300 |  | 1 | [9 empty] | 1 | 1 | 299.5 | 257.3914
302-303 |  | 1 | [9 empty] | 1 | 1 | 302.5 | 250.7571
304-305 | 1 | [10 empty] | 1 | 1 | 304.5 | 245.9512
307-308 | 2 | 2 | [9 empty] | 4 | 4 | 307.5 | 238.1824
308-309 |  | 1 | [9 empty] | 1 | 1 | 308.5 | 235.4467
309-310 |  | 1 | [9 empty] | 1 | 1 | 309.5 | 232.6392
311-312 | 1 | [10 empty] | 1 | 1 | 311.5 | 226.8125
312-313 | 3 | 1 | [9 empty] | 4 | 4 | 312.5 | 223.7951
313-314 |  | 1 | [9 empty] | 1 | 1 | 313.5 | 220.7095
314-315 | 1 | 1 | [9 empty] | 2 | 2 | 314.5 | 217.5566
315-316 | 1 | 1 | [9 empty] | 2 | 2 | 315.5 | 214.3375
316-317 | 2 | 1 | [9 empty] | 3 | 3 | 316.5 | 211.0531
317-318 |  | 2 | [9 empty] | 2 | 2 | 317.5 | 207.7045
318-319 |  | 2 | [9 empty] | 2 | 2 | 318.5 | 204.2925
319-320 | 1 | [10 empty] | 1 | 1 | 319.5 | 200.8183
320-321 | 2 | [10 empty] | 2 | 2 | 320.5 | 197.283
322-323 |  | 1 | [9 empty] | 1 | 1 | 322.5 | 190.0331
324-325 |  | 2 | 1 | [8 empty] | 3 | 3 | 324.5 | 182.5517
325-326 | 4 | 2 | [9 empty] | 6 | 6 | 325.5 | 178.727
326-327 |  | 1 | [9 empty] | 1 | 1 | 326.5 | 174.8479
327-328 |  |  | 2 | [8 empty] | 2 | 2 | 327.5 | 170.9155
328-329 |  | 2 | [9 empty] | 2 | 2 | 328.5 | 166.931
329-330 | 1 | [10 empty] | 1 | 1 | 329.5 | 162.8957
330-331 | 2 | [10 empty] | 2 | 2 | 330.5 | 158.8108
331-332 |  | 1 | [9 empty] | 1 | 1 | 331.5 | 154.6775
332-333 | 1 | 1 | [9 empty] | 2 | 2 | 332.5 | 150.4971
333-334 |  | 2 | [9 empty] | 2 | 2 | 333.5 | 146.2708
334-335 | 1 | [10 empty] | 1 | 1 | 334.5 | 142
335-336 |  | 3 | [9 empty] | 3 | 3 | 335.5 | 137.6859
336-337 |  | 1 | [9 empty] | 1 | 1 | 336.5 | 133.3299
337-338 |  | 2 | [9 empty] | 2 | 2 | 337.5 | 128.9333
338-339 |  | 4 | [9 empty] | 4 | 4 | 338.5 | 124.4974
339-340 | 2 | 3 | [9 empty] | 5 | 5 | 339.5 | 120.0236
340-341 |  | 1 | [9 empty] | 1 | 1 | 340.5 | 115.5132
341-342 | 1 |  | 1 | [8 empty] | 2 | 2 | 341.5 | 110.9676
342-343 | 1 | 1 | 2 | 2 | [7 empty] | 6 | 6 | 342.5 | 106.3883
343-344 |  | 3 | 4 | [8 empty] | 7 | 7 | 343.5 | 101.7765
344-345 | 2 | 2 | 1 | [8 empty] | 5 | 5 | 344.5 | 97.1337
345-346 |  | 2 | 3 | 2 | [7 empty] | 7 | 7 | 345.5 | 92.4614
346-347 |  | 6 | 3 | 2 | [7 empty] | 11 | 11 | 346.5 | 87.7608
347-348 |  | 5 | 3 | 1 | [7 empty] | 9 | 9 | 347.5 | 83.0336
348-349 |  | 1 | 3 | 2 | 1 | [6 empty] | 7 | 7 | 348.5 | 78.281
349-350 |  | 1 | 3 | [8 empty] | 4 | 4 | 349.5 | 73.5046
350-351 | 1 |  | 4 | 1 | [7 empty] | 6 | 6 | 350.5 | 68.7058
351-352 |  | 2 | 6 | 5 | 1 | [6 empty] | 14 | 14 | 351.5 | 63.8861
352-353 | 2 | 1 | 2 | 2 | [7 empty] | 7 | 7 | 352.5 | 59.0469
353-354 |  | 2 | 6 | 5 | 1 | [6 empty] | 14 | 14 | 353.5 | 54.1898
354-355 |  | 1 | 2 | 2 | 2 | 3 | [5 empty] | 10 | 10 | 354.5 | 49.3161
355-356 |  | 2 | 9 | 6 |  |  | 1 |  |  |  |  | 18 | 18 | 355.5 | 44.4274
356-357 |  | 1 | 1 | 11 | 5 | 3 | 1 | 1 |  |  |  | 23 | 23 | 356.5 | 39.5252
357-358 |  | 4 | 3 | 4 | 6 | 7 | 2 |  |  |  |  | 26 | 26 | 357.5 | 34.6109
358-359 |  | 2 | 8 | 15 | 18 | 8 | 3 | 4 |  |  |  | 58 | 58 | 358.5 | 29.6861
359-360 |  | 1 | 7 | 6 | 10 | 6 | 8 | 4 |  |  |  | 42 | 42 | 359.5 | 24.7522
Grand Total | 175 | 436 | 391 | 484 | 707 | 661 | 569 | 544 | 299 | 48 | 6 | 4320
Grand Total | 175 | 436 | 391 | 484 | 707 | 661 | 569 | 544 | 299 | 48 | 6 | 4320
"weight" speed | 0 | 0.15 | 0.25 | 0.35 | 0.45 | 0.55 | 0.65 | 0.75 | 0.85 | 0.95 | 1.05
slack weight | 0: 175; 0.35: slack area; 0.45: 228.65; 0.55: ratio; 0.65: 4.051%
|  |  |  | slack speed (intake velocity) | 0.3
Inflow = area * weight speed * count
Direction | 0-0.1 | 0.1-0.2 | 0.2-0.3 | 0.3-0.4 | 0.4-0.5 | 0.5-0.6 | 0.6-0.7 | 0.7-0.8 | 0.8-0.9 | 0.9-1 | 1-1.1 | direction total
0-1 | 0 | 11.8865 | 19.8108 | 76.2717 | 80.2339 | 98.0637 | 154.5245 | 178.2975 | 50.5176 | 0 | 0 | 669.6063
1-2 | 0 | 2.2295 | 18.5793 | 36.4154 | 120.3936 | 106.2734 | 96.6122 | 167.2134 | 63.1695 | 0 | 0 | 610.8862
2-3 | 0 | 5.9469 | 0 | 45.0971 | 71.3625 | 54.513 | 64.4245 | 111.5039 | 143.2206 | 37.6635 | 0 | 533.732
3-4 | 0 | 0 | 7.4347 | 20.8172 | 37.9171 | 49.0692 | 57.9909 | 104.0862 | 84.2602 | 4.7087 | 0 | 366.2841
4-5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5-6 | 0 | 0.74347 | 6.1956 | 13.8782 | 17.8433 | 68.1516 | 83.7646 | 89.2167 | 80.0472 | 9.4173 | 5.2043 | 374.4623
6-7 | 0 | 0 | 12.3893 | 20.8141 | 111.5039 | 130.8312 | 167.5036 | 289.9101 | 193.769 | 84.743 | 0 | 1011.4642
7-8 | 0 | 2.2295 | 40.8744 | 31.2132 | 93.6395 | 171.6724 | 231.8692 | 479.345 | 341.1153 | 28.2405 | 0 | 1420.199
8-9 | 0 | 2.9716 | 14.8581 | 48.5366 | 151.5529 | 239.7111 | 360.5573 | 252.5882 | 252.5882 | 94.1015 | 41.6028 | 1459.0683
9-10 | 0 | 0 | 61.8806 | 51.9797 | 200.4931 | 217.8196 | 337.868 | 575.4894 | 378.7091 | 141.0877 | 51.9797 | 2017.3068
10-11 | 0 | 13.3587 | 22.2646 | 72.7309 | 160.3049 | 310.2196 | 443.8069 | 178.1165 | 479.4302 | 141.0089 | 0 | 1821.2412
11-12 | 0 | 10.3833 | 34.6109 | 218.0486 | 218.0486 | 228.4319 | 269.965 | 233.6235 | 264.7733 | 32.8803 | 0 | 1510.7655
12-13 | 0 | 11.8575 | 39.5252 | 166.0057 | 213.4359 | 239.1272 | 51.3827 | 29.6439 | 67.1928 | 0 | 0 | 818.1708
13-14 | 0 | 13.3282 | 33.3205 | 62.1983 | 179.9309 | 244.3506 | 259.9002 | 166.6027 | 264.343 | 42.206 | 0 | 1266.1806
14-15 | 0 | 29.5896 | 73.9741 | 207.1275 | 244.1146 | 271.2385 | 160.2773 | 258.9094 | 83.8373 | 0 | 0 | 1329.0684
15-16 | 0 | 0 | 54.1898 | 75.8657 | 146.3123 | 178.8262 | 105.67 | 40.6423 | 0 | 0 | 0 | 601.5063
16-17 | 0 | 26.5711 | 14.7617 | 103.3321 | 26.5711 | 162.379 | 38.3805 | 0 | 0 | 0 | 0 | 371.9956
17-18 | 0 | 47.9146 | 31.943 | 89.4405 | 373.7337 | 175.6868 | 0 | 0 | 0 | 0 | 0 | 718.7186
18-19 | 0 | 0 | 51.5294 | 192.3763 | 278.2586 | 302.3056 | 89.3176 | 0 | 0 | 0 | 0 | 913.7874
19-20 | 0 | 44.1028 | 55.1285 | 205.8129 | 66.1541 | 161.7101 | 0 | 0 | 0 | 0 | 0 | 532.9084
20-21 | 0 | 0 | 39.1405 | 109.5934 | 105.6794 | 0 | 0 | 0 | 0 | 0 | 0 | 254.4133
21-22 | 0 | 0 | 62.2752 | 87.1852 | 112.0953 | 0 | 0 | 0 | 0 | 0 | 0 | 261.5557
22-23 | 0 | 26.3282 | 65.8206 | 92.1489 | 197.4619 | 48.2685 | 0 | 0 | 0 | 0 | 0 | 430.028
23-24 | 0 | 41.6076 | 138.692 | 97.0844 | 124.8228 | 0 | 0 | 0 | 0 | 0 | 0 | 402.2069
24-25 | 0 | 29.1401 | 121.4172 | 101.9904 | 43.7102 | 0 | 0 | 0 | 0 | 0 | 0 | 296.2578
25-26 | 0 | 45.7994 | 25.4441 | 0 | 137.3983 | 0 | 0 | 0 | 0 | 0 | 0 | 208.6418
26-27 | 0 | 31.9165 | 26.5971 | 111.7077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170.2212
27-28 | 0 | 16.6451 | 138.7096 | 155.3547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.7094
28-29 | 0 | 0 | 28.8783 | 121.2889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150.1672
29-30 | 0 | 0 | 60.0118 | 168.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228.0448
30-31 | 0 | 37.3492 | 31.1244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.4736
31-32 | 0 | 0 | 32.2333 | 90.2533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.4866
32-33 | 0 | 39.999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.999
33-34 | 0 | 0 | 0 | 96.3802 | 61.9587 | 0 | 0 | 0 | 0 | 0 | 0 | 158.3388
34-35 | 0 | 63.9 | 0 | 49.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.6
35-36 | 0 | 65.8219 | 73.1354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138.9573
36-37 | 0 | 45.1491 | 75.2485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.3977
37-38 | 0 | 23.2016 | 38.6694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.871
38-39 | 0 | 47.6432 | 39.7027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.3459
39-40 | 0 | 24.4344 | 40.7239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.1583
40-41 | 0 | 25.0397 | 0 | 116.8517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141.8914
41-42 | 0 | 25.6373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.6373
42-43 | 0 | 52.4544 | 131.1359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183.5903
43-44 | 0 | 53.6181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6181
44-45 | 0 | 109.531 | 45.6379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155.1689
46-47 | 0 | 85.5149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.5149
47-48 | 0 | 116.2125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.2125
48-49 | 0 | 29.5924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.5924
49-50 | 0 | 90.3682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.3682
50-51 | 0 | 91.9316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.9316
51-52 | 0 | 93.467 | 51.9261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145.3931
52-53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54-55 | 0 | 32.6335 | 54.3892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.0226
55-56 | 0 | 0 | 110.3547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.3547
56-57 | 0 | 167.8463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167.8463
58-59 | 0 | 34.4641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.4641
59-60 | 0 | 34.8959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.8959
60-61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
63-64 | 0 | 73.0307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.0307
64-65 | 0 | 73.7854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.7854
66-67 | 0 | 37.6136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.6136
67-68 | 0 | 37.9569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.9569
69-70 | 0 | 38.6087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.6087
71-72 | 0 | 39.2135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.2135
72-73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73-74 | 0 | 39.7705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.7705
75-76 | 0 | 40.2791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.2791
77-78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78-79 | 0 | 81.8995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.8995
79-80 | 0 | 41.1484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.1484
80-81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
81-82 | 0 | 83.0163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.0163
82-83 | 0 | 41.6691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.6691
83-84 | 0 | 41.8173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.8173
84-85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
87-88 | 0 | 42.2825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2825
89-90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90-91 | 0 | 42.4962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.4962
91-92 | 0 | 42.5416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.5416
92-93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95-96 | 0 | 42.5935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.5935
99-100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102-103 | 0 | 42.1854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1854
103-104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104-105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
105-106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
107-108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108-109 | 0 | 82.6692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.6692
109-110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110-111 | 0 | 40.9497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.9497
111-112 | 0 | 81.4772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.4772
113-114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
114-115 | 0 | 40.0309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.0309
115-116 | 0 | 39.7705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.7705
117-118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
118-119 | 0 | 0 | 64.8617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.8617
119-120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
122-123 | 0 | 37.6136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.6136
123-124 | 0 | 74.5176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.5176
125-126 | 0 | 36.5153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.5153
126-127 | 0 | 36.1268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.1268
127-128 | 0 | 71.4547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.4547
128-129 | 0 | 35.317 | 117.7233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153.0403
129-130 | 0 | 0 | 58.1598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.1598
132-133 | 0 | 67.1385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.1385
133-134 | 0 | 33.1064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.1064
134-135 | 0 | 65.267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.267
135-136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
137-138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
138-139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
139-140 | 0 | 60.2455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.2455
141-142 | 0 | 0 | 48.4219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.4219
143-144 | 0 | 55.8962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.8962
144-145 | 0 | 27.3828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.3828
145-146 | 0 | 26.809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.809
147-148 | 0 | 25.6373 | 85.4577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.0951
148-149 | 0 | 50.0793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.0793
149-150 | 0 | 48.8687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.8687
150-151 | 0 | 47.6432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.6432
151-152 | 0 | 69.6049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.6049
152-153 | 0 | 0 | 188.1213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188.1213
153-154 | 0 | 175.525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175.525
154-155 | 0 | 42.6 | 71 | 99.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 213
155-156 | 0 | 20.6529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.6529
156-157 | 0 | 59.9985 | 33.3325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.3309
157-158 | 0 | 0 | 32.2333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.2333
158-159 | 0 | 74.6984 | 31.1244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.8228
159-160 | 0 | 72.0142 | 30.0059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.02
160-161 | 0 | 69.3079 | 28.8783 | 80.8592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179.0455
161-162 | 0 | 66.5806 | 83.2257 | 38.8387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188.645
162-163 | 0 | 79.7912 | 79.7912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159.5824
163-164 | 0 | 30.5329 | 76.3324 | 35.6218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142.4871
164-165 | 0 | 14.5701 | 24.2834 | 101.9904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140.8439
165-166 | 0 | 55.4768 | 138.692 | 0 | 0 | 50.8537 | 0 | 0 | 0 | 0 | 0 | 245.0226
166-167 | 0 | 26.3282 | 21.9402 | 92.1489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140.4173
167-168 | 0 | 49.8201 | 41.5168 | 29.0617 | 74.7302 | 0 | 0 | 0 | 0 | 0 | 0 | 195.1289
168-169 | 0 | 70.4529 | 19.5703 | 27.3984 | 140.9058 | 0 | 0 | 0 | 0 | 0 | 0 | 258.3273
169-170 | 0 | 11.0257 | 73.5046 | 25.7266 | 165.3854 | 0 | 0 | 0 | 0 | 0 | 0 | 275.6423
170-171 | 0 | 51.5294 | 68.7058 | 72.1411 | 185.5057 | 264.5174 | 0 | 0 | 0 | 0 | 0 | 642.3994
171-172 | 0 | 0 | 95.8291 | 67.0804 | 172.4925 | 0 | 0 | 95.8291 | 0 | 0 | 0 | 431.2312
172-173 | 0 | 8.857 | 118.0938 | 206.6642 | 132.8556 | 97.4274 | 76.761 | 44.2852 | 0 | 0 | 0 | 684.9443
173-174 | 0 | 8.1285 | 27.0949 | 132.7649 | 121.9269 | 119.2175 | 35.2233 | 40.6423 | 0 | 0 | 0 | 484.9983
174-175 | 0 | 7.3974 | 73.9741 | 86.3031 | 133.1534 | 54.2477 | 128.2218 | 110.9612 | 0 | 0 | 0 | 594.2588
175-176 | 0 | 13.3282 | 44.4274 | 15.5496 | 379.8542 | 439.8311 | 173.2668 | 199.9232 | 37.7633 | 0 | 0 | 1303.9438
176-177 | 0 | 11.8575 | 49.4065 | 83.0028 | 213.4359 | 195.6495 | 308.2963 | 207.5071 | 100.7892 | 0 | 0 | 1169.9448
177-178 | 0 | 5.1916 | 34.6109 | 72.6829 | 140.1741 | 361.6838 | 314.9591 | 467.2471 | 29.4193 | 0 | 0 | 1425.9688
178-179 | 0 | 8.9058 | 14.843 | 124.6816 | 267.1748 | 310.2196 | 270.1434 | 289.4393 | 50.4663 | 0 | 0 | 1335.8738
179-180 | 0 | 3.7128 | 24.7522 | 60.643 | 144.8006 | 367.5706 | 305.6901 | 371.2835 | 210.394 | 0 | 0 | 1488.8467
180-181 | 0 | 8.9149 | 24.7635 | 83.2055 | 205.0422 | 261.5031 | 412.0654 | 371.4532 | 235.749 | 18.8203 | 0 | 1621.5171
181-182 | 0 | 2.2295 | 33.4427 | 36.4154 | 140.4592 | 179.8473 | 270.5141 | 245.2463 | 101.0712 | 14.1202 | 0 | 1023.3459
182-183 | 0 | 4.4602 | 4.9557 | 20.8141 | 71.3625 | 174.4416 | 199.7159 | 185.8398 | 210.6185 | 0 | 0 | 872.2082
183-184 | 0 | 0 | 4.9565 | 19.0825 | 55.7604 | 95.4123 | 96.6514 | 111.5209 | 46.3431 | 23.5433 | 0 | 453.2704
184-185 | 0 | 5.2191e-15 | 5.2191e-14 | 4.8712e-14 | 3.1315e-13 | 4.0187e-13 | 6.1064e-13 | 3.9143e-13 | 1.7745e-13 | 0 | 0 | 2.0007e-12
185-186 | 0 | 3.7174 | 2.4782 | 6.9391 | 46.8388 | 87.2341 | 77.3211 | 59.4778 | 12.639 | 0 | 0 | 296.6455
186-187 | 0 | 2.9734 | 4.9557 | 17.345 | 66.9023 | 103.5747 | 115.964 | 74.3359 | 33.699 | 0 | 0 | 419.7502
187-188 | 0 | 2.2295 | 7.4317 | 52.0219 | 247.4758 | 98.0985 | 125.5958 | 211.8036 | 37.9017 | 28.2405 | 0 | 810.7991
188-189 | 0 | 2.9716 | 9.9054 | 34.669 | 124.8083 | 152.5435 | 115.8934 | 59.4325 | 16.8392 | 0 | 0 | 517.0629
189-190 | 0 | 7.4257 | 18.5642 | 43.3164 | 122.5235 | 149.751 | 64.3558 | 92.8209 | 0 | 0 | 0 | 498.7575
190-191 | 0 | 8.9058 | 37.1076 | 41.5605 | 146.9461 | 228.5828 | 115.7757 | 22.2646 | 25.2332 | 0 | 0 | 626.3764
191-192 | 0 | 15.5749 | 8.6527 | 36.3414 | 264.7733 | 133.2519 | 44.9942 | 25.9582 | 0 | 0 | 0 | 529.5467
192-193 | 0 | 0 | 0 | 55.3352 | 142.2906 | 282.6049 | 77.0741 | 0 | 0 | 0 | 0 | 557.3048
193-194 | 0 | 0 | 22.2137 | 139.9463 | 119.9539 | 48.8701 | 28.8778 | 66.6411 | 0 | 0 | 0 | 426.5029
194-195 | 0 | 7.3974 | 61.6451 | 120.8244 | 110.9612 | 54.2477 | 96.1664 | 0 | 0 | 0 | 0 | 451.2422
195-196 | 0 | 8.1285 | 40.6423 | 37.9328 | 146.3123 | 29.8044 | 0 | 0 | 0 | 0 | 0 | 262.8203
196-197 | 0 | 8.857 | 14.7617 | 82.6657 | 265.7111 | 0 | 0 | 0 | 0 | 0 | 0 | 371.9956
197-198 | 0 | 0 | 47.9146 | 67.0804 | 86.2462 | 0 | 0 | 0 | 0 | 0 | 0 | 201.2412
198-199 | 0 | 0 | 17.1765 | 72.1411 | 61.8352 | 0 | 0 | 0 | 0 | 0 | 0 | 151.1528
199-200 | 0 | 22.0514 | 18.3762 | 51.4532 | 99.2312 | 0 | 0 | 0 | 0 | 0 | 0 | 191.112
200-201 | 0 | 11.7422 | 39.1405 | 191.7885 | 140.9058 | 43.0546 | 0 | 0 | 0 | 0 | 0 | 426.6315
201-202 | 0 | 49.8201 | 83.0336 | 29.0617 | 74.7302 | 0 | 0 | 0 | 0 | 0 | 0 | 236.6457
202-203 | 0 | 13.1641 | 43.8804 | 92.1489 | 78.9847 | 0 | 0 | 0 | 0 | 0 | 0 | 228.1781
203-204 | 0 | 13.8692 | 46.2307 | 64.7229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124.8228
204-205 | 0 | 58.2802 | 24.2834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.5637
205-206 | 0 | 0 | 25.4441 | 142.4871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167.9312
206-207 | 0 | 79.7912 | 53.1941 | 37.2359 | 95.7494 | 0 | 0 | 0 | 0 | 0 | 0 | 265.9707
207-208 | 0 | 49.9354 | 110.9676 | 38.8387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199.7418
208-209 | 0 | 17.327 | 144.3915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161.7185
209-210 | 0 | 0 | 90.0177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.0177
210-211 | 0 | 74.6984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6984
211-212 | 0 | 0 | 0 | 90.2533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.2533
212-213 | 0 | 39.999 | 66.665 | 46.6655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153.3294
213-214 | 0 | 41.3058 | 34.4215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.7273
214-215 | 0 | 21.3 | 71 | 49.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142
215-216 | 0 | 131.6437 | 36.5677 | 51.1948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.4062
216-217 | 0 | 45.1491 | 75.2485 | 158.0219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278.4196
217-218 | 0 | 46.4032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.4032
218-219 | 0 | 23.8216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.8216
219-220 | 0 | 48.8687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.8687
220-221 | 0 | 50.0793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.0793
221-222 | 0 | 51.2746 | 85.4577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136.7324
222-223 | 0 | 26.2272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.2272
223-224 | 0 | 26.809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.809
224-225 | 0 | 27.3828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.3828
225-226 | 0 | 27.9481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9481
226-227 | 0 | 114.0199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.0199
227-228 | 0 | 87.1594 | 48.4219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135.5813
228-229 | 0 | 0 | 49.3207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.3207
229-230 | 0 | 30.1227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.1227
230-231 | 0 | 122.5755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.5755
231-232 | 0 | 93.467 | 103.8522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197.3192
232-233 | 0 | 31.658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.658
234-235 | 0 | 65.267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.267
235-236 | 0 | 66.2128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.2128
236-237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
237-238 | 0 | 34.0219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.0219
240-241 | 0 | 35.317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.317
242-243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
243-244 | 0 | 36.5153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.5153
247-248 | 0 | 37.9569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.9569
251-252 | 0 | 78.427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.427
252-253 | 0 | 39.498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.498
253-254 | 0 | 39.7705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.7705
255-256 | 0 | 80.5582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.5582
257-258 | 0 | 40.7386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.7386
258-259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
260-261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
262-263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
263-264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
265-266 | 0 | 42.0755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.0755
267-268 | 0 | 42.2825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2825
268-269 | 0 | 42.3666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.3666
270-271 | 0 | 84.9925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.9925
271-272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
273-274 | 0 | 127.7805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.7805
274-275 | 0 | 42.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.6
276-277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
277-278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
279-280 | 0 | 42.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.4379
282-283 | 0 | 42.1854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1854
284-285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
285-286 | 0 | 41.8173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.8173
286-287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
289-290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
291-292 | 0 | 40.7386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.7386
293-294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
296-297 | 0 | 39.498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.498
297-298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
298-299 | 0 | 38.917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.917
299-300 | 0 | 38.6087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.6087
302-303 | 0 | 37.6136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.6136
304-305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
307-308 | 0 | 71.4547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.4547
308-309 | 0 | 35.317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.317
309-310 | 0 | 34.8959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.8959
311-312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
312-313 | 0 | 33.5693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.5693
313-314 | 0 | 33.1064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.1064
314-315 | 0 | 32.6335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.6335
315-316 | 0 | 32.1506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.1506
316-317 | 0 | 31.658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.658
317-318 | 0 | 62.3113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.3113
318-319 | 0 | 61.2878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.2878
319-320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
320-321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
322-323 | 0 | 28.505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.505
324-325 | 0 | 54.7655 | 45.6379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.4034
325-326 | 0 | 53.6181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6181
326-327 | 0 | 26.2272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.2272
327-328 | 0 | 0 | 85.4577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.4577
328-329 | 0 | 50.0793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.0793
329-330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
330-331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
331-332 | 0 | 23.2016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.2016
332-333 | 0 | 22.5746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.5746
333-334 | 0 | 43.8812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8812
334-335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
335-336 | 0 | 61.9587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9587
336-337 | 0 | 19.9995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.9995
337-338 | 0 | 38.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.68
338-339 | 0 | 74.6984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6984
339-340 | 0 | 54.0106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.0106
340-341 | 0 | 17.327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.327
341-342 | 0 | 0 | 27.7419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.7419
342-343 | 0 | 15.9582 | 53.1941 | 74.4718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143.6242
343-344 | 0 | 45.7994 | 101.7765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147.5759
344-345 | 0 | 29.1401 | 24.2834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.4235
345-346 | 0 | 27.7384 | 69.346 | 64.7229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161.8074
346-347 | 0 | 78.9847 | 65.8206 | 61.4326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206.2379
347-348 | 0 | 62.2752 | 62.2752 | 29.0617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153.6121
348-349 | 0 | 11.7422 | 58.7108 | 54.7967 | 35.2265 | 0 | 0 | 0 | 0 | 0 | 0 | 160.4761
349-350 | 0 | 11.0257 | 55.1285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.1541
350-351 | 0 | 0 | 68.7058 | 24.047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.7529
351-352 | 0 | 19.1658 | 95.8291 | 111.8007 | 28.7487 | 0 | 0 | 0 | 0 | 0 | 0 | 255.5444
352-353 | 0 | 8.857 | 29.5235 | 41.3328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.7133
353-354 | 0 | 16.2569 | 81.2846 | 94.8321 | 24.3854 | 0 | 0 | 0 | 0 | 0 | 0 | 216.759
354-355 | 0 | 7.3974 | 24.658 | 34.5213 | 44.3845 | 81.3715 | 0 | 0 | 0 | 0 | 0 | 192.3327
355-356 | 0 | 13.3282 | 99.9616 | 93.2975 | 0 | 0 | 28.8778 | 0 | 0 | 0 | 0 | 235.4652
356-357 | 0 | 5.9288 | 9.8813 | 152.1719 | 88.9316 | 65.2165 | 25.6914 | 29.6439 | 0 | 0 | 0 | 377.4653
357-358 | 0 | 20.7665 | 25.9582 | 48.4553 | 93.4494 | 133.2519 | 44.9942 | 0 | 0 | 0 | 0 | 366.8755
358-359 | 0 | 8.9058 | 59.3722 | 155.8519 | 240.4573 | 130.6188 | 57.8879 | 89.0583 | 0 | 0 | 0 | 742.1521
359-360 | 0 | 3.7128 | 43.3164 | 51.9797 | 111.385 | 81.6824 | 128.7116 | 74.2567 | 0 | 0 | 0 | 495.0446
draw excl slacks | 59376.181 |  |  |  | 1.5 | 2.5 | 3.5 | 4.5 | 5.5 | 6.5 | 7.5
slacks | 12004.125 |  |  |  | 36.97 | 35.03 | 33.73 | 33.19 | 33.27 | 33.96 | 35.31
total draw | 0: 71380.306
divisor | 0: 2150.65
Average | 0: 33.1901; 0.15: m2

## northern slk 0.2
SZC northern slk 0.2 |  |  | SZC intake alignment: |  |  | 4.5
Count of Direction at 2.04m above bed (deg) | Column Labels | [13 empty] | 284
Row Labels | 0-0.1 | 0.1-0.2 | 0.2-0.3 | 0.3-0.4 | 0.4-0.5 | 0.5-0.6 | 0.6-0.7 | 0.7-0.8 | 0.8-0.9 | 0.9-1 | 1-1.1 | Grand Total |  | mid bin | area m2
0-1 | 3 | 4 | 4 | 11 | 9 | 9 | 12 | 12 | 3 |  |  | 67 | 67 | 0.5 | 19.8108
1-2 |  | 1 | 5 | 7 | 18 | 13 | 10 | 15 | 5 |  |  | 74 | 74 | 1.5 | 14.8634
2-3 | 1 | 4 |  | 13 | 16 | 10 | 10 | 15 | 17 | 4 |  | 90 | 90 | 2.5 | 9.9115
3-4 | 2 |  | 6 | 12 | 17 | 18 | 18 | 28 | 20 | 1 |  | 122 | 122 | 3.5 | 4.9565
4-5 |  | 3 | 2 | 11 | 17 | 14 | 19 | 34 | 20 | 3 | 1 | 124 | 124 | 4.5 | 0
5-6 | 1 | 1 | 5 | 8 | 8 | 25 | 26 | 24 | 19 | 2 | 1 | 120 | 120 | 5.5 | 4.9565
6-7 |  |  | 5 | 6 | 25 | 24 | 26 | 39 | 23 | 9 |  | 157 | 157 | 6.5 | 9.9115
7-8 |  | 1 | 11 | 6 | 14 | 21 | 24 | 43 | 27 | 2 |  | 149 | 149 | 7.5 | 14.8634
8-9 | 1 | 1 | 3 | 7 | 17 | 22 | 28 | 17 | 15 | 5 | 2 | 118 | 118 | 8.5 | 19.8108
9-10 | 1 |  | 10 | 6 | 18 | 16 | 21 | 31 | 18 | 6 | 2 | 129 | 129 | 9.5 | 24.7522
10-11 |  | 3 | 3 | 7 | 12 | 19 | 23 | 8 | 19 | 5 |  | 99 | 99 | 10.5 | 29.6861
11-12 |  | 2 | 4 | 18 | 14 | 12 | 12 | 9 | 9 | 1 |  | 81 | 81 | 11.5 | 34.6109
12-13 |  | 2 | 4 | 12 | 12 | 11 | 2 | 1 | 2 |  |  | 46 | 46 | 12.5 | 39.5252
13-14 | 1 | 2 | 3 | 4 | 9 | 10 | 9 | 5 | 7 | 1 |  | 51 | 51 | 13.5 | 44.4274
14-15 |  | 4 | 6 | 12 | 11 | 10 | 5 | 7 | 2 |  |  | 57 | 57 | 14.5 | 49.3161
15-16 |  |  | 4 | 4 | 6 | 6 | 3 | 1 |  |  |  | 24 | 24 | 15.5 | 54.1898
16-17 | 2 | 3 | 1 | 5 | 1 | 5 | 1 |  |  |  |  | 18 | 18 | 16.5 | 59.0469
17-18 |  | 5 | 2 | 4 | 13 | 5 | [5 empty] | 29 | 29 | 17.5 | 63.8861
18-19 | 2 |  | 3 | 8 | 9 | 8 | 2 |  |  |  |  | 32 | 32 | 18.5 | 68.7058
19-20 |  | 4 | 3 | 8 | 2 | 4 | [5 empty] | 21 | 21 | 19.5 | 73.5046
20-21 |  |  | 2 | 4 | 3 | [6 empty] | 9 | 9 | 20.5 | 78.281
21-22 |  |  | 3 | 3 | 3 | [6 empty] | 9 | 9 | 21.5 | 83.0336
22-23 | 1 | 2 | 3 | 3 | 5 | 1 | [5 empty] | 15 | 15 | 22.5 | 87.7608
23-24 | 1 | 3 | 6 | 3 | 3 | [6 empty] | 16 | 16 | 23.5 | 92.4614
24-25 |  | 2 | 5 | 3 | 1 | [6 empty] | 11 | 11 | 24.5 | 97.1337
25-26 |  | 3 | 1 |  | 3 | [6 empty] | 7 | 7 | 25.5 | 101.7765
26-27 | 3 | 2 | 1 | 3 | [7 empty] | 9 | 9 | 26.5 | 106.3883
27-28 | 1 | 1 | 5 | 4 | [7 empty] | 11 | 11 | 27.5 | 110.9676
28-29 |  |  | 1 | 3 | [7 empty] | 4 | 4 | 28.5 | 115.5132
29-30 |  |  | 2 | 4 | [7 empty] | 6 | 6 | 29.5 | 120.0236
30-31 |  | 2 | 1 | [8 empty] | 3 | 3 | 30.5 | 124.4974
31-32 |  |  | 1 | 2 | [7 empty] | 3 | 3 | 31.5 | 128.9333
32-33 |  | 2 | [9 empty] | 2 | 2 | 32.5 | 133.3299
33-34 |  |  |  | 2 | 1 | [6 empty] | 3 | 3 | 33.5 | 137.6859
34-35 |  | 3 |  | 1 | [7 empty] | 4 | 4 | 34.5 | 142
35-36 |  | 3 | 2 | [8 empty] | 5 | 5 | 35.5 | 146.2708
36-37 | 3 | 2 | 2 | [8 empty] | 7 | 7 | 36.5 | 150.4971
37-38 | 1 | 1 | 1 | [8 empty] | 3 | 3 | 37.5 | 154.6775
38-39 |  | 2 | 1 | [8 empty] | 3 | 3 | 38.5 | 158.8108
39-40 |  | 1 | 1 | [8 empty] | 2 | 2 | 39.5 | 162.8957
40-41 | 3 | 1 |  | 2 | [7 empty] | 6 | 6 | 40.5 | 166.931
41-42 | 1 | 1 | [9 empty] | 2 | 2 | 41.5 | 170.9155
42-43 | 3 | 2 | 3 | [8 empty] | 8 | 8 | 42.5 | 174.8479
43-44 | 1 | 2 | [9 empty] | 3 | 3 | 43.5 | 178.727
44-45 |  | 4 | 1 | [8 empty] | 5 | 5 | 44.5 | 182.5517
46-47 |  | 3 | [9 empty] | 3 | 3 | 46.5 | 190.0331
47-48 |  | 4 | [9 empty] | 4 | 4 | 47.5 | 193.6875
48-49 |  | 1 | [9 empty] | 1 | 1 | 48.5 | 197.283
49-50 | 1 | 3 | [9 empty] | 4 | 4 | 49.5 | 200.8183
50-51 |  | 3 | [9 empty] | 3 | 3 | 50.5 | 204.2925
51-52 |  | 3 | 1 | [8 empty] | 4 | 4 | 51.5 | 207.7045
52-53 | 4 | [10 empty] | 4 | 4 | 52.5 | 211.0531
54-55 |  | 1 | 1 | [8 empty] | 2 | 2 | 54.5 | 217.5566
55-56 | 1 |  | 2 | [8 empty] | 3 | 3 | 55.5 | 220.7095
56-57 |  | 5 | [9 empty] | 5 | 5 | 56.5 | 223.7951
58-59 |  | 1 | [9 empty] | 1 | 1 | 58.5 | 229.7608
59-60 |  | 1 | [9 empty] | 1 | 1 | 59.5 | 232.6392
60-61 | 1 | [10 empty] | 1 | 1 | 60.5 | 235.4467
63-64 |  | 2 | [9 empty] | 2 | 2 | 63.5 | 243.4355
64-65 |  | 2 | [9 empty] | 2 | 2 | 64.5 | 245.9512
66-67 |  | 1 | [9 empty] | 1 | 1 | 66.5 | 250.7571
67-68 | 1 | 1 | [9 empty] | 2 | 2 | 67.5 | 253.0459
69-70 | 1 | 1 | [9 empty] | 2 | 2 | 69.5 | 257.3914
71-72 |  | 1 | [9 empty] | 1 | 1 | 71.5 | 261.4234
72-73 | 2 | [10 empty] | 2 | 2 | 72.5 | 263.3202
73-74 |  | 1 | [9 empty] | 1 | 1 | 73.5 | 265.1368
75-76 |  | 1 | [9 empty] | 1 | 1 | 75.5 | 268.5273
77-78 | 1 | [10 empty] | 1 | 1 | 77.5 | 271.5906
78-79 | 1 | 2 | [9 empty] | 3 | 3 | 78.5 | 272.9983
79-80 | 1 | 1 | [9 empty] | 2 | 2 | 79.5 | 274.3229
80-81 | 2 | [10 empty] | 2 | 2 | 80.5 | 275.564
81-82 |  | 2 | [9 empty] | 2 | 2 | 81.5 | 276.7211
82-83 |  | 1 | [9 empty] | 1 | 1 | 82.5 | 277.7939
83-84 |  | 1 | [9 empty] | 1 | 1 | 83.5 | 278.7821
84-85 | 1 | [10 empty] | 1 | 1 | 84.5 | 279.6854
87-88 |  | 1 | [9 empty] | 1 | 1 | 87.5 | 281.8831
89-90 | 1 | [10 empty] | 1 | 1 | 89.5 | 282.9193
90-91 | 3 | 1 | [9 empty] | 4 | 4 | 90.5 | 283.3082
91-92 |  | 1 | [9 empty] | 1 | 1 | 91.5 | 283.6108
92-93 | 2 | [10 empty] | 2 | 2 | 92.5 | 283.827
95-96 |  | 1 | [9 empty] | 1 | 1 | 95.5 | 283.9567
99-100 | 2 | [10 empty] | 2 | 2 | 99.5 | 282.9193
101-102 | 1 | [10 empty] | 1 | 1 | 101.5 | 281.8831
102-103 |  | 1 | [9 empty] | 1 | 1 | 102.5 | 281.2361
103-104 | 1 | [10 empty] | 1 | 1 | 103.5 | 280.5035
104-105 | 2 | [10 empty] | 2 | 2 | 104.5 | 279.6854
105-106 | 1 | [10 empty] | 1 | 1 | 105.5 | 278.7821
107-108 | 1 | [10 empty] | 1 | 1 | 107.5 | 276.7211
108-109 | 1 | 2 | [9 empty] | 3 | 3 | 108.5 | 275.564
109-110 | 2 | [10 empty] | 2 | 2 | 109.5 | 274.3229
110-111 |  | 1 | [9 empty] | 1 | 1 | 110.5 | 272.9983
111-112 |  | 2 | [9 empty] | 2 | 2 | 111.5 | 271.5906
113-114 | 1 | [10 empty] | 1 | 1 | 113.5 | 268.5273
114-115 |  | 1 | [9 empty] | 1 | 1 | 114.5 | 266.8727
115-116 |  | 1 | [9 empty] | 1 | 1 | 115.5 | 265.1368
117-118 | 1 | [10 empty] | 1 | 1 | 117.5 | 261.4234
118-119 |  |  | 1 | [8 empty] | 1 | 1 | 118.5 | 259.4469
119-120 | 3 | [10 empty] | 3 | 3 | 119.5 | 257.3914
122-123 | 2 | 1 | [9 empty] | 3 | 3 | 122.5 | 250.7571
123-124 |  | 2 | [9 empty] | 2 | 2 | 123.5 | 248.392
125-126 |  | 1 | [9 empty] | 1 | 1 | 125.5 | 243.4355
126-127 |  | 1 | [9 empty] | 1 | 1 | 126.5 | 240.8457
127-128 |  | 2 | [9 empty] | 2 | 2 | 127.5 | 238.1824
128-129 |  | 1 | 2 | [8 empty] | 3 | 3 | 128.5 | 235.4467
129-130 |  |  | 1 | [8 empty] | 1 | 1 | 129.5 | 232.6392
132-133 |  | 2 | [9 empty] | 2 | 2 | 132.5 | 223.7951
133-134 |  | 1 | [9 empty] | 1 | 1 | 133.5 | 220.7095
134-135 |  | 2 | [9 empty] | 2 | 2 | 134.5 | 217.5566
135-136 | 2 | [10 empty] | 2 | 2 | 135.5 | 214.3375
137-138 | 1 | [10 empty] | 1 | 1 | 137.5 | 207.7045
138-139 | 2 | [10 empty] | 2 | 2 | 138.5 | 204.2925
139-140 |  | 2 | [9 empty] | 2 | 2 | 139.5 | 200.8183
141-142 |  |  | 1 | [8 empty] | 1 | 1 | 141.5 | 193.6875
143-144 |  | 2 | [9 empty] | 2 | 2 | 143.5 | 186.3208
144-145 | 2 | 1 | [9 empty] | 3 | 3 | 144.5 | 182.5517
145-146 |  | 1 | [9 empty] | 1 | 1 | 145.5 | 178.727
147-148 | 2 | 1 | 2 | [8 empty] | 5 | 5 | 147.5 | 170.9155
148-149 |  | 2 | [9 empty] | 2 | 2 | 148.5 | 166.931
149-150 |  | 2 | [9 empty] | 2 | 2 | 149.5 | 162.8957
150-151 | 2 | 2 | [9 empty] | 4 | 4 | 150.5 | 158.8108
151-152 |  | 3 | [9 empty] | 3 | 3 | 151.5 | 154.6775
152-153 |  |  | 5 | [8 empty] | 5 | 5 | 152.5 | 150.4971
153-154 | 2 | 8 | [9 empty] | 10 | 10 | 153.5 | 146.2708
154-155 | 1 | 2 | 2 | 2 | [7 empty] | 7 | 7 | 154.5 | 142
155-156 |  | 1 | [9 empty] | 1 | 1 | 155.5 | 137.6859
156-157 |  | 3 | 1 | [8 empty] | 4 | 4 | 156.5 | 133.3299
157-158 |  |  | 1 | [8 empty] | 1 | 1 | 157.5 | 128.9333
158-159 |  | 4 | 1 | [8 empty] | 5 | 5 | 158.5 | 124.4974
159-160 |  | 4 | 1 | [8 empty] | 5 | 5 | 159.5 | 120.0236
160-161 | 1 | 4 | 1 | 2 | [7 empty] | 8 | 8 | 160.5 | 115.5132
161-162 | 1 | 4 | 3 | 1 | [7 empty] | 9 | 9 | 161.5 | 110.9676
162-163 |  | 5 | 3 | [8 empty] | 8 | 8 | 162.5 | 106.3883
163-164 | 2 | 2 | 3 | 1 | [7 empty] | 8 | 8 | 163.5 | 101.7765
164-165 | 1 | 1 | 1 | 3 | [7 empty] | 6 | 6 | 164.5 | 97.1337
165-166 |  | 4 | 6 |  |  | 1 | [5 empty] | 11 | 11 | 165.5 | 92.4614
166-167 |  | 2 | 1 | 3 | [7 empty] | 6 | 6 | 166.5 | 87.7608
167-168 | 2 | 4 | 2 | 1 | 2 | [6 empty] | 11 | 11 | 167.5 | 83.0336
168-169 |  | 6 | 1 | 1 | 4 | [6 empty] | 12 | 12 | 168.5 | 78.281
169-170 |  | 1 | 4 | 1 | 5 | [6 empty] | 11 | 11 | 169.5 | 73.5046
170-171 | 1 | 5 | 4 | 3 | 6 | 7 | [5 empty] | 26 | 26 | 170.5 | 68.7058
171-172 |  |  | 6 | 3 | 6 |  |  | 2 |  |  |  | 17 | 17 | 171.5 | 63.8861
172-173 | 1 | 1 | 8 | 10 | 5 | 3 | 2 | 1 |  |  |  | 31 | 31 | 172.5 | 59.0469
173-174 |  | 1 | 2 | 7 | 5 | 4 | 1 | 1 |  |  |  | 21 | 21 | 173.5 | 54.1898
174-175 |  | 1 | 6 | 5 | 6 | 2 | 4 | 3 |  |  |  | 27 | 27 | 174.5 | 49.3161
175-176 |  | 2 | 4 | 1 | 19 | 18 | 6 | 6 | 1 |  |  | 57 | 57 | 175.5 | 44.4274
176-177 |  | 2 | 5 | 6 | 12 | 9 | 12 | 7 | 3 |  |  | 56 | 56 | 176.5 | 39.5252
177-178 |  | 1 | 4 | 6 | 9 | 19 | 14 | 18 | 1 |  |  | 72 | 72 | 177.5 | 34.6109
178-179 |  | 2 | 2 | 12 | 20 | 19 | 14 | 13 | 2 |  |  | 84 | 84 | 178.5 | 29.6861
179-180 |  | 1 | 4 | 7 | 13 | 27 | 19 | 20 | 10 |  |  | 101 | 101 | 179.5 | 24.7522
180-181 | 1 | 3 | 5 | 12 | 23 | 24 | 32 | 25 | 14 | 1 |  | 140 | 140 | 180.5 | 19.8108
181-182 | 1 | 1 | 9 | 7 | 21 | 22 | 28 | 22 | 8 | 1 |  | 120 | 120 | 181.5 | 14.8634
182-183 |  | 3 | 2 | 6 | 16 | 32 | 31 | 25 | 25 |  |  | 140 | 140 | 182.5 | 9.9115
183-184 |  |  | 4 | 11 | 25 | 35 | 30 | 30 | 11 | 5 |  | 151 | 151 | 183.5 | 4.9565
184-185 |  | 1 | 6 | 4 | 20 | 21 | 27 | 15 | 6 |  |  | 100 | 100 | 184.5 | 3.4794e-14
185-186 |  | 5 | 2 | 4 | 21 | 32 | 24 | 16 | 3 |  |  | 107 | 107 | 185.5 | 4.9565
186-187 | 1 | 2 | 2 | 5 | 15 | 19 | 18 | 10 | 4 |  |  | 76 | 76 | 186.5 | 9.9115
187-188 |  | 1 | 2 | 10 | 37 | 12 | 13 | 19 | 3 | 2 |  | 99 | 99 | 187.5 | 14.8634
188-189 | 1 | 1 | 2 | 5 | 14 | 14 | 9 | 4 | 1 |  |  | 51 | 51 | 188.5 | 19.8108
189-190 | 2 | 2 | 3 | 5 | 11 | 11 | 4 | 5 |  |  |  | 43 | 43 | 189.5 | 24.7522
190-191 |  | 2 | 5 | 4 | 11 | 14 | 6 | 1 | 1 |  |  | 44 | 44 | 190.5 | 29.6861
191-192 |  | 3 | 1 | 3 | 17 | 7 | 2 | 1 |  |  |  | 34 | 34 | 191.5 | 34.6109
192-193 |  |  |  | 4 | 8 | 13 | 3 |  |  |  |  | 28 | 28 | 192.5 | 39.5252
193-194 | 2 |  | 2 | 9 | 6 | 2 | 1 | 2 |  |  |  | 24 | 24 | 193.5 | 44.4274
194-195 |  | 1 | 5 | 7 | 5 | 2 | 3 |  |  |  |  | 23 | 23 | 194.5 | 49.3161
195-196 |  | 1 | 3 | 2 | 6 | 1 | [5 empty] | 13 | 13 | 195.5 | 54.1898
196-197 |  | 1 | 1 | 4 | 10 | [6 empty] | 16 | 16 | 196.5 | 59.0469
197-198 |  |  | 3 | 3 | 3 | [6 empty] | 9 | 9 | 197.5 | 63.8861
198-199 |  |  | 1 | 3 | 2 | [6 empty] | 6 | 6 | 198.5 | 68.7058
199-200 |  | 2 | 1 | 2 | 3 | [6 empty] | 8 | 8 | 199.5 | 73.5046
200-201 |  | 1 | 2 | 7 | 4 | 1 | [5 empty] | 15 | 15 | 200.5 | 78.281
201-202 | 2 | 4 | 4 | 1 | 2 | [6 empty] | 13 | 13 | 201.5 | 83.0336
202-203 |  | 1 | 2 | 3 | 2 | [6 empty] | 8 | 8 | 202.5 | 87.7608
203-204 |  | 1 | 2 | 2 | [7 empty] | 5 | 5 | 203.5 | 92.4614
204-205 | 2 | 4 | 1 | [8 empty] | 7 | 7 | 204.5 | 97.1337
205-206 |  |  | 1 | 4 | [7 empty] | 5 | 5 | 205.5 | 101.7765
206-207 |  | 5 | 2 | 1 | 2 | [6 empty] | 10 | 10 | 206.5 | 106.3883
207-208 | 1 | 3 | 4 | 1 | [7 empty] | 9 | 9 | 207.5 | 110.9676
208-209 | 2 | 1 | 5 | [8 empty] | 8 | 8 | 208.5 | 115.5132
209-210 |  |  | 3 | [8 empty] | 3 | 3 | 209.5 | 120.0236
210-211 |  | 4 | [9 empty] | 4 | 4 | 210.5 | 124.4974
211-212 | 1 |  |  | 2 | [7 empty] | 3 | 3 | 211.5 | 128.9333
212-213 |  | 2 | 2 | 1 | [7 empty] | 5 | 5 | 212.5 | 133.3299
213-214 |  | 2 | 1 | [8 empty] | 3 | 3 | 213.5 | 137.6859
214-215 |  | 1 | 2 | 1 | [7 empty] | 4 | 4 | 214.5 | 142
215-216 |  | 6 | 1 | 1 | [7 empty] | 8 | 8 | 215.5 | 146.2708
216-217 |  | 2 | 2 | 3 | [7 empty] | 7 | 7 | 216.5 | 150.4971
217-218 |  | 2 | [9 empty] | 2 | 2 | 217.5 | 154.6775
218-219 |  | 1 | [9 empty] | 1 | 1 | 218.5 | 158.8108
219-220 |  | 2 | [9 empty] | 2 | 2 | 219.5 | 162.8957
220-221 |  | 2 | [9 empty] | 2 | 2 | 220.5 | 166.931
221-222 |  | 2 | 2 | [8 empty] | 4 | 4 | 221.5 | 170.9155
222-223 |  | 1 | [9 empty] | 1 | 1 | 222.5 | 174.8479
223-224 |  | 1 | [9 empty] | 1 | 1 | 223.5 | 178.727
224-225 |  | 1 | [9 empty] | 1 | 1 | 224.5 | 182.5517
225-226 |  | 1 | [9 empty] | 1 | 1 | 225.5 | 186.3208
226-227 | 1 | 4 | [9 empty] | 5 | 5 | 226.5 | 190.0331
227-228 |  | 3 | 1 | [8 empty] | 4 | 4 | 227.5 | 193.6875
228-229 | 1 |  | 1 | [8 empty] | 2 | 2 | 228.5 | 197.283
229-230 | 1 | 1 | [9 empty] | 2 | 2 | 229.5 | 200.8183
230-231 | 1 | 4 | [9 empty] | 5 | 5 | 230.5 | 204.2925
231-232 | 1 | 3 | 2 | [8 empty] | 6 | 6 | 231.5 | 207.7045
232-233 |  | 1 | [9 empty] | 1 | 1 | 232.5 | 211.0531
234-235 |  | 2 | [9 empty] | 2 | 2 | 234.5 | 217.5566
235-236 | 1 | 2 | [9 empty] | 3 | 3 | 235.5 | 220.7095
236-237 | 1 | [10 empty] | 1 | 1 | 236.5 | 223.7951
237-238 |  | 1 | [9 empty] | 1 | 1 | 237.5 | 226.8125
240-241 |  | 1 | [9 empty] | 1 | 1 | 240.5 | 235.4467
242-243 | 3 | [10 empty] | 3 | 3 | 242.5 | 240.8457
243-244 | 1 | 1 | [9 empty] | 2 | 2 | 243.5 | 243.4355
247-248 |  | 1 | [9 empty] | 1 | 1 | 247.5 | 253.0459
251-252 |  | 2 | [9 empty] | 2 | 2 | 251.5 | 261.4234
252-253 |  | 1 | [9 empty] | 1 | 1 | 252.5 | 263.3202
253-254 |  | 1 | [9 empty] | 1 | 1 | 253.5 | 265.1368
255-256 |  | 2 | [9 empty] | 2 | 2 | 255.5 | 268.5273
257-258 |  | 1 | [9 empty] | 1 | 1 | 257.5 | 271.5906
258-259 | 1 | [10 empty] | 1 | 1 | 258.5 | 272.9983
260-261 | 1 | [10 empty] | 1 | 1 | 260.5 | 275.564
262-263 | 1 | [10 empty] | 1 | 1 | 262.5 | 277.7939
263-264 | 2 | [10 empty] | 2 | 2 | 263.5 | 278.7821
265-266 |  | 1 | [9 empty] | 1 | 1 | 265.5 | 280.5035
267-268 | 4 | 1 | [9 empty] | 5 | 5 | 267.5 | 281.8831
268-269 |  | 1 | [9 empty] | 1 | 1 | 268.5 | 282.4442
270-271 | 1 | 2 | [9 empty] | 3 | 3 | 270.5 | 283.3082
271-272 | 1 | [10 empty] | 1 | 1 | 271.5 | 283.6108
273-274 |  | 3 | [9 empty] | 3 | 3 | 273.5 | 283.9567
274-275 |  | 1 | [9 empty] | 1 | 1 | 274.5 | 284
276-277 | 1 | [10 empty] | 1 | 1 | 276.5 | 283.827
277-278 | 1 | [10 empty] | 1 | 1 | 277.5 | 283.6108
279-280 |  | 1 | [9 empty] | 1 | 1 | 279.5 | 282.9193
282-283 |  | 1 | [9 empty] | 1 | 1 | 282.5 | 281.2361
284-285 | 1 | [10 empty] | 1 | 1 | 284.5 | 279.6854
285-286 |  | 1 | [9 empty] | 1 | 1 | 285.5 | 278.7821
286-287 | 1 | [10 empty] | 1 | 1 | 286.5 | 277.7939
289-290 | 3 | [10 empty] | 3 | 3 | 289.5 | 274.3229
291-292 |  | 1 | [9 empty] | 1 | 1 | 291.5 | 271.5906
293-294 | 1 | [10 empty] | 1 | 1 | 293.5 | 268.5273
296-297 |  | 1 | [9 empty] | 1 | 1 | 296.5 | 263.3202
297-298 | 1 | [10 empty] | 1 | 1 | 297.5 | 261.4234
298-299 |  | 1 | [9 empty] | 1 | 1 | 298.5 | 259.4469
299-300 |  | 1 | [9 empty] | 1 | 1 | 299.5 | 257.3914
302-303 |  | 1 | [9 empty] | 1 | 1 | 302.5 | 250.7571
304-305 | 1 | [10 empty] | 1 | 1 | 304.5 | 245.9512
307-308 | 2 | 2 | [9 empty] | 4 | 4 | 307.5 | 238.1824
308-309 |  | 1 | [9 empty] | 1 | 1 | 308.5 | 235.4467
309-310 |  | 1 | [9 empty] | 1 | 1 | 309.5 | 232.6392
311-312 | 1 | [10 empty] | 1 | 1 | 311.5 | 226.8125
312-313 | 3 | 1 | [9 empty] | 4 | 4 | 312.5 | 223.7951
313-314 |  | 1 | [9 empty] | 1 | 1 | 313.5 | 220.7095
314-315 | 1 | 1 | [9 empty] | 2 | 2 | 314.5 | 217.5566
315-316 | 1 | 1 | [9 empty] | 2 | 2 | 315.5 | 214.3375
316-317 | 2 | 1 | [9 empty] | 3 | 3 | 316.5 | 211.0531
317-318 |  | 2 | [9 empty] | 2 | 2 | 317.5 | 207.7045
318-319 |  | 2 | [9 empty] | 2 | 2 | 318.5 | 204.2925
319-320 | 1 | [10 empty] | 1 | 1 | 319.5 | 200.8183
320-321 | 2 | [10 empty] | 2 | 2 | 320.5 | 197.283
322-323 |  | 1 | [9 empty] | 1 | 1 | 322.5 | 190.0331
324-325 |  | 2 | 1 | [8 empty] | 3 | 3 | 324.5 | 182.5517
325-326 | 4 | 2 | [9 empty] | 6 | 6 | 325.5 | 178.727
326-327 |  | 1 | [9 empty] | 1 | 1 | 326.5 | 174.8479
327-328 |  |  | 2 | [8 empty] | 2 | 2 | 327.5 | 170.9155
328-329 |  | 2 | [9 empty] | 2 | 2 | 328.5 | 166.931
329-330 | 1 | [10 empty] | 1 | 1 | 329.5 | 162.8957
330-331 | 2 | [10 empty] | 2 | 2 | 330.5 | 158.8108
331-332 |  | 1 | [9 empty] | 1 | 1 | 331.5 | 154.6775
332-333 | 1 | 1 | [9 empty] | 2 | 2 | 332.5 | 150.4971
333-334 |  | 2 | [9 empty] | 2 | 2 | 333.5 | 146.2708
334-335 | 1 | [10 empty] | 1 | 1 | 334.5 | 142
335-336 |  | 3 | [9 empty] | 3 | 3 | 335.5 | 137.6859
336-337 |  | 1 | [9 empty] | 1 | 1 | 336.5 | 133.3299
337-338 |  | 2 | [9 empty] | 2 | 2 | 337.5 | 128.9333
338-339 |  | 4 | [9 empty] | 4 | 4 | 338.5 | 124.4974
339-340 | 2 | 3 | [9 empty] | 5 | 5 | 339.5 | 120.0236
340-341 |  | 1 | [9 empty] | 1 | 1 | 340.5 | 115.5132
341-342 | 1 |  | 1 | [8 empty] | 2 | 2 | 341.5 | 110.9676
342-343 | 1 | 1 | 2 | 2 | [7 empty] | 6 | 6 | 342.5 | 106.3883
343-344 |  | 3 | 4 | [8 empty] | 7 | 7 | 343.5 | 101.7765
344-345 | 2 | 2 | 1 | [8 empty] | 5 | 5 | 344.5 | 97.1337
345-346 |  | 2 | 3 | 2 | [7 empty] | 7 | 7 | 345.5 | 92.4614
346-347 |  | 6 | 3 | 2 | [7 empty] | 11 | 11 | 346.5 | 87.7608
347-348 |  | 5 | 3 | 1 | [7 empty] | 9 | 9 | 347.5 | 83.0336
348-349 |  | 1 | 3 | 2 | 1 | [6 empty] | 7 | 7 | 348.5 | 78.281
349-350 |  | 1 | 3 | [8 empty] | 4 | 4 | 349.5 | 73.5046
350-351 | 1 |  | 4 | 1 | [7 empty] | 6 | 6 | 350.5 | 68.7058
351-352 |  | 2 | 6 | 5 | 1 | [6 empty] | 14 | 14 | 351.5 | 63.8861
352-353 | 2 | 1 | 2 | 2 | [7 empty] | 7 | 7 | 352.5 | 59.0469
353-354 |  | 2 | 6 | 5 | 1 | [6 empty] | 14 | 14 | 353.5 | 54.1898
354-355 |  | 1 | 2 | 2 | 2 | 3 | [5 empty] | 10 | 10 | 354.5 | 49.3161
355-356 |  | 2 | 9 | 6 |  |  | 1 |  |  |  |  | 18 | 18 | 355.5 | 44.4274
356-357 |  | 1 | 1 | 11 | 5 | 3 | 1 | 1 |  |  |  | 23 | 23 | 356.5 | 39.5252
357-358 |  | 4 | 3 | 4 | 6 | 7 | 2 |  |  |  |  | 26 | 26 | 357.5 | 34.6109
358-359 |  | 2 | 8 | 15 | 18 | 8 | 3 | 4 |  |  |  | 58 | 58 | 358.5 | 29.6861
359-360 |  | 1 | 7 | 6 | 10 | 6 | 8 | 4 |  |  |  | 42 | 42 | 359.5 | 24.7522
Grand Total | 175 | 436 | 391 | 484 | 707 | 661 | 569 | 544 | 299 | 48 | 6 | 4320
Grand Total | 175 | 436 | 391 | 484 | 707 | 661 | 569 | 544 | 299 | 48 | 6 | 4320
"weight" speed | 0 | 0 | 0.25 | 0.35 | 0.45 | 0.55 | 0.65 | 0.75 | 0.85 | 0.95 | 1.05
slack weight | 0: 611; 0.35: slack area; 0.45: 228.65; 0.55: ratio; 0.65: 14.14%
|  |  |  | slack speed (intake velocity) | 0.3
Inflow = area * weight speed * count
Direction | 0-0.1 | 0.1-0.2 | 0.2-0.3 | 0.3-0.4 | 0.4-0.5 | 0.5-0.6 | 0.6-0.7 | 0.7-0.8 | 0.8-0.9 | 0.9-1 | 1-1.1 | direction total
0-1 | 0 | 0 | 19.8108 | 76.2717 | 80.2339 | 98.0637 | 154.5245 | 178.2975 | 50.5176 | 0 | 0 | 657.7198
1-2 | 0 | 0 | 18.5793 | 36.4154 | 120.3936 | 106.2734 | 96.6122 | 167.2134 | 63.1695 | 0 | 0 | 608.6567
2-3 | 0 | 0 | 0 | 45.0971 | 71.3625 | 54.513 | 64.4245 | 111.5039 | 143.2206 | 37.6635 | 0 | 527.7851
3-4 | 0 | 0 | 7.4347 | 20.8172 | 37.9171 | 49.0692 | 57.9909 | 104.0862 | 84.2602 | 4.7087 | 0 | 366.2841
4-5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5-6 | 0 | 0 | 6.1956 | 13.8782 | 17.8433 | 68.1516 | 83.7646 | 89.2167 | 80.0472 | 9.4173 | 5.2043 | 373.7189
6-7 | 0 | 0 | 12.3893 | 20.8141 | 111.5039 | 130.8312 | 167.5036 | 289.9101 | 193.769 | 84.743 | 0 | 1011.4642
7-8 | 0 | 0 | 40.8744 | 31.2132 | 93.6395 | 171.6724 | 231.8692 | 479.345 | 341.1153 | 28.2405 | 0 | 1417.9695
8-9 | 0 | 0 | 14.8581 | 48.5366 | 151.5529 | 239.7111 | 360.5573 | 252.5882 | 252.5882 | 94.1015 | 41.6028 | 1456.0966
9-10 | 0 | 0 | 61.8806 | 51.9797 | 200.4931 | 217.8196 | 337.868 | 575.4894 | 378.7091 | 141.0877 | 51.9797 | 2017.3068
10-11 | 0 | 0 | 22.2646 | 72.7309 | 160.3049 | 310.2196 | 443.8069 | 178.1165 | 479.4302 | 141.0089 | 0 | 1807.8825
11-12 | 0 | 0 | 34.6109 | 218.0486 | 218.0486 | 228.4319 | 269.965 | 233.6235 | 264.7733 | 32.8803 | 0 | 1500.3822
12-13 | 0 | 0 | 39.5252 | 166.0057 | 213.4359 | 239.1272 | 51.3827 | 29.6439 | 67.1928 | 0 | 0 | 806.3133
13-14 | 0 | 0 | 33.3205 | 62.1983 | 179.9309 | 244.3506 | 259.9002 | 166.6027 | 264.343 | 42.206 | 0 | 1252.8523
14-15 | 0 | 0 | 73.9741 | 207.1275 | 244.1146 | 271.2385 | 160.2773 | 258.9094 | 83.8373 | 0 | 0 | 1299.4788
15-16 | 0 | 0 | 54.1898 | 75.8657 | 146.3123 | 178.8262 | 105.67 | 40.6423 | 0 | 0 | 0 | 601.5063
16-17 | 0 | 0 | 14.7617 | 103.3321 | 26.5711 | 162.379 | 38.3805 | 0 | 0 | 0 | 0 | 345.4245
17-18 | 0 | 0 | 31.943 | 89.4405 | 373.7337 | 175.6868 | 0 | 0 | 0 | 0 | 0 | 670.804
18-19 | 0 | 0 | 51.5294 | 192.3763 | 278.2586 | 302.3056 | 89.3176 | 0 | 0 | 0 | 0 | 913.7874
19-20 | 0 | 0 | 55.1285 | 205.8129 | 66.1541 | 161.7101 | 0 | 0 | 0 | 0 | 0 | 488.8056
20-21 | 0 | 0 | 39.1405 | 109.5934 | 105.6794 | 0 | 0 | 0 | 0 | 0 | 0 | 254.4133
21-22 | 0 | 0 | 62.2752 | 87.1852 | 112.0953 | 0 | 0 | 0 | 0 | 0 | 0 | 261.5557
22-23 | 0 | 0 | 65.8206 | 92.1489 | 197.4619 | 48.2685 | 0 | 0 | 0 | 0 | 0 | 403.6998
23-24 | 0 | 0 | 138.692 | 97.0844 | 124.8228 | 0 | 0 | 0 | 0 | 0 | 0 | 360.5993
24-25 | 0 | 0 | 121.4172 | 101.9904 | 43.7102 | 0 | 0 | 0 | 0 | 0 | 0 | 267.1177
25-26 | 0 | 0 | 25.4441 | 0 | 137.3983 | 0 | 0 | 0 | 0 | 0 | 0 | 162.8424
26-27 | 0 | 0 | 26.5971 | 111.7077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138.3048
27-28 | 0 | 0 | 138.7096 | 155.3547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 294.0642
28-29 | 0 | 0 | 28.8783 | 121.2889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150.1672
29-30 | 0 | 0 | 60.0118 | 168.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228.0448
30-31 | 0 | 0 | 31.1244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.1244
31-32 | 0 | 0 | 32.2333 | 90.2533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.4866
32-33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33-34 | 0 | 0 | 0 | 96.3802 | 61.9587 | 0 | 0 | 0 | 0 | 0 | 0 | 158.3388
34-35 | 0 | 0 | 0 | 49.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.7
35-36 | 0 | 0 | 73.1354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.1354
36-37 | 0 | 0 | 75.2485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.2485
37-38 | 0 | 0 | 38.6694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.6694
38-39 | 0 | 0 | 39.7027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.7027
39-40 | 0 | 0 | 40.7239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.7239
40-41 | 0 | 0 | 0 | 116.8517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.8517
41-42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42-43 | 0 | 0 | 131.1359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131.1359
43-44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44-45 | 0 | 0 | 45.6379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.6379
46-47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47-48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48-49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
49-50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50-51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51-52 | 0 | 0 | 51.9261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.9261
52-53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54-55 | 0 | 0 | 54.3892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.3892
55-56 | 0 | 0 | 110.3547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.3547
56-57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58-59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59-60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60-61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
63-64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
64-65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
66-67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67-68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
69-70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
71-72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72-73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73-74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
75-76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
77-78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78-79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79-80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
80-81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
81-82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
82-83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
83-84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
84-85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
87-88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
89-90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90-91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91-92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
92-93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95-96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
99-100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103-104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104-105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
105-106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
107-108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108-109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109-110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110-111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111-112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
113-114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
114-115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
115-116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
117-118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
118-119 | 0 | 0 | 64.8617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.8617
119-120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
122-123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
123-124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
125-126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
126-127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
127-128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
128-129 | 0 | 0 | 117.7233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.7233
129-130 | 0 | 0 | 58.1598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.1598
132-133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
133-134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
134-135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
135-136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
137-138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
138-139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
139-140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
141-142 | 0 | 0 | 48.4219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.4219
143-144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
144-145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
145-146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
147-148 | 0 | 0 | 85.4577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.4577
148-149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149-150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150-151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
151-152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
152-153 | 0 | 0 | 188.1213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188.1213
153-154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154-155 | 0 | 0 | 71 | 99.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170.4
155-156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156-157 | 0 | 0 | 33.3325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.3325
157-158 | 0 | 0 | 32.2333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.2333
158-159 | 0 | 0 | 31.1244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.1244
159-160 | 0 | 0 | 30.0059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.0059
160-161 | 0 | 0 | 28.8783 | 80.8592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.7375
161-162 | 0 | 0 | 83.2257 | 38.8387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.0644
162-163 | 0 | 0 | 79.7912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.7912
163-164 | 0 | 0 | 76.3324 | 35.6218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.9541
164-165 | 0 | 0 | 24.2834 | 101.9904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126.2738
165-166 | 0 | 0 | 138.692 | 0 | 0 | 50.8537 | 0 | 0 | 0 | 0 | 0 | 189.5458
166-167 | 0 | 0 | 21.9402 | 92.1489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.0891
167-168 | 0 | 0 | 41.5168 | 29.0617 | 74.7302 | 0 | 0 | 0 | 0 | 0 | 0 | 145.3087
168-169 | 0 | 0 | 19.5703 | 27.3984 | 140.9058 | 0 | 0 | 0 | 0 | 0 | 0 | 187.8744
169-170 | 0 | 0 | 73.5046 | 25.7266 | 165.3854 | 0 | 0 | 0 | 0 | 0 | 0 | 264.6166
170-171 | 0 | 0 | 68.7058 | 72.1411 | 185.5057 | 264.5174 | 0 | 0 | 0 | 0 | 0 | 590.87
171-172 | 0 | 0 | 95.8291 | 67.0804 | 172.4925 | 0 | 0 | 95.8291 | 0 | 0 | 0 | 431.2312
172-173 | 0 | 0 | 118.0938 | 206.6642 | 132.8556 | 97.4274 | 76.761 | 44.2852 | 0 | 0 | 0 | 676.0872
173-174 | 0 | 0 | 27.0949 | 132.7649 | 121.9269 | 119.2175 | 35.2233 | 40.6423 | 0 | 0 | 0 | 476.8698
174-175 | 0 | 0 | 73.9741 | 86.3031 | 133.1534 | 54.2477 | 128.2218 | 110.9612 | 0 | 0 | 0 | 586.8614
175-176 | 0 | 0 | 44.4274 | 15.5496 | 379.8542 | 439.8311 | 173.2668 | 199.9232 | 37.7633 | 0 | 0 | 1290.6156
176-177 | 0 | 0 | 49.4065 | 83.0028 | 213.4359 | 195.6495 | 308.2963 | 207.5071 | 100.7892 | 0 | 0 | 1158.0872
177-178 | 0 | 0 | 34.6109 | 72.6829 | 140.1741 | 361.6838 | 314.9591 | 467.2471 | 29.4193 | 0 | 0 | 1420.7772
178-179 | 0 | 0 | 14.843 | 124.6816 | 267.1748 | 310.2196 | 270.1434 | 289.4393 | 50.4663 | 0 | 0 | 1326.9679
179-180 | 0 | 0 | 24.7522 | 60.643 | 144.8006 | 367.5706 | 305.6901 | 371.2835 | 210.394 | 0 | 0 | 1485.1339
180-181 | 0 | 0 | 24.7635 | 83.2055 | 205.0422 | 261.5031 | 412.0654 | 371.4532 | 235.749 | 18.8203 | 0 | 1612.6023
181-182 | 0 | 0 | 33.4427 | 36.4154 | 140.4592 | 179.8473 | 270.5141 | 245.2463 | 101.0712 | 14.1202 | 0 | 1021.1164
182-183 | 0 | 0 | 4.9557 | 20.8141 | 71.3625 | 174.4416 | 199.7159 | 185.8398 | 210.6185 | 0 | 0 | 867.7481
183-184 | 0 | 0 | 4.9565 | 19.0825 | 55.7604 | 95.4123 | 96.6514 | 111.5209 | 46.3431 | 23.5433 | 0 | 453.2704
184-185 | 0 | 0 | 5.2191e-14 | 4.8712e-14 | 3.1315e-13 | 4.0187e-13 | 6.1064e-13 | 3.9143e-13 | 1.7745e-13 | 0 | 0 | 1.9954e-12
185-186 | 0 | 0 | 2.4782 | 6.9391 | 46.8388 | 87.2341 | 77.3211 | 59.4778 | 12.639 | 0 | 0 | 292.9282
186-187 | 0 | 0 | 4.9557 | 17.345 | 66.9023 | 103.5747 | 115.964 | 74.3359 | 33.699 | 0 | 0 | 416.7768
187-188 | 0 | 0 | 7.4317 | 52.0219 | 247.4758 | 98.0985 | 125.5958 | 211.8036 | 37.9017 | 28.2405 | 0 | 808.5696
188-189 | 0 | 0 | 9.9054 | 34.669 | 124.8083 | 152.5435 | 115.8934 | 59.4325 | 16.8392 | 0 | 0 | 514.0913
189-190 | 0 | 0 | 18.5642 | 43.3164 | 122.5235 | 149.751 | 64.3558 | 92.8209 | 0 | 0 | 0 | 491.3318
190-191 | 0 | 0 | 37.1076 | 41.5605 | 146.9461 | 228.5828 | 115.7757 | 22.2646 | 25.2332 | 0 | 0 | 617.4705
191-192 | 0 | 0 | 8.6527 | 36.3414 | 264.7733 | 133.2519 | 44.9942 | 25.9582 | 0 | 0 | 0 | 513.9718
192-193 | 0 | 0 | 0 | 55.3352 | 142.2906 | 282.6049 | 77.0741 | 0 | 0 | 0 | 0 | 557.3048
193-194 | 0 | 0 | 22.2137 | 139.9463 | 119.9539 | 48.8701 | 28.8778 | 66.6411 | 0 | 0 | 0 | 426.5029
194-195 | 0 | 0 | 61.6451 | 120.8244 | 110.9612 | 54.2477 | 96.1664 | 0 | 0 | 0 | 0 | 443.8447
195-196 | 0 | 0 | 40.6423 | 37.9328 | 146.3123 | 29.8044 | 0 | 0 | 0 | 0 | 0 | 254.6918
196-197 | 0 | 0 | 14.7617 | 82.6657 | 265.7111 | 0 | 0 | 0 | 0 | 0 | 0 | 363.1386
197-198 | 0 | 0 | 47.9146 | 67.0804 | 86.2462 | 0 | 0 | 0 | 0 | 0 | 0 | 201.2412
198-199 | 0 | 0 | 17.1765 | 72.1411 | 61.8352 | 0 | 0 | 0 | 0 | 0 | 0 | 151.1528
199-200 | 0 | 0 | 18.3762 | 51.4532 | 99.2312 | 0 | 0 | 0 | 0 | 0 | 0 | 169.0606
200-201 | 0 | 0 | 39.1405 | 191.7885 | 140.9058 | 43.0546 | 0 | 0 | 0 | 0 | 0 | 414.8893
201-202 | 0 | 0 | 83.0336 | 29.0617 | 74.7302 | 0 | 0 | 0 | 0 | 0 | 0 | 186.8255
202-203 | 0 | 0 | 43.8804 | 92.1489 | 78.9847 | 0 | 0 | 0 | 0 | 0 | 0 | 215.014
203-204 | 0 | 0 | 46.2307 | 64.7229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.9536
204-205 | 0 | 0 | 24.2834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.2834
205-206 | 0 | 0 | 25.4441 | 142.4871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167.9312
206-207 | 0 | 0 | 53.1941 | 37.2359 | 95.7494 | 0 | 0 | 0 | 0 | 0 | 0 | 186.1795
207-208 | 0 | 0 | 110.9676 | 38.8387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149.8063
208-209 | 0 | 0 | 144.3915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 144.3915
209-210 | 0 | 0 | 90.0177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.0177
210-211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
211-212 | 0 | 0 | 0 | 90.2533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.2533
212-213 | 0 | 0 | 66.665 | 46.6655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.3304
213-214 | 0 | 0 | 34.4215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.4215
214-215 | 0 | 0 | 71 | 49.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.7
215-216 | 0 | 0 | 36.5677 | 51.1948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.7625
216-217 | 0 | 0 | 75.2485 | 158.0219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 233.2705
217-218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
218-219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
219-220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220-221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
221-222 | 0 | 0 | 85.4577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.4577
222-223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
223-224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
224-225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
225-226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
226-227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
227-228 | 0 | 0 | 48.4219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.4219
228-229 | 0 | 0 | 49.3207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.3207
229-230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
230-231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
231-232 | 0 | 0 | 103.8522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.8522
232-233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
234-235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
235-236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
236-237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
237-238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
240-241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242-243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
243-244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247-248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
251-252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
252-253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
253-254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
255-256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257-258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
258-259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
260-261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
262-263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
263-264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
265-266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
267-268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
268-269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
270-271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
271-272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
273-274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
274-275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
276-277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
277-278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
279-280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
282-283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
284-285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
285-286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
286-287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
289-290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
291-292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
293-294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
296-297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297-298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
298-299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
299-300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
302-303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
304-305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
307-308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
308-309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
309-310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311-312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
312-313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313-314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314-315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
315-316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
316-317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
317-318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
318-319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
319-320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
320-321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
322-323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
324-325 | 0 | 0 | 45.6379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.6379
325-326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
326-327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
327-328 | 0 | 0 | 85.4577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.4577
328-329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
329-330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
330-331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
331-332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
332-333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333-334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
334-335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
335-336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
336-337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
337-338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
338-339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
339-340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
340-341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
341-342 | 0 | 0 | 27.7419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.7419
342-343 | 0 | 0 | 53.1941 | 74.4718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.6659
343-344 | 0 | 0 | 101.7765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.7765
344-345 | 0 | 0 | 24.2834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.2834
345-346 | 0 | 0 | 69.346 | 64.7229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134.069
346-347 | 0 | 0 | 65.8206 | 61.4326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.2532
347-348 | 0 | 0 | 62.2752 | 29.0617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.3369
348-349 | 0 | 0 | 58.7108 | 54.7967 | 35.2265 | 0 | 0 | 0 | 0 | 0 | 0 | 148.7339
349-350 | 0 | 0 | 55.1285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.1285
350-351 | 0 | 0 | 68.7058 | 24.047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.7529
351-352 | 0 | 0 | 95.8291 | 111.8007 | 28.7487 | 0 | 0 | 0 | 0 | 0 | 0 | 236.3786
352-353 | 0 | 0 | 29.5235 | 41.3328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.8563
353-354 | 0 | 0 | 81.2846 | 94.8321 | 24.3854 | 0 | 0 | 0 | 0 | 0 | 0 | 200.5021
354-355 | 0 | 0 | 24.658 | 34.5213 | 44.3845 | 81.3715 | 0 | 0 | 0 | 0 | 0 | 184.9353
355-356 | 0 | 0 | 99.9616 | 93.2975 | 0 | 0 | 28.8778 | 0 | 0 | 0 | 0 | 222.1369
356-357 | 0 | 0 | 9.8813 | 152.1719 | 88.9316 | 65.2165 | 25.6914 | 29.6439 | 0 | 0 | 0 | 371.5365
357-358 | 0 | 0 | 25.9582 | 48.4553 | 93.4494 | 133.2519 | 44.9942 | 0 | 0 | 0 | 0 | 346.1089
358-359 | 0 | 0 | 59.3722 | 155.8519 | 240.4573 | 130.6188 | 57.8879 | 89.0583 | 0 | 0 | 0 | 733.2463
359-360 | 0 | 0 | 43.3164 | 51.9797 | 111.385 | 81.6824 | 128.7116 | 74.2567 | 0 | 0 | 0 | 491.3318
draw excl slacks | 50291.84 |  |  |  | 1.5 | 2.5 | 3.5 | 4.5 | 5.5 | 6.5 | 7.5
slacks | 41911.545 |  |  |  | 45.27 | 43.39 | 42.13 | 41.61 | 41.68 | 42.35 | 43.66
total draw | 0: 92203.385
divisor | 0: 2216.05
Average | 0: 41.6071; 0: m2

## northern slk 0.3
SZC northern slk 0.3 |  |  | SZC intake alignment: |  |  | 4.5
Count of Direction at 2.04m above bed (deg) | Column Labels | [13 empty] | 284
Row Labels | 0-0.1 | 0.1-0.2 | 0.2-0.3 | 0.3-0.4 | 0.4-0.5 | 0.5-0.6 | 0.6-0.7 | 0.7-0.8 | 0.8-0.9 | 0.9-1 | 1-1.1 | Grand Total |  | mid bin | area m2
0-1 | 3 | 4 | 4 | 11 | 9 | 9 | 12 | 12 | 3 |  |  | 67 | 67 | 0.5 | 19.8108
1-2 |  | 1 | 5 | 7 | 18 | 13 | 10 | 15 | 5 |  |  | 74 | 74 | 1.5 | 14.8634
2-3 | 1 | 4 |  | 13 | 16 | 10 | 10 | 15 | 17 | 4 |  | 90 | 90 | 2.5 | 9.9115
3-4 | 2 |  | 6 | 12 | 17 | 18 | 18 | 28 | 20 | 1 |  | 122 | 122 | 3.5 | 4.9565
4-5 |  | 3 | 2 | 11 | 17 | 14 | 19 | 34 | 20 | 3 | 1 | 124 | 124 | 4.5 | 0
5-6 | 1 | 1 | 5 | 8 | 8 | 25 | 26 | 24 | 19 | 2 | 1 | 120 | 120 | 5.5 | 4.9565
6-7 |  |  | 5 | 6 | 25 | 24 | 26 | 39 | 23 | 9 |  | 157 | 157 | 6.5 | 9.9115
7-8 |  | 1 | 11 | 6 | 14 | 21 | 24 | 43 | 27 | 2 |  | 149 | 149 | 7.5 | 14.8634
8-9 | 1 | 1 | 3 | 7 | 17 | 22 | 28 | 17 | 15 | 5 | 2 | 118 | 118 | 8.5 | 19.8108
9-10 | 1 |  | 10 | 6 | 18 | 16 | 21 | 31 | 18 | 6 | 2 | 129 | 129 | 9.5 | 24.7522
10-11 |  | 3 | 3 | 7 | 12 | 19 | 23 | 8 | 19 | 5 |  | 99 | 99 | 10.5 | 29.6861
11-12 |  | 2 | 4 | 18 | 14 | 12 | 12 | 9 | 9 | 1 |  | 81 | 81 | 11.5 | 34.6109
12-13 |  | 2 | 4 | 12 | 12 | 11 | 2 | 1 | 2 |  |  | 46 | 46 | 12.5 | 39.5252
13-14 | 1 | 2 | 3 | 4 | 9 | 10 | 9 | 5 | 7 | 1 |  | 51 | 51 | 13.5 | 44.4274
14-15 |  | 4 | 6 | 12 | 11 | 10 | 5 | 7 | 2 |  |  | 57 | 57 | 14.5 | 49.3161
15-16 |  |  | 4 | 4 | 6 | 6 | 3 | 1 |  |  |  | 24 | 24 | 15.5 | 54.1898
16-17 | 2 | 3 | 1 | 5 | 1 | 5 | 1 |  |  |  |  | 18 | 18 | 16.5 | 59.0469
17-18 |  | 5 | 2 | 4 | 13 | 5 | [5 empty] | 29 | 29 | 17.5 | 63.8861
18-19 | 2 |  | 3 | 8 | 9 | 8 | 2 |  |  |  |  | 32 | 32 | 18.5 | 68.7058
19-20 |  | 4 | 3 | 8 | 2 | 4 | [5 empty] | 21 | 21 | 19.5 | 73.5046
20-21 |  |  | 2 | 4 | 3 | [6 empty] | 9 | 9 | 20.5 | 78.281
21-22 |  |  | 3 | 3 | 3 | [6 empty] | 9 | 9 | 21.5 | 83.0336
22-23 | 1 | 2 | 3 | 3 | 5 | 1 | [5 empty] | 15 | 15 | 22.5 | 87.7608
23-24 | 1 | 3 | 6 | 3 | 3 | [6 empty] | 16 | 16 | 23.5 | 92.4614
24-25 |  | 2 | 5 | 3 | 1 | [6 empty] | 11 | 11 | 24.5 | 97.1337
25-26 |  | 3 | 1 |  | 3 | [6 empty] | 7 | 7 | 25.5 | 101.7765
26-27 | 3 | 2 | 1 | 3 | [7 empty] | 9 | 9 | 26.5 | 106.3883
27-28 | 1 | 1 | 5 | 4 | [7 empty] | 11 | 11 | 27.5 | 110.9676
28-29 |  |  | 1 | 3 | [7 empty] | 4 | 4 | 28.5 | 115.5132
29-30 |  |  | 2 | 4 | [7 empty] | 6 | 6 | 29.5 | 120.0236
30-31 |  | 2 | 1 | [8 empty] | 3 | 3 | 30.5 | 124.4974
31-32 |  |  | 1 | 2 | [7 empty] | 3 | 3 | 31.5 | 128.9333
32-33 |  | 2 | [9 empty] | 2 | 2 | 32.5 | 133.3299
33-34 |  |  |  | 2 | 1 | [6 empty] | 3 | 3 | 33.5 | 137.6859
34-35 |  | 3 |  | 1 | [7 empty] | 4 | 4 | 34.5 | 142
35-36 |  | 3 | 2 | [8 empty] | 5 | 5 | 35.5 | 146.2708
36-37 | 3 | 2 | 2 | [8 empty] | 7 | 7 | 36.5 | 150.4971
37-38 | 1 | 1 | 1 | [8 empty] | 3 | 3 | 37.5 | 154.6775
38-39 |  | 2 | 1 | [8 empty] | 3 | 3 | 38.5 | 158.8108
39-40 |  | 1 | 1 | [8 empty] | 2 | 2 | 39.5 | 162.8957
40-41 | 3 | 1 |  | 2 | [7 empty] | 6 | 6 | 40.5 | 166.931
41-42 | 1 | 1 | [9 empty] | 2 | 2 | 41.5 | 170.9155
42-43 | 3 | 2 | 3 | [8 empty] | 8 | 8 | 42.5 | 174.8479
43-44 | 1 | 2 | [9 empty] | 3 | 3 | 43.5 | 178.727
44-45 |  | 4 | 1 | [8 empty] | 5 | 5 | 44.5 | 182.5517
46-47 |  | 3 | [9 empty] | 3 | 3 | 46.5 | 190.0331
47-48 |  | 4 | [9 empty] | 4 | 4 | 47.5 | 193.6875
48-49 |  | 1 | [9 empty] | 1 | 1 | 48.5 | 197.283
49-50 | 1 | 3 | [9 empty] | 4 | 4 | 49.5 | 200.8183
50-51 |  | 3 | [9 empty] | 3 | 3 | 50.5 | 204.2925
51-52 |  | 3 | 1 | [8 empty] | 4 | 4 | 51.5 | 207.7045
52-53 | 4 | [10 empty] | 4 | 4 | 52.5 | 211.0531
54-55 |  | 1 | 1 | [8 empty] | 2 | 2 | 54.5 | 217.5566
55-56 | 1 |  | 2 | [8 empty] | 3 | 3 | 55.5 | 220.7095
56-57 |  | 5 | [9 empty] | 5 | 5 | 56.5 | 223.7951
58-59 |  | 1 | [9 empty] | 1 | 1 | 58.5 | 229.7608
59-60 |  | 1 | [9 empty] | 1 | 1 | 59.5 | 232.6392
60-61 | 1 | [10 empty] | 1 | 1 | 60.5 | 235.4467
63-64 |  | 2 | [9 empty] | 2 | 2 | 63.5 | 243.4355
64-65 |  | 2 | [9 empty] | 2 | 2 | 64.5 | 245.9512
66-67 |  | 1 | [9 empty] | 1 | 1 | 66.5 | 250.7571
67-68 | 1 | 1 | [9 empty] | 2 | 2 | 67.5 | 253.0459
69-70 | 1 | 1 | [9 empty] | 2 | 2 | 69.5 | 257.3914
71-72 |  | 1 | [9 empty] | 1 | 1 | 71.5 | 261.4234
72-73 | 2 | [10 empty] | 2 | 2 | 72.5 | 263.3202
73-74 |  | 1 | [9 empty] | 1 | 1 | 73.5 | 265.1368
75-76 |  | 1 | [9 empty] | 1 | 1 | 75.5 | 268.5273
77-78 | 1 | [10 empty] | 1 | 1 | 77.5 | 271.5906
78-79 | 1 | 2 | [9 empty] | 3 | 3 | 78.5 | 272.9983
79-80 | 1 | 1 | [9 empty] | 2 | 2 | 79.5 | 274.3229
80-81 | 2 | [10 empty] | 2 | 2 | 80.5 | 275.564
81-82 |  | 2 | [9 empty] | 2 | 2 | 81.5 | 276.7211
82-83 |  | 1 | [9 empty] | 1 | 1 | 82.5 | 277.7939
83-84 |  | 1 | [9 empty] | 1 | 1 | 83.5 | 278.7821
84-85 | 1 | [10 empty] | 1 | 1 | 84.5 | 279.6854
87-88 |  | 1 | [9 empty] | 1 | 1 | 87.5 | 281.8831
89-90 | 1 | [10 empty] | 1 | 1 | 89.5 | 282.9193
90-91 | 3 | 1 | [9 empty] | 4 | 4 | 90.5 | 283.3082
91-92 |  | 1 | [9 empty] | 1 | 1 | 91.5 | 283.6108
92-93 | 2 | [10 empty] | 2 | 2 | 92.5 | 283.827
95-96 |  | 1 | [9 empty] | 1 | 1 | 95.5 | 283.9567
99-100 | 2 | [10 empty] | 2 | 2 | 99.5 | 282.9193
101-102 | 1 | [10 empty] | 1 | 1 | 101.5 | 281.8831
102-103 |  | 1 | [9 empty] | 1 | 1 | 102.5 | 281.2361
103-104 | 1 | [10 empty] | 1 | 1 | 103.5 | 280.5035
104-105 | 2 | [10 empty] | 2 | 2 | 104.5 | 279.6854
105-106 | 1 | [10 empty] | 1 | 1 | 105.5 | 278.7821
107-108 | 1 | [10 empty] | 1 | 1 | 107.5 | 276.7211
108-109 | 1 | 2 | [9 empty] | 3 | 3 | 108.5 | 275.564
109-110 | 2 | [10 empty] | 2 | 2 | 109.5 | 274.3229
110-111 |  | 1 | [9 empty] | 1 | 1 | 110.5 | 272.9983
111-112 |  | 2 | [9 empty] | 2 | 2 | 111.5 | 271.5906
113-114 | 1 | [10 empty] | 1 | 1 | 113.5 | 268.5273
114-115 |  | 1 | [9 empty] | 1 | 1 | 114.5 | 266.8727
115-116 |  | 1 | [9 empty] | 1 | 1 | 115.5 | 265.1368
117-118 | 1 | [10 empty] | 1 | 1 | 117.5 | 261.4234
118-119 |  |  | 1 | [8 empty] | 1 | 1 | 118.5 | 259.4469
119-120 | 3 | [10 empty] | 3 | 3 | 119.5 | 257.3914
122-123 | 2 | 1 | [9 empty] | 3 | 3 | 122.5 | 250.7571
123-124 |  | 2 | [9 empty] | 2 | 2 | 123.5 | 248.392
125-126 |  | 1 | [9 empty] | 1 | 1 | 125.5 | 243.4355
126-127 |  | 1 | [9 empty] | 1 | 1 | 126.5 | 240.8457
127-128 |  | 2 | [9 empty] | 2 | 2 | 127.5 | 238.1824
128-129 |  | 1 | 2 | [8 empty] | 3 | 3 | 128.5 | 235.4467
129-130 |  |  | 1 | [8 empty] | 1 | 1 | 129.5 | 232.6392
132-133 |  | 2 | [9 empty] | 2 | 2 | 132.5 | 223.7951
133-134 |  | 1 | [9 empty] | 1 | 1 | 133.5 | 220.7095
134-135 |  | 2 | [9 empty] | 2 | 2 | 134.5 | 217.5566
135-136 | 2 | [10 empty] | 2 | 2 | 135.5 | 214.3375
137-138 | 1 | [10 empty] | 1 | 1 | 137.5 | 207.7045
138-139 | 2 | [10 empty] | 2 | 2 | 138.5 | 204.2925
139-140 |  | 2 | [9 empty] | 2 | 2 | 139.5 | 200.8183
141-142 |  |  | 1 | [8 empty] | 1 | 1 | 141.5 | 193.6875
143-144 |  | 2 | [9 empty] | 2 | 2 | 143.5 | 186.3208
144-145 | 2 | 1 | [9 empty] | 3 | 3 | 144.5 | 182.5517
145-146 |  | 1 | [9 empty] | 1 | 1 | 145.5 | 178.727
147-148 | 2 | 1 | 2 | [8 empty] | 5 | 5 | 147.5 | 170.9155
148-149 |  | 2 | [9 empty] | 2 | 2 | 148.5 | 166.931
149-150 |  | 2 | [9 empty] | 2 | 2 | 149.5 | 162.8957
150-151 | 2 | 2 | [9 empty] | 4 | 4 | 150.5 | 158.8108
151-152 |  | 3 | [9 empty] | 3 | 3 | 151.5 | 154.6775
152-153 |  |  | 5 | [8 empty] | 5 | 5 | 152.5 | 150.4971
153-154 | 2 | 8 | [9 empty] | 10 | 10 | 153.5 | 146.2708
154-155 | 1 | 2 | 2 | 2 | [7 empty] | 7 | 7 | 154.5 | 142
155-156 |  | 1 | [9 empty] | 1 | 1 | 155.5 | 137.6859
156-157 |  | 3 | 1 | [8 empty] | 4 | 4 | 156.5 | 133.3299
157-158 |  |  | 1 | [8 empty] | 1 | 1 | 157.5 | 128.9333
158-159 |  | 4 | 1 | [8 empty] | 5 | 5 | 158.5 | 124.4974
159-160 |  | 4 | 1 | [8 empty] | 5 | 5 | 159.5 | 120.0236
160-161 | 1 | 4 | 1 | 2 | [7 empty] | 8 | 8 | 160.5 | 115.5132
161-162 | 1 | 4 | 3 | 1 | [7 empty] | 9 | 9 | 161.5 | 110.9676
162-163 |  | 5 | 3 | [8 empty] | 8 | 8 | 162.5 | 106.3883
163-164 | 2 | 2 | 3 | 1 | [7 empty] | 8 | 8 | 163.5 | 101.7765
164-165 | 1 | 1 | 1 | 3 | [7 empty] | 6 | 6 | 164.5 | 97.1337
165-166 |  | 4 | 6 |  |  | 1 | [5 empty] | 11 | 11 | 165.5 | 92.4614
166-167 |  | 2 | 1 | 3 | [7 empty] | 6 | 6 | 166.5 | 87.7608
167-168 | 2 | 4 | 2 | 1 | 2 | [6 empty] | 11 | 11 | 167.5 | 83.0336
168-169 |  | 6 | 1 | 1 | 4 | [6 empty] | 12 | 12 | 168.5 | 78.281
169-170 |  | 1 | 4 | 1 | 5 | [6 empty] | 11 | 11 | 169.5 | 73.5046
170-171 | 1 | 5 | 4 | 3 | 6 | 7 | [5 empty] | 26 | 26 | 170.5 | 68.7058
171-172 |  |  | 6 | 3 | 6 |  |  | 2 |  |  |  | 17 | 17 | 171.5 | 63.8861
172-173 | 1 | 1 | 8 | 10 | 5 | 3 | 2 | 1 |  |  |  | 31 | 31 | 172.5 | 59.0469
173-174 |  | 1 | 2 | 7 | 5 | 4 | 1 | 1 |  |  |  | 21 | 21 | 173.5 | 54.1898
174-175 |  | 1 | 6 | 5 | 6 | 2 | 4 | 3 |  |  |  | 27 | 27 | 174.5 | 49.3161
175-176 |  | 2 | 4 | 1 | 19 | 18 | 6 | 6 | 1 |  |  | 57 | 57 | 175.5 | 44.4274
176-177 |  | 2 | 5 | 6 | 12 | 9 | 12 | 7 | 3 |  |  | 56 | 56 | 176.5 | 39.5252
177-178 |  | 1 | 4 | 6 | 9 | 19 | 14 | 18 | 1 |  |  | 72 | 72 | 177.5 | 34.6109
178-179 |  | 2 | 2 | 12 | 20 | 19 | 14 | 13 | 2 |  |  | 84 | 84 | 178.5 | 29.6861
179-180 |  | 1 | 4 | 7 | 13 | 27 | 19 | 20 | 10 |  |  | 101 | 101 | 179.5 | 24.7522
180-181 | 1 | 3 | 5 | 12 | 23 | 24 | 32 | 25 | 14 | 1 |  | 140 | 140 | 180.5 | 19.8108
181-182 | 1 | 1 | 9 | 7 | 21 | 22 | 28 | 22 | 8 | 1 |  | 120 | 120 | 181.5 | 14.8634
182-183 |  | 3 | 2 | 6 | 16 | 32 | 31 | 25 | 25 |  |  | 140 | 140 | 182.5 | 9.9115
183-184 |  |  | 4 | 11 | 25 | 35 | 30 | 30 | 11 | 5 |  | 151 | 151 | 183.5 | 4.9565
184-185 |  | 1 | 6 | 4 | 20 | 21 | 27 | 15 | 6 |  |  | 100 | 100 | 184.5 | 3.4794e-14
185-186 |  | 5 | 2 | 4 | 21 | 32 | 24 | 16 | 3 |  |  | 107 | 107 | 185.5 | 4.9565
186-187 | 1 | 2 | 2 | 5 | 15 | 19 | 18 | 10 | 4 |  |  | 76 | 76 | 186.5 | 9.9115
187-188 |  | 1 | 2 | 10 | 37 | 12 | 13 | 19 | 3 | 2 |  | 99 | 99 | 187.5 | 14.8634
188-189 | 1 | 1 | 2 | 5 | 14 | 14 | 9 | 4 | 1 |  |  | 51 | 51 | 188.5 | 19.8108
189-190 | 2 | 2 | 3 | 5 | 11 | 11 | 4 | 5 |  |  |  | 43 | 43 | 189.5 | 24.7522
190-191 |  | 2 | 5 | 4 | 11 | 14 | 6 | 1 | 1 |  |  | 44 | 44 | 190.5 | 29.6861
191-192 |  | 3 | 1 | 3 | 17 | 7 | 2 | 1 |  |  |  | 34 | 34 | 191.5 | 34.6109
192-193 |  |  |  | 4 | 8 | 13 | 3 |  |  |  |  | 28 | 28 | 192.5 | 39.5252
193-194 | 2 |  | 2 | 9 | 6 | 2 | 1 | 2 |  |  |  | 24 | 24 | 193.5 | 44.4274
194-195 |  | 1 | 5 | 7 | 5 | 2 | 3 |  |  |  |  | 23 | 23 | 194.5 | 49.3161
195-196 |  | 1 | 3 | 2 | 6 | 1 | [5 empty] | 13 | 13 | 195.5 | 54.1898
196-197 |  | 1 | 1 | 4 | 10 | [6 empty] | 16 | 16 | 196.5 | 59.0469
197-198 |  |  | 3 | 3 | 3 | [6 empty] | 9 | 9 | 197.5 | 63.8861
198-199 |  |  | 1 | 3 | 2 | [6 empty] | 6 | 6 | 198.5 | 68.7058
199-200 |  | 2 | 1 | 2 | 3 | [6 empty] | 8 | 8 | 199.5 | 73.5046
200-201 |  | 1 | 2 | 7 | 4 | 1 | [5 empty] | 15 | 15 | 200.5 | 78.281
201-202 | 2 | 4 | 4 | 1 | 2 | [6 empty] | 13 | 13 | 201.5 | 83.0336
202-203 |  | 1 | 2 | 3 | 2 | [6 empty] | 8 | 8 | 202.5 | 87.7608
203-204 |  | 1 | 2 | 2 | [7 empty] | 5 | 5 | 203.5 | 92.4614
204-205 | 2 | 4 | 1 | [8 empty] | 7 | 7 | 204.5 | 97.1337
205-206 |  |  | 1 | 4 | [7 empty] | 5 | 5 | 205.5 | 101.7765
206-207 |  | 5 | 2 | 1 | 2 | [6 empty] | 10 | 10 | 206.5 | 106.3883
207-208 | 1 | 3 | 4 | 1 | [7 empty] | 9 | 9 | 207.5 | 110.9676
208-209 | 2 | 1 | 5 | [8 empty] | 8 | 8 | 208.5 | 115.5132
209-210 |  |  | 3 | [8 empty] | 3 | 3 | 209.5 | 120.0236
210-211 |  | 4 | [9 empty] | 4 | 4 | 210.5 | 124.4974
211-212 | 1 |  |  | 2 | [7 empty] | 3 | 3 | 211.5 | 128.9333
212-213 |  | 2 | 2 | 1 | [7 empty] | 5 | 5 | 212.5 | 133.3299
213-214 |  | 2 | 1 | [8 empty] | 3 | 3 | 213.5 | 137.6859
214-215 |  | 1 | 2 | 1 | [7 empty] | 4 | 4 | 214.5 | 142
215-216 |  | 6 | 1 | 1 | [7 empty] | 8 | 8 | 215.5 | 146.2708
216-217 |  | 2 | 2 | 3 | [7 empty] | 7 | 7 | 216.5 | 150.4971
217-218 |  | 2 | [9 empty] | 2 | 2 | 217.5 | 154.6775
218-219 |  | 1 | [9 empty] | 1 | 1 | 218.5 | 158.8108
219-220 |  | 2 | [9 empty] | 2 | 2 | 219.5 | 162.8957
220-221 |  | 2 | [9 empty] | 2 | 2 | 220.5 | 166.931
221-222 |  | 2 | 2 | [8 empty] | 4 | 4 | 221.5 | 170.9155
222-223 |  | 1 | [9 empty] | 1 | 1 | 222.5 | 174.8479
223-224 |  | 1 | [9 empty] | 1 | 1 | 223.5 | 178.727
224-225 |  | 1 | [9 empty] | 1 | 1 | 224.5 | 182.5517
225-226 |  | 1 | [9 empty] | 1 | 1 | 225.5 | 186.3208
226-227 | 1 | 4 | [9 empty] | 5 | 5 | 226.5 | 190.0331
227-228 |  | 3 | 1 | [8 empty] | 4 | 4 | 227.5 | 193.6875
228-229 | 1 |  | 1 | [8 empty] | 2 | 2 | 228.5 | 197.283
229-230 | 1 | 1 | [9 empty] | 2 | 2 | 229.5 | 200.8183
230-231 | 1 | 4 | [9 empty] | 5 | 5 | 230.5 | 204.2925
231-232 | 1 | 3 | 2 | [8 empty] | 6 | 6 | 231.5 | 207.7045
232-233 |  | 1 | [9 empty] | 1 | 1 | 232.5 | 211.0531
234-235 |  | 2 | [9 empty] | 2 | 2 | 234.5 | 217.5566
235-236 | 1 | 2 | [9 empty] | 3 | 3 | 235.5 | 220.7095
236-237 | 1 | [10 empty] | 1 | 1 | 236.5 | 223.7951
237-238 |  | 1 | [9 empty] | 1 | 1 | 237.5 | 226.8125
240-241 |  | 1 | [9 empty] | 1 | 1 | 240.5 | 235.4467
242-243 | 3 | [10 empty] | 3 | 3 | 242.5 | 240.8457
243-244 | 1 | 1 | [9 empty] | 2 | 2 | 243.5 | 243.4355
247-248 |  | 1 | [9 empty] | 1 | 1 | 247.5 | 253.0459
251-252 |  | 2 | [9 empty] | 2 | 2 | 251.5 | 261.4234
252-253 |  | 1 | [9 empty] | 1 | 1 | 252.5 | 263.3202
253-254 |  | 1 | [9 empty] | 1 | 1 | 253.5 | 265.1368
255-256 |  | 2 | [9 empty] | 2 | 2 | 255.5 | 268.5273
257-258 |  | 1 | [9 empty] | 1 | 1 | 257.5 | 271.5906
258-259 | 1 | [10 empty] | 1 | 1 | 258.5 | 272.9983
260-261 | 1 | [10 empty] | 1 | 1 | 260.5 | 275.564
262-263 | 1 | [10 empty] | 1 | 1 | 262.5 | 277.7939
263-264 | 2 | [10 empty] | 2 | 2 | 263.5 | 278.7821
265-266 |  | 1 | [9 empty] | 1 | 1 | 265.5 | 280.5035
267-268 | 4 | 1 | [9 empty] | 5 | 5 | 267.5 | 281.8831
268-269 |  | 1 | [9 empty] | 1 | 1 | 268.5 | 282.4442
270-271 | 1 | 2 | [9 empty] | 3 | 3 | 270.5 | 283.3082
271-272 | 1 | [10 empty] | 1 | 1 | 271.5 | 283.6108
273-274 |  | 3 | [9 empty] | 3 | 3 | 273.5 | 283.9567
274-275 |  | 1 | [9 empty] | 1 | 1 | 274.5 | 284
276-277 | 1 | [10 empty] | 1 | 1 | 276.5 | 283.827
277-278 | 1 | [10 empty] | 1 | 1 | 277.5 | 283.6108
279-280 |  | 1 | [9 empty] | 1 | 1 | 279.5 | 282.9193
282-283 |  | 1 | [9 empty] | 1 | 1 | 282.5 | 281.2361
284-285 | 1 | [10 empty] | 1 | 1 | 284.5 | 279.6854
285-286 |  | 1 | [9 empty] | 1 | 1 | 285.5 | 278.7821
286-287 | 1 | [10 empty] | 1 | 1 | 286.5 | 277.7939
289-290 | 3 | [10 empty] | 3 | 3 | 289.5 | 274.3229
291-292 |  | 1 | [9 empty] | 1 | 1 | 291.5 | 271.5906
293-294 | 1 | [10 empty] | 1 | 1 | 293.5 | 268.5273
296-297 |  | 1 | [9 empty] | 1 | 1 | 296.5 | 263.3202
297-298 | 1 | [10 empty] | 1 | 1 | 297.5 | 261.4234
298-299 |  | 1 | [9 empty] | 1 | 1 | 298.5 | 259.4469
299-300 |  | 1 | [9 empty] | 1 | 1 | 299.5 | 257.3914
302-303 |  | 1 | [9 empty] | 1 | 1 | 302.5 | 250.7571
304-305 | 1 | [10 empty] | 1 | 1 | 304.5 | 245.9512
307-308 | 2 | 2 | [9 empty] | 4 | 4 | 307.5 | 238.1824
308-309 |  | 1 | [9 empty] | 1 | 1 | 308.5 | 235.4467
309-310 |  | 1 | [9 empty] | 1 | 1 | 309.5 | 232.6392
311-312 | 1 | [10 empty] | 1 | 1 | 311.5 | 226.8125
312-313 | 3 | 1 | [9 empty] | 4 | 4 | 312.5 | 223.7951
313-314 |  | 1 | [9 empty] | 1 | 1 | 313.5 | 220.7095
314-315 | 1 | 1 | [9 empty] | 2 | 2 | 314.5 | 217.5566
315-316 | 1 | 1 | [9 empty] | 2 | 2 | 315.5 | 214.3375
316-317 | 2 | 1 | [9 empty] | 3 | 3 | 316.5 | 211.0531
317-318 |  | 2 | [9 empty] | 2 | 2 | 317.5 | 207.7045
318-319 |  | 2 | [9 empty] | 2 | 2 | 318.5 | 204.2925
319-320 | 1 | [10 empty] | 1 | 1 | 319.5 | 200.8183
320-321 | 2 | [10 empty] | 2 | 2 | 320.5 | 197.283
322-323 |  | 1 | [9 empty] | 1 | 1 | 322.5 | 190.0331
324-325 |  | 2 | 1 | [8 empty] | 3 | 3 | 324.5 | 182.5517
325-326 | 4 | 2 | [9 empty] | 6 | 6 | 325.5 | 178.727
326-327 |  | 1 | [9 empty] | 1 | 1 | 326.5 | 174.8479
327-328 |  |  | 2 | [8 empty] | 2 | 2 | 327.5 | 170.9155
328-329 |  | 2 | [9 empty] | 2 | 2 | 328.5 | 166.931
329-330 | 1 | [10 empty] | 1 | 1 | 329.5 | 162.8957
330-331 | 2 | [10 empty] | 2 | 2 | 330.5 | 158.8108
331-332 |  | 1 | [9 empty] | 1 | 1 | 331.5 | 154.6775
332-333 | 1 | 1 | [9 empty] | 2 | 2 | 332.5 | 150.4971
333-334 |  | 2 | [9 empty] | 2 | 2 | 333.5 | 146.2708
334-335 | 1 | [10 empty] | 1 | 1 | 334.5 | 142
335-336 |  | 3 | [9 empty] | 3 | 3 | 335.5 | 137.6859
336-337 |  | 1 | [9 empty] | 1 | 1 | 336.5 | 133.3299
337-338 |  | 2 | [9 empty] | 2 | 2 | 337.5 | 128.9333
338-339 |  | 4 | [9 empty] | 4 | 4 | 338.5 | 124.4974
339-340 | 2 | 3 | [9 empty] | 5 | 5 | 339.5 | 120.0236
340-341 |  | 1 | [9 empty] | 1 | 1 | 340.5 | 115.5132
341-342 | 1 |  | 1 | [8 empty] | 2 | 2 | 341.5 | 110.9676
342-343 | 1 | 1 | 2 | 2 | [7 empty] | 6 | 6 | 342.5 | 106.3883
343-344 |  | 3 | 4 | [8 empty] | 7 | 7 | 343.5 | 101.7765
344-345 | 2 | 2 | 1 | [8 empty] | 5 | 5 | 344.5 | 97.1337
345-346 |  | 2 | 3 | 2 | [7 empty] | 7 | 7 | 345.5 | 92.4614
346-347 |  | 6 | 3 | 2 | [7 empty] | 11 | 11 | 346.5 | 87.7608
347-348 |  | 5 | 3 | 1 | [7 empty] | 9 | 9 | 347.5 | 83.0336
348-349 |  | 1 | 3 | 2 | 1 | [6 empty] | 7 | 7 | 348.5 | 78.281
349-350 |  | 1 | 3 | [8 empty] | 4 | 4 | 349.5 | 73.5046
350-351 | 1 |  | 4 | 1 | [7 empty] | 6 | 6 | 350.5 | 68.7058
351-352 |  | 2 | 6 | 5 | 1 | [6 empty] | 14 | 14 | 351.5 | 63.8861
352-353 | 2 | 1 | 2 | 2 | [7 empty] | 7 | 7 | 352.5 | 59.0469
353-354 |  | 2 | 6 | 5 | 1 | [6 empty] | 14 | 14 | 353.5 | 54.1898
354-355 |  | 1 | 2 | 2 | 2 | 3 | [5 empty] | 10 | 10 | 354.5 | 49.3161
355-356 |  | 2 | 9 | 6 |  |  | 1 |  |  |  |  | 18 | 18 | 355.5 | 44.4274
356-357 |  | 1 | 1 | 11 | 5 | 3 | 1 | 1 |  |  |  | 23 | 23 | 356.5 | 39.5252
357-358 |  | 4 | 3 | 4 | 6 | 7 | 2 |  |  |  |  | 26 | 26 | 357.5 | 34.6109
358-359 |  | 2 | 8 | 15 | 18 | 8 | 3 | 4 |  |  |  | 58 | 58 | 358.5 | 29.6861
359-360 |  | 1 | 7 | 6 | 10 | 6 | 8 | 4 |  |  |  | 42 | 42 | 359.5 | 24.7522
Grand Total | 175 | 436 | 391 | 484 | 707 | 661 | 569 | 544 | 299 | 48 | 6 | 4320
Grand Total | 175 | 436 | 391 | 484 | 707 | 661 | 569 | 544 | 299 | 48 | 6 | 4320
"weight" speed | 0 | 0 | 0 | 0.35 | 0.45 | 0.55 | 0.65 | 0.75 | 0.85 | 0.95 | 1.05
slack weight | 1002 |  |  | slack area | 228.65 | ratio | 23.19%
|  |  |  | slack speed (intake velocity) | 0.3
Inflow = area * weight speed * count
Direction | 0-0.1 | 0.1-0.2 | 0.2-0.3 | 0.3-0.4 | 0.4-0.5 | 0.5-0.6 | 0.6-0.7 | 0.7-0.8 | 0.8-0.9 | 0.9-1 | 1-1.1 | direction total
0-1 | 0 | 0 | 0 | 76.2717 | 80.2339 | 98.0637 | 154.5245 | 178.2975 | 50.5176 | 0 | 0 | 637.909
1-2 | 0 | 0 | 0 | 36.4154 | 120.3936 | 106.2734 | 96.6122 | 167.2134 | 63.1695 | 0 | 0 | 590.0774
2-3 | 0 | 0 | 0 | 45.0971 | 71.3625 | 54.513 | 64.4245 | 111.5039 | 143.2206 | 37.6635 | 0 | 527.7851
3-4 | 0 | 0 | 0 | 20.8172 | 37.9171 | 49.0692 | 57.9909 | 104.0862 | 84.2602 | 4.7087 | 0 | 358.8494
4-5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5-6 | 0 | 0 | 0 | 13.8782 | 17.8433 | 68.1516 | 83.7646 | 89.2167 | 80.0472 | 9.4173 | 5.2043 | 367.5232
6-7 | 0 | 0 | 0 | 20.8141 | 111.5039 | 130.8312 | 167.5036 | 289.9101 | 193.769 | 84.743 | 0 | 999.0749
7-8 | 0 | 0 | 0 | 31.2132 | 93.6395 | 171.6724 | 231.8692 | 479.345 | 341.1153 | 28.2405 | 0 | 1377.0951
8-9 | 0 | 0 | 0 | 48.5366 | 151.5529 | 239.7111 | 360.5573 | 252.5882 | 252.5882 | 94.1015 | 41.6028 | 1441.2385
9-10 | 0 | 0 | 0 | 51.9797 | 200.4931 | 217.8196 | 337.868 | 575.4894 | 378.7091 | 141.0877 | 51.9797 | 1955.4262
10-11 | 0 | 0 | 0 | 72.7309 | 160.3049 | 310.2196 | 443.8069 | 178.1165 | 479.4302 | 141.0089 | 0 | 1785.6179
11-12 | 0 | 0 | 0 | 218.0486 | 218.0486 | 228.4319 | 269.965 | 233.6235 | 264.7733 | 32.8803 | 0 | 1465.7713
12-13 | 0 | 0 | 0 | 166.0057 | 213.4359 | 239.1272 | 51.3827 | 29.6439 | 67.1928 | 0 | 0 | 766.7881
13-14 | 0 | 0 | 0 | 62.1983 | 179.9309 | 244.3506 | 259.9002 | 166.6027 | 264.343 | 42.206 | 0 | 1219.5318
14-15 | 0 | 0 | 0 | 207.1275 | 244.1146 | 271.2385 | 160.2773 | 258.9094 | 83.8373 | 0 | 0 | 1225.5046
15-16 | 0 | 0 | 0 | 75.8657 | 146.3123 | 178.8262 | 105.67 | 40.6423 | 0 | 0 | 0 | 547.3165
16-17 | 0 | 0 | 0 | 103.3321 | 26.5711 | 162.379 | 38.3805 | 0 | 0 | 0 | 0 | 330.6628
17-18 | 0 | 0 | 0 | 89.4405 | 373.7337 | 175.6868 | 0 | 0 | 0 | 0 | 0 | 638.861
18-19 | 0 | 0 | 0 | 192.3763 | 278.2586 | 302.3056 | 89.3176 | 0 | 0 | 0 | 0 | 862.258
19-20 | 0 | 0 | 0 | 205.8129 | 66.1541 | 161.7101 | 0 | 0 | 0 | 0 | 0 | 433.6772
20-21 | 0 | 0 | 0 | 109.5934 | 105.6794 | 0 | 0 | 0 | 0 | 0 | 0 | 215.2728
21-22 | 0 | 0 | 0 | 87.1852 | 112.0953 | 0 | 0 | 0 | 0 | 0 | 0 | 199.2806
22-23 | 0 | 0 | 0 | 92.1489 | 197.4619 | 48.2685 | 0 | 0 | 0 | 0 | 0 | 337.8792
23-24 | 0 | 0 | 0 | 97.0844 | 124.8228 | 0 | 0 | 0 | 0 | 0 | 0 | 221.9073
24-25 | 0 | 0 | 0 | 101.9904 | 43.7102 | 0 | 0 | 0 | 0 | 0 | 0 | 145.7006
25-26 | 0 | 0 | 0 | 0 | 137.3983 | 0 | 0 | 0 | 0 | 0 | 0 | 137.3983
26-27 | 0 | 0 | 0 | 111.7077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.7077
27-28 | 0 | 0 | 0 | 155.3547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155.3547
28-29 | 0 | 0 | 0 | 121.2889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.2889
29-30 | 0 | 0 | 0 | 168.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168.033
30-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31-32 | 0 | 0 | 0 | 90.2533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.2533
32-33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33-34 | 0 | 0 | 0 | 96.3802 | 61.9587 | 0 | 0 | 0 | 0 | 0 | 0 | 158.3388
34-35 | 0 | 0 | 0 | 49.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.7
35-36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36-37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37-38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38-39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39-40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40-41 | 0 | 0 | 0 | 116.8517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.8517
41-42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42-43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43-44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44-45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46-47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47-48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48-49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
49-50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50-51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51-52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
52-53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54-55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55-56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56-57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58-59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59-60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60-61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
63-64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
64-65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
66-67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67-68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
69-70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
71-72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72-73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73-74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
75-76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
77-78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78-79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79-80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
80-81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
81-82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
82-83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
83-84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
84-85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
87-88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
89-90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90-91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91-92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
92-93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95-96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
99-100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103-104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104-105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
105-106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
107-108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108-109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109-110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110-111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111-112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
113-114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
114-115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
115-116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
117-118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
118-119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
119-120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
122-123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
123-124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
125-126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
126-127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
127-128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
128-129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
129-130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
132-133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
133-134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
134-135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
135-136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
137-138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
138-139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
139-140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
141-142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
143-144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
144-145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
145-146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
147-148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
148-149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149-150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150-151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
151-152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
152-153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153-154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154-155 | 0 | 0 | 0 | 99.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.4
155-156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156-157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157-158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
158-159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
159-160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160-161 | 0 | 0 | 0 | 80.8592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.8592
161-162 | 0 | 0 | 0 | 38.8387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.8387
162-163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
163-164 | 0 | 0 | 0 | 35.6218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.6218
164-165 | 0 | 0 | 0 | 101.9904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.9904
165-166 | 0 | 0 | 0 | 0 | 0 | 50.8537 | 0 | 0 | 0 | 0 | 0 | 50.8537
166-167 | 0 | 0 | 0 | 92.1489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.1489
167-168 | 0 | 0 | 0 | 29.0617 | 74.7302 | 0 | 0 | 0 | 0 | 0 | 0 | 103.792
168-169 | 0 | 0 | 0 | 27.3984 | 140.9058 | 0 | 0 | 0 | 0 | 0 | 0 | 168.3042
169-170 | 0 | 0 | 0 | 25.7266 | 165.3854 | 0 | 0 | 0 | 0 | 0 | 0 | 191.112
170-171 | 0 | 0 | 0 | 72.1411 | 185.5057 | 264.5174 | 0 | 0 | 0 | 0 | 0 | 522.1642
171-172 | 0 | 0 | 0 | 67.0804 | 172.4925 | 0 | 0 | 95.8291 | 0 | 0 | 0 | 335.402
172-173 | 0 | 0 | 0 | 206.6642 | 132.8556 | 97.4274 | 76.761 | 44.2852 | 0 | 0 | 0 | 557.9934
173-174 | 0 | 0 | 0 | 132.7649 | 121.9269 | 119.2175 | 35.2233 | 40.6423 | 0 | 0 | 0 | 449.775
174-175 | 0 | 0 | 0 | 86.3031 | 133.1534 | 54.2477 | 128.2218 | 110.9612 | 0 | 0 | 0 | 512.8873
175-176 | 0 | 0 | 0 | 15.5496 | 379.8542 | 439.8311 | 173.2668 | 199.9232 | 37.7633 | 0 | 0 | 1246.1882
176-177 | 0 | 0 | 0 | 83.0028 | 213.4359 | 195.6495 | 308.2963 | 207.5071 | 100.7892 | 0 | 0 | 1108.6808
177-178 | 0 | 0 | 0 | 72.6829 | 140.1741 | 361.6838 | 314.9591 | 467.2471 | 29.4193 | 0 | 0 | 1386.1663
178-179 | 0 | 0 | 0 | 124.6816 | 267.1748 | 310.2196 | 270.1434 | 289.4393 | 50.4663 | 0 | 0 | 1312.1249
179-180 | 0 | 0 | 0 | 60.643 | 144.8006 | 367.5706 | 305.6901 | 371.2835 | 210.394 | 0 | 0 | 1460.3816
180-181 | 0 | 0 | 0 | 83.2055 | 205.0422 | 261.5031 | 412.0654 | 371.4532 | 235.749 | 18.8203 | 0 | 1587.8387
181-182 | 0 | 0 | 0 | 36.4154 | 140.4592 | 179.8473 | 270.5141 | 245.2463 | 101.0712 | 14.1202 | 0 | 987.6737
182-183 | 0 | 0 | 0 | 20.8141 | 71.3625 | 174.4416 | 199.7159 | 185.8398 | 210.6185 | 0 | 0 | 862.7923
183-184 | 0 | 0 | 0 | 19.0825 | 55.7604 | 95.4123 | 96.6514 | 111.5209 | 46.3431 | 23.5433 | 0 | 448.3139
184-185 | 0 | 0 | 0 | 4.8712e-14 | 3.1315e-13 | 4.0187e-13 | 6.1064e-13 | 3.9143e-13 | 1.7745e-13 | 0 | 0 | 1.9433e-12
185-186 | 0 | 0 | 0 | 6.9391 | 46.8388 | 87.2341 | 77.3211 | 59.4778 | 12.639 | 0 | 0 | 290.4499
186-187 | 0 | 0 | 0 | 17.345 | 66.9023 | 103.5747 | 115.964 | 74.3359 | 33.699 | 0 | 0 | 411.821
187-188 | 0 | 0 | 0 | 52.0219 | 247.4758 | 98.0985 | 125.5958 | 211.8036 | 37.9017 | 28.2405 | 0 | 801.1379
188-189 | 0 | 0 | 0 | 34.669 | 124.8083 | 152.5435 | 115.8934 | 59.4325 | 16.8392 | 0 | 0 | 504.1858
189-190 | 0 | 0 | 0 | 43.3164 | 122.5235 | 149.751 | 64.3558 | 92.8209 | 0 | 0 | 0 | 472.7676
190-191 | 0 | 0 | 0 | 41.5605 | 146.9461 | 228.5828 | 115.7757 | 22.2646 | 25.2332 | 0 | 0 | 580.3629
191-192 | 0 | 0 | 0 | 36.3414 | 264.7733 | 133.2519 | 44.9942 | 25.9582 | 0 | 0 | 0 | 505.319
192-193 | 0 | 0 | 0 | 55.3352 | 142.2906 | 282.6049 | 77.0741 | 0 | 0 | 0 | 0 | 557.3048
193-194 | 0 | 0 | 0 | 139.9463 | 119.9539 | 48.8701 | 28.8778 | 66.6411 | 0 | 0 | 0 | 404.2892
194-195 | 0 | 0 | 0 | 120.8244 | 110.9612 | 54.2477 | 96.1664 | 0 | 0 | 0 | 0 | 382.1996
195-196 | 0 | 0 | 0 | 37.9328 | 146.3123 | 29.8044 | 0 | 0 | 0 | 0 | 0 | 214.0495
196-197 | 0 | 0 | 0 | 82.6657 | 265.7111 | 0 | 0 | 0 | 0 | 0 | 0 | 348.3768
197-198 | 0 | 0 | 0 | 67.0804 | 86.2462 | 0 | 0 | 0 | 0 | 0 | 0 | 153.3266
198-199 | 0 | 0 | 0 | 72.1411 | 61.8352 | 0 | 0 | 0 | 0 | 0 | 0 | 133.9763
199-200 | 0 | 0 | 0 | 51.4532 | 99.2312 | 0 | 0 | 0 | 0 | 0 | 0 | 150.6844
200-201 | 0 | 0 | 0 | 191.7885 | 140.9058 | 43.0546 | 0 | 0 | 0 | 0 | 0 | 375.7488
201-202 | 0 | 0 | 0 | 29.0617 | 74.7302 | 0 | 0 | 0 | 0 | 0 | 0 | 103.792
202-203 | 0 | 0 | 0 | 92.1489 | 78.9847 | 0 | 0 | 0 | 0 | 0 | 0 | 171.1336
203-204 | 0 | 0 | 0 | 64.7229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.7229
204-205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
205-206 | 0 | 0 | 0 | 142.4871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142.4871
206-207 | 0 | 0 | 0 | 37.2359 | 95.7494 | 0 | 0 | 0 | 0 | 0 | 0 | 132.9853
207-208 | 0 | 0 | 0 | 38.8387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.8387
208-209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
209-210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
210-211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
211-212 | 0 | 0 | 0 | 90.2533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.2533
212-213 | 0 | 0 | 0 | 46.6655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.6655
213-214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
214-215 | 0 | 0 | 0 | 49.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.7
215-216 | 0 | 0 | 0 | 51.1948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.1948
216-217 | 0 | 0 | 0 | 158.0219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158.0219
217-218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
218-219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
219-220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220-221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
221-222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
222-223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
223-224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
224-225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
225-226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
226-227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
227-228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
228-229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
229-230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
230-231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
231-232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
232-233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
234-235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
235-236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
236-237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
237-238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
240-241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242-243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
243-244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247-248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
251-252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
252-253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
253-254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
255-256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257-258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
258-259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
260-261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
262-263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
263-264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
265-266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
267-268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
268-269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
270-271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
271-272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
273-274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
274-275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
276-277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
277-278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
279-280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
282-283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
284-285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
285-286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
286-287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
289-290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
291-292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
293-294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
296-297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297-298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
298-299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
299-300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
302-303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
304-305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
307-308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
308-309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
309-310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311-312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
312-313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313-314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314-315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
315-316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
316-317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
317-318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
318-319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
319-320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
320-321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
322-323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
324-325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
325-326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
326-327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
327-328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
328-329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
329-330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
330-331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
331-332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
332-333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333-334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
334-335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
335-336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
336-337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
337-338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
338-339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
339-340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
340-341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
341-342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
342-343 | 0 | 0 | 0 | 74.4718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.4718
343-344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
344-345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
345-346 | 0 | 0 | 0 | 64.7229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.7229
346-347 | 0 | 0 | 0 | 61.4326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.4326
347-348 | 0 | 0 | 0 | 29.0617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.0617
348-349 | 0 | 0 | 0 | 54.7967 | 35.2265 | 0 | 0 | 0 | 0 | 0 | 0 | 90.0232
349-350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350-351 | 0 | 0 | 0 | 24.047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.047
351-352 | 0 | 0 | 0 | 111.8007 | 28.7487 | 0 | 0 | 0 | 0 | 0 | 0 | 140.5494
352-353 | 0 | 0 | 0 | 41.3328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.3328
353-354 | 0 | 0 | 0 | 94.8321 | 24.3854 | 0 | 0 | 0 | 0 | 0 | 0 | 119.2175
354-355 | 0 | 0 | 0 | 34.5213 | 44.3845 | 81.3715 | 0 | 0 | 0 | 0 | 0 | 160.2773
355-356 | 0 | 0 | 0 | 93.2975 | 0 | 0 | 28.8778 | 0 | 0 | 0 | 0 | 122.1753
356-357 | 0 | 0 | 0 | 152.1719 | 88.9316 | 65.2165 | 25.6914 | 29.6439 | 0 | 0 | 0 | 361.6552
357-358 | 0 | 0 | 0 | 48.4553 | 93.4494 | 133.2519 | 44.9942 | 0 | 0 | 0 | 0 | 320.1508
358-359 | 0 | 0 | 0 | 155.8519 | 240.4573 | 130.6188 | 57.8879 | 89.0583 | 0 | 0 | 0 | 673.8741
359-360 | 0 | 0 | 0 | 51.9797 | 111.385 | 81.6824 | 128.7116 | 74.2567 | 0 | 0 | 0 | 448.0154
draw excl slacks | 43568.0408 |  |  |  | 1.5 | 2.5 | 3.5 | 4.5 | 5.5 | 6.5 | 7.5
slacks | 68732.19 |  |  |  | 53.85 | 52 | 50.76 | 50.23 | 50.3 | 50.94 | 52.21
total draw | 112300.2308
divisor | 2235.6
Average | 50.2327 | m2

## SZ1 - northern intake
Days | DateTime | Velocity at 2.04m above bed (m/s) | Direction at 2.04m above bed (deg)
0 | 2018-11-13 16:40 | 0.76501 | 359.7753 | Bin
0.0069444 | 2018-11-13 16:50 | 0.6879 | 14.8241 | 0.1
0.013889 | 2018-11-13 17:00 | 0.86808 | 3.9634 | 0.2
0.020833 | 2018-11-13 17:10 | 0.86808 | 3.9634 | 0.3
0.027778 | 2018-11-13 17:20 | 0.76509 | 5.9267 | 0.4
0.034722 | 2018-11-13 17:30 | 0.7931 | 5.0636 | 0.5
0.041667 | 2018-11-13 17:40 | 0.71917 | 7.5104 | 0.6
0.048611 | 2018-11-13 17:50 | 0.64614 | 10.1621 | 0.7
0.055556 | 2018-11-13 18:00 | 0.67231 | 6.4908 | 0.8
0.0625 | 2018-11-13 18:10 | 0.67231 | 6.4908 | 0.9
0.069444 | 2018-11-13 18:20 | 0.57118 | 6.9384 | 1
0.076389 | 2018-11-13 18:30 | 0.52016 | 9.5166 | 1.1
0.083333 | 2018-11-13 18:40 | 0.55509 | 7.7652 | 1.2
0.090278 | 2018-11-13 18:50 | 0.54748 | 10.0989 | 1.3
0.097222 | 2018-11-13 19:00 | 0.34465 | 351.6583
0.10417 | 2018-11-13 19:10 | 0.34465 | 351.6583
0.11111 | 2018-11-13 19:20 | 0.43544 | 6.0641
0.11806 | 2018-11-13 19:30 | 0.31681 | 8.8974
0.125 | 2018-11-13 19:40 | 0.31552 | 8.5667
0.13194 | 2018-11-13 19:50 | 0.25786 | 355.3286
0.13889 | 2018-11-13 20:00 | 0.19922 | 353.6598 |  | Bin | Frequency | Cumulative %
0.14583 | 2018-11-13 20:10 | 0.19922 | 353.6598 |  | 0.1 | 198 | 4.644%
0.15278 | 2018-11-13 20:20 | 0.19901 | 322.5543 |  | 0.2 | 384 | 13.65%
0.15972 | 2018-11-13 20:30 | 0.090554 | 276.3402 |  | 0.3 | 351 | 21.88%
0.16667 | 2018-11-13 20:40 | 0.016401 | 307.5686 |  | 0.4 | 494 | 33.47%
0.17361 | 2018-11-13 20:50 | 0.10328 | 223.4306 |  | 0.5 | 662 | 48.99%
0.18056 | 2018-11-13 21:00 | 0.1365 | 230.9469 |  | 0.6 | 802 | 67.8%
0.1875 | 2018-11-13 21:10 | 0.1365 | 230.9469 |  | 0.7 | 601 | 81.89%
0.19444 | 2018-11-13 21:20 | 0.33116 | 199.584 |  | 0.8 | 445 | 92.33%
0.20139 | 2018-11-13 21:30 | 0.33568 | 194.4916 |  | 0.9 | 235 | 97.84%
0.20833 | 2018-11-13 21:40 | 0.4361 | 194.6098 |  | 1 | 77 | 99.65%
0.21528 | 2018-11-13 21:50 | 0.44952 | 191.8099 |  | 1.1 | 9 | 99.86%
0.22222 | 2018-11-13 22:00 | 0.54615 | 189.9108 |  | 1.2 | 6 | 100%
0.22917 | 2018-11-13 22:10 | 0.54615 | 189.9108 |  | 1.3 | 0 | 100%
0.23611 | 2018-11-13 22:20 | 0.55905 | 188.4345 |  | More | 0 | 100%
0.24306 | 2018-11-13 22:30 | 0.55417 | 183.7247
0.25 | 2018-11-13 22:40 | 0.60878 | 189.7408
0.25694 | 2018-11-13 22:50 | 0.62973 | 191.078
0.26389 | 2018-11-13 23:00 | 0.54947 | 185.4305
0.27083 | 2018-11-13 23:10 | 0.54947 | 185.4305
0.27778 | 2018-11-13 23:20 | 0.53981 | 185.8479
0.28472 | 2018-11-13 23:30 | 0.64351 | 188.7597
0.29167 | 2018-11-13 23:40 | 0.62143 | 187.5825
0.29861 | 2018-11-13 23:50 | 0.66273 | 182.6811
0.30556 | 2018-11-14 | 0.66013 | 181.1284
0.3125 | 2018-11-14 00:10 | 0.66013 | 181.1284
0.31944 | 2018-11-14 00:20 | 0.59142 | 183.9752
0.32639 | 2018-11-14 00:30 | 0.57583 | 176.914
0.33333 | 2018-11-14 00:40 | 0.57519 | 183.6882
0.34028 | 2018-11-14 00:50 | 0.48911 | 183.8686
0.34722 | 2018-11-14 01:00 | 0.46328 | 181.9792
0.35417 | 2018-11-14 01:10 | 0.46328 | 181.9792
0.36111 | 2018-11-14 01:20 | 0.42329 | 175.5286
0.36806 | 2018-11-14 01:30 | 0.37429 | 175.2491
0.375 | 2018-11-14 01:40 | 0.29506 | 181.1652
0.38194 | 2018-11-14 01:50 | 0.34634 | 172.0337
0.38889 | 2018-11-14 02:00 | 0.28458 | 189.0982
0.39583 | 2018-11-14 02:10 | 0.28458 | 189.0982
0.40278 | 2018-11-14 02:20 | 0.132 | 155.3764
0.40972 | 2018-11-14 02:30 | 0.039623 | 137.0454
0.41667 | 2018-11-14 02:40 | 0.098082 | 69.7174
0.42361 | 2018-11-14 02:50 | 0.1506 | 56.0989
0.43056 | 2018-11-14 03:00 | 0.2783 | 15.6343
0.4375 | 2018-11-14 03:10 | 0.2783 | 15.6343
0.44444 | 2018-11-14 03:20 | 0.51261 | 18.1875
0.45139 | 2018-11-14 03:30 | 0.34301 | 26.4903
0.45833 | 2018-11-14 03:40 | 0.42991 | 21.1332
0.46528 | 2018-11-14 03:50 | 0.50302 | 14.0362
0.47222 | 2018-11-14 04:00 | 0.55068 | 12.7996
0.47917 | 2018-11-14 04:10 | 0.55068 | 12.7996
0.48611 | 2018-11-14 04:20 | 0.69958 | 4.9201
0.49306 | 2018-11-14 04:30 | 0.70105 | 6.8817
0.5 | 2018-11-14 04:40 | 0.75713 | 10.271
0.50694 | 2018-11-14 04:50 | 0.6923 | 6.3859
0.51389 | 2018-11-14 05:00 | 0.612 | 0
0.52083 | 2018-11-14 05:10 | 0.612 | 0
0.52778 | 2018-11-14 05:20 | 0.72432 | 6.2616
0.53472 | 2018-11-14 05:30 | 0.80343 | 7.7973
0.54167 | 2018-11-14 05:40 | 0.74633 | 7.4678
0.54861 | 2018-11-14 05:50 | 0.74918 | 6.053
0.55556 | 2018-11-14 06:00 | 0.69123 | 13.8955
0.5625 | 2018-11-14 06:10 | 0.69123 | 13.8955
0.56944 | 2018-11-14 06:20 | 0.60518 | 7.5008
0.57639 | 2018-11-14 06:30 | 0.68935 | 8.9294
0.58333 | 2018-11-14 06:40 | 0.69279 | 9.136
0.59028 | 2018-11-14 06:50 | 0.68722 | 8.8729
0.59722 | 2018-11-14 07:00 | 0.65205 | 3.2529
0.60417 | 2018-11-14 07:10 | 0.65205 | 3.2529
0.61111 | 2018-11-14 07:20 | 0.52036 | 6.5104
0.61806 | 2018-11-14 07:30 | 0.49415 | 1.3915
0.625 | 2018-11-14 07:40 | 0.44282 | 3.4956
0.63194 | 2018-11-14 07:50 | 0.45189 | 6.4802
0.63889 | 2018-11-14 08:00 | 0.39066 | 11.3675
0.64583 | 2018-11-14 08:10 | 0.39066 | 11.3675
0.65278 | 2018-11-14 08:20 | 0.36479 | 14.6077
0.65972 | 2018-11-14 08:30 | 0.30138 | 8.5872
0.66667 | 2018-11-14 08:40 | 0.30636 | 14.9435
0.67361 | 2018-11-14 08:50 | 0.32757 | 12.3391
0.68056 | 2018-11-14 09:00 | 0.15088 | 19.756
0.6875 | 2018-11-14 09:10 | 0.15088 | 19.756
0.69444 | 2018-11-14 09:20 | 0.064 | 0
0.70139 | 2018-11-14 09:30 | 0.034713 | 228.5035
0.70833 | 2018-11-14 09:40 | 0.014866 | 312.2737
0.71528 | 2018-11-14 09:50 | 0.076026 | 271.5074
0.72222 | 2018-11-14 10:00 | 0.11321 | 212.0054
0.72917 | 2018-11-14 10:10 | 0.11321 | 212.0054
0.73611 | 2018-11-14 10:20 | 0.30373 | 211.1255
0.74306 | 2018-11-14 10:30 | 0.2918 | 194.8935
0.75 | 2018-11-14 10:40 | 0.31718 | 198.3778
0.75694 | 2018-11-14 10:50 | 0.44826 | 185.7615
0.76389 | 2018-11-14 11:00 | 0.40244 | 184.8464
0.77083 | 2018-11-14 11:10 | 0.40244 | 184.8464
0.77778 | 2018-11-14 11:20 | 0.43376 | 185.1586
0.78472 | 2018-11-14 11:30 | 0.4805 | 185.853
0.79167 | 2018-11-14 11:40 | 0.46709 | 181.1041
0.79861 | 2018-11-14 11:50 | 0.46857 | 186.0026
0.80556 | 2018-11-14 12:00 | 0.49676 | 187.0535
0.8125 | 2018-11-14 12:10 | 0.49676 | 187.0535
0.81944 | 2018-11-14 12:20 | 0.52584 | 184.7998
0.82639 | 2018-11-14 12:30 | 0.4457 | 186.3118
0.83333 | 2018-11-14 12:40 | 0.48104 | 189.8148
0.84028 | 2018-11-14 12:50 | 0.46504 | 179.2607
0.84722 | 2018-11-14 13:00 | 0.47727 | 181.9212
0.85417 | 2018-11-14 13:10 | 0.47727 | 181.9212
0.86111 | 2018-11-14 13:20 | 0.49505 | 179.1898
0.86806 | 2018-11-14 13:30 | 0.39844 | 186.3402
0.875 | 2018-11-14 13:40 | 0.37986 | 193.0851
0.88194 | 2018-11-14 13:50 | 0.33654 | 191.3099
0.88889 | 2018-11-14 14:00 | 0.32855 | 183.3153
0.89583 | 2018-11-14 14:10 | 0.32855 | 183.3153
0.90278 | 2018-11-14 14:20 | 0.27835 | 169.8609
0.90972 | 2018-11-14 14:30 | 0.22194 | 170.665
0.91667 | 2018-11-14 14:40 | 0.12706 | 181.804
0.92361 | 2018-11-14 14:50 | 0.16471 | 158.2632
0.93056 | 2018-11-14 15:00 | 0.074411 | 138.8141
0.9375 | 2018-11-14 15:10 | 0.074411 | 138.8141
0.94444 | 2018-11-14 15:20 | 0.18768 | 48.2397
0.95139 | 2018-11-14 15:30 | 0.21232 | 23.3049
0.95833 | 2018-11-14 15:40 | 0.2764 | 23.2258
0.96528 | 2018-11-14 15:50 | 0.28727 | 21.6533
0.97222 | 2018-11-14 16:00 | 0.29585 | 22.6646
0.97917 | 2018-11-14 16:10 | 0.29585 | 22.6646
0.98611 | 2018-11-14 16:20 | 0.4113 | 7.2632
0.99306 | 2018-11-14 16:30 | 0.43666 | 10.0232
1 | 2018-11-14 16:40 | 0.48409 | 8.3142
1.0069 | 2018-11-14 16:50 | 0.54105 | 9.8976
1.0139 | 2018-11-14 17:00 | 0.61677 | 13.7884
1.0208 | 2018-11-14 17:10 | 0.61677 | 13.7884
1.0278 | 2018-11-14 17:20 | 0.69994 | 7.4702
1.0347 | 2018-11-14 17:30 | 0.75074 | 10.9807
1.0417 | 2018-11-14 17:40 | 0.668 | 6.2739
1.0486 | 2018-11-14 17:50 | 0.75948 | 2.0373
1.0556 | 2018-11-14 18:00 | 0.61798 | 11.7645
1.0625 | 2018-11-14 18:10 | 0.61798 | 11.7645
1.0694 | 2018-11-14 18:20 | 0.61484 | 7.1944
1.0764 | 2018-11-14 18:30 | 0.56064 | 7.3785
1.0833 | 2018-11-14 18:40 | 0.58342 | 15.2034
1.0903 | 2018-11-14 18:50 | 0.48381 | 3.3178
1.0972 | 2018-11-14 19:00 | 0.56734 | 3.9417
1.1042 | 2018-11-14 19:10 | 0.56734 | 3.9417
1.1111 | 2018-11-14 19:20 | 0.48192 | 6.3139
1.1181 | 2018-11-14 19:30 | 0.47859 | 4.6742
1.125 | 2018-11-14 19:40 | 0.39018 | 358.2376
1.1319 | 2018-11-14 19:50 | 0.34271 | 3.6806
1.1389 | 2018-11-14 20:00 | 0.26831 | 9.0059
1.1458 | 2018-11-14 20:10 | 0.26831 | 9.0059
1.1528 | 2018-11-14 20:20 | 0.23405 | 358.7759
1.1597 | 2018-11-14 20:30 | 0.27791 | 349.2157
1.1667 | 2018-11-14 20:40 | 0.14338 | 10.4478
1.1736 | 2018-11-14 20:50 | 0.12932 | 328.2764
1.1806 | 2018-11-14 21:00 | 0.16362 | 339.239
1.1875 | 2018-11-14 21:10 | 0.16362 | 339.239
1.1944 | 2018-11-14 21:20 | 0.11704 | 268.5312
1.2014 | 2018-11-14 21:30 | 0.11165 | 210.6997
1.2083 | 2018-11-14 21:40 | 0.15654 | 221.6335
1.2153 | 2018-11-14 21:50 | 0.2381 | 204.3046
1.2222 | 2018-11-14 22:00 | 0.24014 | 194.9622
1.2292 | 2018-11-14 22:10 | 0.24014 | 194.9622
1.2361 | 2018-11-14 22:20 | 0.41521 | 188.1691
1.2431 | 2018-11-14 22:30 | 0.3323 | 186.7401
1.25 | 2018-11-14 22:40 | 0.46036 | 190.2603
1.2569 | 2018-11-14 22:50 | 0.39456 | 183.0509
1.2639 | 2018-11-14 23:00 | 0.47024 | 187.6993
1.2708 | 2018-11-14 23:10 | 0.47024 | 187.6993
1.2778 | 2018-11-14 23:20 | 0.49877 | 184.8304
1.2847 | 2018-11-14 23:30 | 0.49132 | 184.2019
1.2917 | 2018-11-14 23:40 | 0.48612 | 183.8925
1.2986 | 2018-11-14 23:50 | 0.57835 | 181.9818
1.3056 | 2018-11-15 | 0.51186 | 186.0559
1.3125 | 2018-11-15 00:10 | 0.51186 | 186.0559
1.3194 | 2018-11-15 00:20 | 0.57232 | 181.9025
1.3264 | 2018-11-15 00:30 | 0.66569 | 186.036
1.3333 | 2018-11-15 00:40 | 0.59721 | 178.4648
1.3403 | 2018-11-15 00:50 | 0.46852 | 182.6914
1.3472 | 2018-11-15 01:00 | 0.46505 | 180.8625
1.3542 | 2018-11-15 01:10 | 0.46505 | 180.8625
1.3611 | 2018-11-15 01:20 | 0.48042 | 187.7759
1.3681 | 2018-11-15 01:30 | 0.5252 | 185.2438
1.375 | 2018-11-15 01:40 | 0.42147 | 172.6389
1.3819 | 2018-11-15 01:50 | 0.50743 | 182.3718
1.3889 | 2018-11-15 02:00 | 0.51742 | 185.5453
1.3958 | 2018-11-15 02:10 | 0.51742 | 185.5453
1.4028 | 2018-11-15 02:20 | 0.45124 | 173.127
1.4097 | 2018-11-15 02:30 | 0.307 | 186.5463
1.4167 | 2018-11-15 02:40 | 0.21106 | 181.3575
1.4236 | 2018-11-15 02:50 | 0.23559 | 161.1805
1.4306 | 2018-11-15 03:00 | 0.17424 | 161.2531
1.4375 | 2018-11-15 03:10 | 0.17424 | 161.2531
1.4444 | 2018-11-15 03:20 | 0.084593 | 186.789
1.4514 | 2018-11-15 03:30 | 0.080777 | 105.0685
1.4583 | 2018-11-15 03:40 | 0.001 | 180
1.4653 | 2018-11-15 03:50 | 0.11243 | 44.6397
1.4722 | 2018-11-15 04:00 | 0.2128 | 36.9776
1.4792 | 2018-11-15 04:10 | 0.2128 | 36.9776
1.4861 | 2018-11-15 04:20 | 0.29692 | 11.4613
1.4931 | 2018-11-15 04:30 | 0.35452 | 29.0232
1.5 | 2018-11-15 04:40 | 0.44239 | 22.7394
1.5069 | 2018-11-15 04:50 | 0.46265 | 11.7228
1.5139 | 2018-11-15 05:00 | 0.39 | 14.25
1.5208 | 2018-11-15 05:10 | 0.39 | 14.25
1.5278 | 2018-11-15 05:20 | 0.5329 | 12.1323
1.5347 | 2018-11-15 05:30 | 0.585 | 13.8462
1.5417 | 2018-11-15 05:40 | 0.4966 | 10.6764
1.5486 | 2018-11-15 05:50 | 0.66781 | 6.8803
1.5556 | 2018-11-15 06:00 | 0.56014 | 11.9519
1.5625 | 2018-11-15 06:10 | 0.56014 | 11.9519
1.5694 | 2018-11-15 06:20 | 0.65119 | 9.6359
1.5764 | 2018-11-15 06:30 | 0.57482 | 14.3022
1.5833 | 2018-11-15 06:40 | 0.55473 | 5.69
1.5903 | 2018-11-15 06:50 | 0.56239 | 12.5288
1.5972 | 2018-11-15 07:00 | 0.63122 | 7.3727
1.6042 | 2018-11-15 07:10 | 0.63122 | 7.3727
1.6111 | 2018-11-15 07:20 | 0.61306 | 9.8618
1.6181 | 2018-11-15 07:30 | 0.52467 | 14.9103
1.625 | 2018-11-15 07:40 | 0.46543 | 12.1549
1.6319 | 2018-11-15 07:50 | 0.44016 | 1.5622
1.6389 | 2018-11-15 08:00 | 0.41302 | 4.0263
1.6458 | 2018-11-15 08:10 | 0.41302 | 4.0263
1.6528 | 2018-11-15 08:20 | 0.31951 | 5.5678
1.6597 | 2018-11-15 08:30 | 0.34484 | 3.9909
1.6667 | 2018-11-15 08:40 | 0.33373 | 356.2202
1.6736 | 2018-11-15 08:50 | 0.33522 | 14.8654
1.6806 | 2018-11-15 09:00 | 0.31769 | 3.7901
1.6875 | 2018-11-15 09:10 | 0.31769 | 3.7901
1.6944 | 2018-11-15 09:20 | 0.2431 | 358.35
1.7014 | 2018-11-15 09:30 | 0.20747 | 3.8692
1.7083 | 2018-11-15 09:40 | 0.17142 | 7.3738
1.7153 | 2018-11-15 09:50 | 0.12243 | 317.3171
1.7222 | 2018-11-15 10:00 | 0.10218 | 273.3665
1.7292 | 2018-11-15 10:10 | 0.10218 | 273.3665
1.7361 | 2018-11-15 10:20 | 0.11075 | 219.8718
1.7431 | 2018-11-15 10:30 | 0.12183 | 221.6726
1.75 | 2018-11-15 10:40 | 0.10255 | 226.1853
1.7569 | 2018-11-15 10:50 | 0.23249 | 201.7099
1.7639 | 2018-11-15 11:00 | 0.28265 | 206.0211
1.7708 | 2018-11-15 11:10 | 0.28265 | 206.0211
1.7778 | 2018-11-15 11:20 | 0.3474 | 195.3564
1.7847 | 2018-11-15 11:30 | 0.36337 | 193.0419
1.7917 | 2018-11-15 11:40 | 0.4359 | 183.6829
1.7986 | 2018-11-15 11:50 | 0.44506 | 187.7478
1.8056 | 2018-11-15 12:00 | 0.43793 | 191.5922
1.8125 | 2018-11-15 12:10 | 0.43793 | 191.5922
1.8194 | 2018-11-15 12:20 | 0.43214 | 186.9112
1.8264 | 2018-11-15 12:30 | 0.50483 | 190.7312
1.8333 | 2018-11-15 12:40 | 0.45619 | 181.633
1.8403 | 2018-11-15 12:50 | 0.53118 | 178.4897
1.8472 | 2018-11-15 13:00 | 0.59586 | 184.5241
1.8542 | 2018-11-15 13:10 | 0.59586 | 184.5241
1.8611 | 2018-11-15 13:20 | 0.59108 | 180.9694
1.8681 | 2018-11-15 13:30 | 0.61045 | 183.9452
1.875 | 2018-11-15 13:40 | 0.61356 | 185.2367
1.8819 | 2018-11-15 13:50 | 0.59334 | 181.9317
1.8889 | 2018-11-15 14:00 | 0.65712 | 185.5891
1.8958 | 2018-11-15 14:10 | 0.65712 | 185.5891
1.9028 | 2018-11-15 14:20 | 0.55309 | 175.0213
1.9097 | 2018-11-15 14:30 | 0.37553 | 183.0529
1.9167 | 2018-11-15 14:40 | 0.39341 | 182.6224
1.9236 | 2018-11-15 14:50 | 0.49125 | 184.0856
1.9306 | 2018-11-15 15:00 | 0.49554 | 184.514
1.9375 | 2018-11-15 15:10 | 0.49554 | 184.514
1.9444 | 2018-11-15 15:20 | 0.30303 | 179.2437
1.9514 | 2018-11-15 15:30 | 0.29931 | 185.3677
1.9583 | 2018-11-15 15:40 | 0.25111 | 160.6992
1.9653 | 2018-11-15 15:50 | 0.25362 | 154.5464
1.9722 | 2018-11-15 16:00 | 0.14187 | 139.5739
1.9792 | 2018-11-15 16:10 | 0.14187 | 139.5739
1.9861 | 2018-11-15 16:20 | 0.070612 | 77.7352
1.9931 | 2018-11-15 16:30 | 0.12043 | 54.4623
2 | 2018-11-15 16:40 | 0.11739 | 69.5582
2.0069 | 2018-11-15 16:50 | 0.14882 | 41.1859
2.0139 | 2018-11-15 17:00 | 0.2401 | 21.7571
2.0208 | 2018-11-15 17:10 | 0.2401 | 21.7571
2.0278 | 2018-11-15 17:20 | 0.30897 | 17.9072
2.0347 | 2018-11-15 17:30 | 0.39336 | 6.2759
2.0417 | 2018-11-15 17:40 | 0.41869 | 18.5215
2.0486 | 2018-11-15 17:50 | 0.39262 | 11.3099
2.0556 | 2018-11-15 18:00 | 0.45348 | 10.4179
2.0625 | 2018-11-15 18:10 | 0.45348 | 10.4179
2.0694 | 2018-11-15 18:20 | 0.42481 | 9.4845
2.0764 | 2018-11-15 18:30 | 0.5719 | 3.2076
2.0833 | 2018-11-15 18:40 | 0.47742 | 2.4009
2.0903 | 2018-11-15 18:50 | 0.51693 | 6.1076
2.0972 | 2018-11-15 19:00 | 0.41427 | 2.075
2.1042 | 2018-11-15 19:10 | 0.41427 | 2.075
2.1111 | 2018-11-15 19:20 | 0.524 | 0
2.1181 | 2018-11-15 19:30 | 0.58307 | 359.1156
2.125 | 2018-11-15 19:40 | 0.51859 | 10.4432
2.1319 | 2018-11-15 19:50 | 0.55237 | 15.2187
2.1389 | 2018-11-15 20:00 | 0.44196 | 7.6717
2.1458 | 2018-11-15 20:10 | 0.44196 | 7.6717
2.1528 | 2018-11-15 20:20 | 0.43278 | 12.816
2.1597 | 2018-11-15 20:30 | 0.45848 | 357.3747
2.1667 | 2018-11-15 20:40 | 0.38659 | 354.8056
2.1736 | 2018-11-15 20:50 | 0.39812 | 11.5922
2.1806 | 2018-11-15 21:00 | 0.33207 | 6.3974
2.1875 | 2018-11-15 21:10 | 0.33207 | 6.3974
2.1944 | 2018-11-15 21:20 | 0.2298 | 344.0888
2.2014 | 2018-11-15 21:30 | 0.17205 | 1.3322
2.2083 | 2018-11-15 21:40 | 0.21168 | 4.6063
2.2153 | 2018-11-15 21:50 | 0.21159 | 351.0274
2.2222 | 2018-11-15 22:00 | 0.079209 | 316.023
2.2292 | 2018-11-15 22:10 | 0.079209 | 316.023
2.2361 | 2018-11-15 22:20 | 0.10466 | 315.7742
2.2431 | 2018-11-15 22:30 | 0.045967 | 314.1186
2.25 | 2018-11-15 22:40 | 0.086885 | 258.0434
2.2569 | 2018-11-15 22:50 | 0.12209 | 199.6223
2.2639 | 2018-11-15 23:00 | 0.12981 | 201.2276
2.2708 | 2018-11-15 23:10 | 0.12981 | 201.2276
2.2778 | 2018-11-15 23:20 | 0.23607 | 200.5845
2.2847 | 2018-11-15 23:30 | 0.33028 | 189.2342
2.2917 | 2018-11-15 23:40 | 0.26901 | 180.426
2.2986 | 2018-11-15 23:50 | 0.30717 | 192.4074
2.3056 | 2018-11-16 | 0.37723 | 186.2395
2.3125 | 2018-11-16 00:10 | 0.37723 | 186.2395
2.3194 | 2018-11-16 00:20 | 0.37451 | 194.8526
2.3264 | 2018-11-16 00:30 | 0.3659 | 187.2221
2.3333 | 2018-11-16 00:40 | 0.42745 | 189.9692
2.3403 | 2018-11-16 00:50 | 0.48545 | 182.4793
2.3472 | 2018-11-16 01:00 | 0.41508 | 178.8956
2.3542 | 2018-11-16 01:10 | 0.41508 | 178.8956
2.3611 | 2018-11-16 01:20 | 0.42906 | 180.9348
2.3681 | 2018-11-16 01:30 | 0.42747 | 182.6817
2.375 | 2018-11-16 01:40 | 0.45775 | 185.0131
2.3819 | 2018-11-16 01:50 | 0.47636 | 175.6659
2.3889 | 2018-11-16 02:00 | 0.40462 | 187.6695
2.3958 | 2018-11-16 02:10 | 0.40462 | 187.6695
2.4028 | 2018-11-16 02:20 | 0.38703 | 180.7402
2.4097 | 2018-11-16 02:30 | 0.49102 | 180.4668
2.4167 | 2018-11-16 02:40 | 0.42686 | 194.1013
2.4236 | 2018-11-16 02:50 | 0.44632 | 182.1829
2.4306 | 2018-11-16 03:00 | 0.40527 | 169.9101
2.4375 | 2018-11-16 03:10 | 0.40527 | 169.9101
2.4444 | 2018-11-16 03:20 | 0.32745 | 172.9835
2.4514 | 2018-11-16 03:30 | 0.28414 | 181.8151
2.4583 | 2018-11-16 03:40 | 0.25563 | 175.9623
2.4653 | 2018-11-16 03:50 | 0.19302 | 169.8545
2.4722 | 2018-11-16 04:00 | 0.18217 | 158.0818
2.4792 | 2018-11-16 04:10 | 0.18217 | 158.0818
2.4861 | 2018-11-16 04:20 | 0.004 | 270
2.4931 | 2018-11-16 04:30 | 0.082861 | 107.5603
2.5 | 2018-11-16 04:40 | 0.064195 | 18.1527
2.5069 | 2018-11-16 04:50 | 0.17723 | 56.0409
2.5139 | 2018-11-16 05:00 | 0.15571 | 14.1255
2.5208 | 2018-11-16 05:10 | 0.15571 | 14.1255
2.5278 | 2018-11-16 05:20 | 0.35132 | 12.4934
2.5347 | 2018-11-16 05:30 | 0.35569 | 20.5749
2.5417 | 2018-11-16 05:40 | 0.39045 | 9.5829
2.5486 | 2018-11-16 05:50 | 0.39132 | 8.5235
2.5556 | 2018-11-16 06:00 | 0.45412 | 7.7197
2.5625 | 2018-11-16 06:10 | 0.45412 | 7.7197
2.5694 | 2018-11-16 06:20 | 0.52032 | 9.6252
2.5764 | 2018-11-16 06:30 | 0.55031 | 11.6366
2.5833 | 2018-11-16 06:40 | 0.57495 | 356.7096
2.5903 | 2018-11-16 06:50 | 0.5418 | 5.8263
2.5972 | 2018-11-16 07:00 | 0.61534 | 5.97
2.6042 | 2018-11-16 07:10 | 0.61534 | 5.97
2.6111 | 2018-11-16 07:20 | 0.63841 | 8.7393
2.6181 | 2018-11-16 07:30 | 0.57177 | 8.1443
2.625 | 2018-11-16 07:40 | 0.62277 | 2.8532
2.6319 | 2018-11-16 07:50 | 0.48817 | 1.526
2.6389 | 2018-11-16 08:00 | 0.58941 | 7.0165
2.6458 | 2018-11-16 08:10 | 0.58941 | 7.0165
2.6528 | 2018-11-16 08:20 | 0.50214 | 1.3694
2.6597 | 2018-11-16 08:30 | 0.51364 | 11.6818
2.6667 | 2018-11-16 08:40 | 0.52806 | 0.86805
2.6736 | 2018-11-16 08:50 | 0.50735 | 9.0724
2.6806 | 2018-11-16 09:00 | 0.44095 | 356.2291
2.6875 | 2018-11-16 09:10 | 0.44095 | 356.2291
2.6944 | 2018-11-16 09:20 | 0.28774 | 10.4117
2.7014 | 2018-11-16 09:30 | 0.31619 | 358.0063
2.7083 | 2018-11-16 09:40 | 0.339 | 4.3987
2.7153 | 2018-11-16 09:50 | 0.25689 | 15.1182
2.7222 | 2018-11-16 10:00 | 0.30913 | 358.3317
2.7292 | 2018-11-16 10:10 | 0.30913 | 358.3317
2.7361 | 2018-11-16 10:20 | 0.19148 | 343.9313
2.7431 | 2018-11-16 10:30 | 0.062129 | 3.6914
2.75 | 2018-11-16 10:40 | 0.13408 | 352.716
2.7569 | 2018-11-16 10:50 | 0.065299 | 40.0303
2.7639 | 2018-11-16 11:00 | 0.033242 | 263.0888
2.7708 | 2018-11-16 11:10 | 0.033242 | 263.0888
2.7778 | 2018-11-16 11:20 | 0.1212 | 243.0121
2.7847 | 2018-11-16 11:30 | 0.13442 | 226.8087
2.7917 | 2018-11-16 11:40 | 0.18873 | 220.272
2.7986 | 2018-11-16 11:50 | 0.24446 | 183.5179
2.8056 | 2018-11-16 12:00 | 0.27164 | 190.6067
2.8125 | 2018-11-16 12:10 | 0.27164 | 190.6067
2.8194 | 2018-11-16 12:20 | 0.33254 | 183.2754
2.8264 | 2018-11-16 12:30 | 0.30754 | 194.3074
2.8333 | 2018-11-16 12:40 | 0.44224 | 189.6327
2.8403 | 2018-11-16 12:50 | 0.38302 | 187.1992
2.8472 | 2018-11-16 13:00 | 0.437 | 187.7593
2.8542 | 2018-11-16 13:10 | 0.437 | 187.7593
2.8611 | 2018-11-16 13:20 | 0.3906 | 173.3844
2.8681 | 2018-11-16 13:30 | 0.56635 | 182.0237
2.875 | 2018-11-16 13:40 | 0.52111 | 190.7277
2.8819 | 2018-11-16 13:50 | 0.60652 | 177.6376
2.8889 | 2018-11-16 14:00 | 0.49941 | 185.6307
2.8958 | 2018-11-16 14:10 | 0.49941 | 185.6307
2.9028 | 2018-11-16 14:20 | 0.55426 | 181.7576
2.9097 | 2018-11-16 14:30 | 0.50993 | 190.737
2.9167 | 2018-11-16 14:40 | 0.48491 | 186.2749
2.9236 | 2018-11-16 14:50 | 0.51799 | 183.5418
2.9306 | 2018-11-16 15:00 | 0.52988 | 186.9373
2.9375 | 2018-11-16 15:10 | 0.52988 | 186.9373
2.9444 | 2018-11-16 15:20 | 0.48846 | 185.7573
2.9514 | 2018-11-16 15:30 | 0.49021 | 173.4404
2.9583 | 2018-11-16 15:40 | 0.48853 | 191.3329
2.9653 | 2018-11-16 15:50 | 0.443 | 180.2587
2.9722 | 2018-11-16 16:00 | 0.37871 | 185.4547
2.9792 | 2018-11-16 16:10 | 0.37871 | 185.4547
2.9861 | 2018-11-16 16:20 | 0.29604 | 179.0323
2.9931 | 2018-11-16 16:30 | 0.29222 | 190.8485
3 | 2018-11-16 16:40 | 0.23186 | 184.9483
3.0069 | 2018-11-16 16:50 | 0.27098 | 184.869
3.0139 | 2018-11-16 17:00 | 0.23641 | 170.2588
3.0208 | 2018-11-16 17:10 | 0.23641 | 170.2588
3.0278 | 2018-11-16 17:20 | 0.19079 | 156.5254
3.0347 | 2018-11-16 17:30 | 0.088284 | 99.7824
3.0417 | 2018-11-16 17:40 | 0.082389 | 84.4278
3.0486 | 2018-11-16 17:50 | 0.039294 | 104.7436
3.0556 | 2018-11-16 18:00 | 0.077156 | 42.3736
3.0625 | 2018-11-16 18:10 | 0.077156 | 42.3736
3.0694 | 2018-11-16 18:20 | 0.16415 | 25.6284
3.0764 | 2018-11-16 18:30 | 0.23598 | 31.1303
3.0833 | 2018-11-16 18:40 | 0.22365 | 25.4193
3.0903 | 2018-11-16 18:50 | 0.27577 | 22.3801
3.0972 | 2018-11-16 19:00 | 0.33419 | 11.0409
3.1042 | 2018-11-16 19:10 | 0.33419 | 11.0409
3.1111 | 2018-11-16 19:20 | 0.35459 | 14.0362
3.1181 | 2018-11-16 19:30 | 0.35445 | 9.0903
3.125 | 2018-11-16 19:40 | 0.42695 | 9.5726
3.1319 | 2018-11-16 19:50 | 0.38273 | 9.9299
3.1389 | 2018-11-16 20:00 | 0.49623 | 1.7322
3.1458 | 2018-11-16 20:10 | 0.49623 | 1.7322
3.1528 | 2018-11-16 20:20 | 0.50132 | 2.0576
3.1597 | 2018-11-16 20:30 | 0.41701 | 3.9877
3.1667 | 2018-11-16 20:40 | 0.46717 | 4.0507
3.1736 | 2018-11-16 20:50 | 0.47609 | 358.9168
3.1806 | 2018-11-16 21:00 | 0.50522 | 358.2986
3.1875 | 2018-11-16 21:10 | 0.50522 | 358.2986
3.1944 | 2018-11-16 21:20 | 0.43095 | 5.4592
3.2014 | 2018-11-16 21:30 | 0.44032 | 7.0443
3.2083 | 2018-11-16 21:40 | 0.5016 | 5.8356
3.2153 | 2018-11-16 21:50 | 0.46975 | 10.4248
3.2222 | 2018-11-16 22:00 | 0.39015 | 12.4332
3.2292 | 2018-11-16 22:10 | 0.39015 | 12.4332
3.2361 | 2018-11-16 22:20 | 0.31584 | 4.1761
3.2431 | 2018-11-16 22:30 | 0.33901 | 359.493
3.25 | 2018-11-16 22:40 | 0.23025 | 5.983
3.2569 | 2018-11-16 22:50 | 0.145 | 0.39514
3.2639 | 2018-11-16 23:00 | 0.23717 | 7.7543
3.2708 | 2018-11-16 23:10 | 0.23717 | 7.7543
3.2778 | 2018-11-16 23:20 | 0.15785 | 16.9426
3.2847 | 2018-11-16 23:30 | 0.0764 | 307.0199
3.2917 | 2018-11-16 23:40 | 0.074967 | 9.211
3.2986 | 2018-11-16 23:50 | 0.10332 | 317.3533
3.3056 | 2018-11-17 | 0.038601 | 163.4429
3.3125 | 2018-11-17 00:10 | 0.038601 | 163.4429
3.3194 | 2018-11-17 00:20 | 0.13822 | 234.125
3.3264 | 2018-11-17 00:30 | 0.14897 | 173.4474
3.3333 | 2018-11-17 00:40 | 0.19506 | 195.4612
3.3403 | 2018-11-17 00:50 | 0.26809 | 191.1842
3.3472 | 2018-11-17 01:00 | 0.23594 | 174.8935
3.3542 | 2018-11-17 01:10 | 0.23594 | 174.8935
3.3611 | 2018-11-17 01:20 | 0.29711 | 194.2233
3.3681 | 2018-11-17 01:30 | 0.34604 | 179.1721
3.375 | 2018-11-17 01:40 | 0.46601 | 179.6311
3.3819 | 2018-11-17 01:50 | 0.35672 | 187.0852
3.3889 | 2018-11-17 02:00 | 0.41854 | 186.31
3.3958 | 2018-11-17 02:10 | 0.41854 | 186.31
3.4028 | 2018-11-17 02:20 | 0.42017 | 178.3634
3.4097 | 2018-11-17 02:30 | 0.47577 | 184.9437
3.4167 | 2018-11-17 02:40 | 0.46302 | 188.4451
3.4236 | 2018-11-17 02:50 | 0.51446 | 192.1181
3.4306 | 2018-11-17 03:00 | 0.4121 | 181.2514
3.4375 | 2018-11-17 03:10 | 0.4121 | 181.2514
3.4444 | 2018-11-17 03:20 | 0.42652 | 182.8222
3.4514 | 2018-11-17 03:30 | 0.56729 | 186.1729
3.4583 | 2018-11-17 03:40 | 0.42702 | 180.5367
3.4653 | 2018-11-17 03:50 | 0.381 | 180.1504
3.4722 | 2018-11-17 04:00 | 0.36723 | 184.6859
3.4792 | 2018-11-17 04:10 | 0.36723 | 184.6859
3.4861 | 2018-11-17 04:20 | 0.39628 | 177.8307
3.4931 | 2018-11-17 04:30 | 0.39706 | 178.9899
3.5 | 2018-11-17 04:40 | 0.2686 | 176.1575
3.5069 | 2018-11-17 04:50 | 0.34284 | 172.6262
3.5139 | 2018-11-17 05:00 | 0.27441 | 183.1335
3.5208 | 2018-11-17 05:10 | 0.27441 | 183.1335
3.5278 | 2018-11-17 05:20 | 0.16925 | 168.7565
3.5347 | 2018-11-17 05:30 | 0.18438 | 160.6806
3.5417 | 2018-11-17 05:40 | 0.14001 | 158.1986
3.5486 | 2018-11-17 05:50 | 0.027731 | 154.359
3.5556 | 2018-11-17 06:00 | 0.098112 | 150.0378
3.5625 | 2018-11-17 06:10 | 0.098112 | 150.0378
3.5694 | 2018-11-17 06:20 | 0.19725 | 25.5258
3.5764 | 2018-11-17 06:30 | 0.099202 | 52.7836
3.5833 | 2018-11-17 06:40 | 0.25539 | 30.0788
3.5903 | 2018-11-17 06:50 | 0.22095 | 27.4928
3.5972 | 2018-11-17 07:00 | 0.34244 | 11.9662
3.6042 | 2018-11-17 07:10 | 0.34244 | 11.9662
3.6111 | 2018-11-17 07:20 | 0.35523 | 12.3539
3.6181 | 2018-11-17 07:30 | 0.33127 | 12.0223
3.625 | 2018-11-17 07:40 | 0.45569 | 18.1566
3.6319 | 2018-11-17 07:50 | 0.45949 | 15.3973
3.6389 | 2018-11-17 08:00 | 0.49612 | 358.7295
3.6458 | 2018-11-17 08:10 | 0.49612 | 358.7295
3.6528 | 2018-11-17 08:20 | 0.55068 | 4.4785
3.6597 | 2018-11-17 08:30 | 0.74919 | 8.9846
3.6667 | 2018-11-17 08:40 | 0.60501 | 9.8983
3.6736 | 2018-11-17 08:50 | 0.48835 | 11.8162
3.6806 | 2018-11-17 09:00 | 0.55091 | 9.0862
3.6875 | 2018-11-17 09:10 | 0.55091 | 9.0862
3.6944 | 2018-11-17 09:20 | 0.58595 | 7.4525
3.7014 | 2018-11-17 09:30 | 0.56014 | 11.9519
3.7083 | 2018-11-17 09:40 | 0.47422 | 4.1114
3.7153 | 2018-11-17 09:50 | 0.41255 | 14.171
3.7222 | 2018-11-17 10:00 | 0.48354 | 12.5417
3.7292 | 2018-11-17 10:10 | 0.48354 | 12.5417
3.7361 | 2018-11-17 10:20 | 0.42862 | 3.076
3.7431 | 2018-11-17 10:30 | 0.37226 | 6.3232
3.75 | 2018-11-17 10:40 | 0.3416 | 5.5437
3.7569 | 2018-11-17 10:50 | 0.31963 | 3.5875
3.7639 | 2018-11-17 11:00 | 0.45811 | 1.2508
3.7708 | 2018-11-17 11:10 | 0.45811 | 1.2508
3.7778 | 2018-11-17 11:20 | 0.21032 | 12.9129
3.7847 | 2018-11-17 11:30 | 0.26219 | 14.3543
3.7917 | 2018-11-17 11:40 | 0.2226 | 348.3367
3.7986 | 2018-11-17 11:50 | 0.20112 | 1.9946
3.8056 | 2018-11-17 12:00 | 0.21704 | 358.944
3.8125 | 2018-11-17 12:10 | 0.21704 | 358.944
3.8194 | 2018-11-17 12:20 | 0.11573 | 347.5249
3.8264 | 2018-11-17 12:30 | 0.021633 | 236.3099
3.8333 | 2018-11-17 12:40 | 0.09368 | 286.1134
3.8403 | 2018-11-17 12:50 | 0.029682 | 147.3808
3.8472 | 2018-11-17 13:00 | 0.11236 | 175.4057
3.8542 | 2018-11-17 13:10 | 0.11236 | 175.4057
3.8611 | 2018-11-17 13:20 | 0.1481 | 186.9811
3.8681 | 2018-11-17 13:30 | 0.19846 | 186.946
3.875 | 2018-11-17 13:40 | 0.20673 | 195.717
3.8819 | 2018-11-17 13:50 | 0.27234 | 174.3103
3.8889 | 2018-11-17 14:00 | 0.38005 | 180.9046
3.8958 | 2018-11-17 14:10 | 0.38005 | 180.9046
3.9028 | 2018-11-17 14:20 | 0.49591 | 183.4682
3.9097 | 2018-11-17 14:30 | 0.36731 | 177.6595
3.9167 | 2018-11-17 14:40 | 0.419 | 179.8633
3.9236 | 2018-11-17 14:50 | 0.50202 | 179.4293
3.9306 | 2018-11-17 15:00 | 0.57878 | 182.9712
3.9375 | 2018-11-17 15:10 | 0.57878 | 182.9712
3.9444 | 2018-11-17 15:20 | 0.48537 | 182.2434
3.9514 | 2018-11-17 15:30 | 0.54933 | 181.9821
3.9583 | 2018-11-17 15:40 | 0.53749 | 184.2679
3.9653 | 2018-11-17 15:50 | 0.56242 | 184.0784
3.9722 | 2018-11-17 16:00 | 0.55097 | 186.8799
3.9792 | 2018-11-17 16:10 | 0.55097 | 186.8799
3.9861 | 2018-11-17 16:20 | 0.55523 | 187.8674
3.9931 | 2018-11-17 16:30 | 0.46813 | 181.3465
4 | 2018-11-17 16:40 | 0.47369 | 187.155
4.0069 | 2018-11-17 16:50 | 0.50232 | 182.0535
4.0139 | 2018-11-17 17:00 | 0.39966 | 187.7652
4.0208 | 2018-11-17 17:10 | 0.39966 | 187.7652
4.0278 | 2018-11-17 17:20 | 0.45433 | 185.811
4.0347 | 2018-11-17 17:30 | 0.53634 | 177.9698
4.0417 | 2018-11-17 17:40 | 0.40965 | 176.7814
4.0486 | 2018-11-17 17:50 | 0.301 | 180
4.0556 | 2018-11-17 18:00 | 0.29486 | 172.0073
4.0625 | 2018-11-17 18:10 | 0.29486 | 172.0073
4.0694 | 2018-11-17 18:20 | 0.23621 | 182.4263
4.0764 | 2018-11-17 18:30 | 0.12804 | 178.6574
4.0833 | 2018-11-17 18:40 | 0.15567 | 159.7024
4.0903 | 2018-11-17 18:50 | 0.18334 | 149.5186
4.0972 | 2018-11-17 19:00 | 0.089499 | 193.5704
4.1042 | 2018-11-17 19:10 | 0.089499 | 193.5704
4.1111 | 2018-11-17 19:20 | 0.12532 | 42.0892
4.1181 | 2018-11-17 19:30 | 0.095079 | 22.249
4.125 | 2018-11-17 19:40 | 0.20623 | 35.9252
4.1319 | 2018-11-17 19:50 | 0.1955 | 14.8181
4.1389 | 2018-11-17 20:00 | 0.23099 | 24.0129
4.1458 | 2018-11-17 20:10 | 0.23099 | 24.0129
4.1528 | 2018-11-17 20:20 | 0.31283 | 17.1027
4.1597 | 2018-11-17 20:30 | 0.34342 | 18.3294
4.1667 | 2018-11-17 20:40 | 0.39435 | 18.9403
4.1736 | 2018-11-17 20:50 | 0.40376 | 7.8291
4.1806 | 2018-11-17 21:00 | 0.34098 | 7.5835
4.1875 | 2018-11-17 21:10 | 0.34098 | 7.5835
4.1944 | 2018-11-17 21:20 | 0.41037 | 6.1552
4.2014 | 2018-11-17 21:30 | 0.44481 | 13.7863
4.2083 | 2018-11-17 21:40 | 0.50419 | 1.5911
4.2153 | 2018-11-17 21:50 | 0.52146 | 4.2892
4.2222 | 2018-11-17 22:00 | 0.53003 | 3.5696
4.2292 | 2018-11-17 22:10 | 0.53003 | 3.5696
4.2361 | 2018-11-17 22:20 | 0.43312 | 358.677
4.2431 | 2018-11-17 22:30 | 0.4251 | 358.7869
4.25 | 2018-11-17 22:40 | 0.53995 | 3.3976
4.2569 | 2018-11-17 22:50 | 0.48993 | 13.6959
4.2639 | 2018-11-17 23:00 | 0.43501 | 359.6049
4.2708 | 2018-11-17 23:10 | 0.43501 | 359.6049
4.2778 | 2018-11-17 23:20 | 0.35446 | 10.0735
4.2847 | 2018-11-17 23:30 | 0.33825 | 357.7974
4.2917 | 2018-11-17 23:40 | 0.35251 | 3.0897
4.2986 | 2018-11-17 23:50 | 0.33245 | 12.1549
4.3056 | 2018-11-18 | 0.27767 | 9.3266
4.3125 | 2018-11-18 00:10 | 0.27767 | 9.3266
4.3194 | 2018-11-18 00:20 | 0.29403 | 0.77949
4.3264 | 2018-11-18 00:30 | 0.23005 | 358.7546
4.3333 | 2018-11-18 00:40 | 0.10787 | 349.3151
4.3403 | 2018-11-18 00:50 | 0.16952 | 19.2901
4.3472 | 2018-11-18 01:00 | 0.053075 | 312.7094
4.3542 | 2018-11-18 01:10 | 0.053075 | 312.7094
4.3611 | 2018-11-18 01:20 | 0.15023 | 210.8329
4.3681 | 2018-11-18 01:30 | 0.19543 | 206.4339
4.375 | 2018-11-18 01:40 | 0.11162 | 202.6593
4.3819 | 2018-11-18 01:50 | 0.20977 | 189.3276
4.3889 | 2018-11-18 02:00 | 0.33167 | 187.275
4.3958 | 2018-11-18 02:10 | 0.33167 | 187.275
4.4028 | 2018-11-18 02:20 | 0.3407 | 185.7273
4.4097 | 2018-11-18 02:30 | 0.45974 | 184.9913
4.4167 | 2018-11-18 02:40 | 0.47295 | 187.4105
4.4236 | 2018-11-18 02:50 | 0.45782 | 187.4044
4.4306 | 2018-11-18 03:00 | 0.44463 | 175.0972
4.4375 | 2018-11-18 03:10 | 0.44463 | 175.0972
4.4444 | 2018-11-18 03:20 | 0.52122 | 181.6491
4.4514 | 2018-11-18 03:30 | 0.55045 | 188.7778
4.4583 | 2018-11-18 03:40 | 0.57436 | 185.1944
4.4653 | 2018-11-18 03:50 | 0.54877 | 183.0293
4.4722 | 2018-11-18 04:00 | 0.65669 | 177.3816
4.4792 | 2018-11-18 04:10 | 0.65669 | 177.3816
4.4861 | 2018-11-18 04:20 | 0.63966 | 182.5985
4.4931 | 2018-11-18 04:30 | 0.64856 | 188.1551
4.5 | 2018-11-18 04:40 | 0.52736 | 191.3739
4.5069 | 2018-11-18 04:50 | 0.57842 | 182.1797
4.5139 | 2018-11-18 05:00 | 0.49714 | 178.6169
4.5208 | 2018-11-18 05:10 | 0.49714 | 178.6169
4.5278 | 2018-11-18 05:20 | 0.51401 | 179.6656
4.5347 | 2018-11-18 05:30 | 0.48869 | 183.0498
4.5417 | 2018-11-18 05:40 | 0.55015 | 188.572
4.5486 | 2018-11-18 05:50 | 0.41588 | 176.2776
4.5556 | 2018-11-18 06:00 | 0.40702 | 180.5631
4.5625 | 2018-11-18 06:10 | 0.40702 | 180.5631
4.5694 | 2018-11-18 06:20 | 0.35304 | 179.1885
4.5764 | 2018-11-18 06:30 | 0.28094 | 173.2544
4.5833 | 2018-11-18 06:40 | 0.24 | 179.7613
4.5903 | 2018-11-18 06:50 | 0.20156 | 166.5153
4.5972 | 2018-11-18 07:00 | 0.1847 | 153.2962
4.6042 | 2018-11-18 07:10 | 0.1847 | 153.2962
4.6111 | 2018-11-18 07:20 | 0.13132 | 159.495
4.6181 | 2018-11-18 07:30 | 0.17066 | 148.1725
4.625 | 2018-11-18 07:40 | 0.12612 | 63.6381
4.6319 | 2018-11-18 07:50 | 0.14569 | 43.8876
4.6389 | 2018-11-18 08:00 | 0.14827 | 49.6502
4.6458 | 2018-11-18 08:10 | 0.14827 | 49.6502
4.6528 | 2018-11-18 08:20 | 0.22146 | 42.9872
4.6597 | 2018-11-18 08:30 | 0.36112 | 33.25
4.6667 | 2018-11-18 08:40 | 0.32769 | 14.6724
4.6736 | 2018-11-18 08:50 | 0.43118 | 15.7446
4.6806 | 2018-11-18 09:00 | 0.42879 | 3.4763
4.6875 | 2018-11-18 09:10 | 0.42879 | 3.4763
4.6944 | 2018-11-18 09:20 | 0.42596 | 9.595
4.7014 | 2018-11-18 09:30 | 0.49687 | 17.4503
4.7083 | 2018-11-18 09:40 | 0.53455 | 13.8543
4.7153 | 2018-11-18 09:50 | 0.53782 | 5.8696
4.7222 | 2018-11-18 10:00 | 0.49797 | 3.5692
4.7292 | 2018-11-18 10:10 | 0.49797 | 3.5692
4.7361 | 2018-11-18 10:20 | 0.49354 | 2.6711
4.7431 | 2018-11-18 10:30 | 0.63705 | 0.71953
4.75 | 2018-11-18 10:40 | 0.5211 | 358.9004
4.7569 | 2018-11-18 10:50 | 0.41521 | 8.1691
4.7639 | 2018-11-18 11:00 | 0.47318 | 1.5743
4.7708 | 2018-11-18 11:10 | 0.47318 | 1.5743
4.7778 | 2018-11-18 11:20 | 0.53725 | 6.3049
4.7847 | 2018-11-18 11:30 | 0.47638 | 2.2858
4.7917 | 2018-11-18 11:40 | 0.47867 | 4.7935
4.7986 | 2018-11-18 11:50 | 0.41465 | 5.1194
4.8056 | 2018-11-18 12:00 | 0.36223 | 2.0567
4.8125 | 2018-11-18 12:10 | 0.36223 | 2.0567
4.8194 | 2018-11-18 12:20 | 0.28339 | 5.6704
4.8264 | 2018-11-18 12:30 | 0.28814 | 13.6504
4.8333 | 2018-11-18 12:40 | 0.25541 | 7.8763
4.8403 | 2018-11-18 12:50 | 0.2 | 0.28648
4.8472 | 2018-11-18 13:00 | 0.20256 | 355.7531
4.8542 | 2018-11-18 13:10 | 0.20256 | 355.7531
4.8611 | 2018-11-18 13:20 | 0.09684 | 16.1892
4.8681 | 2018-11-18 13:30 | 0.068007 | 89.1575
4.875 | 2018-11-18 13:40 | 0.029069 | 3.9452
4.8819 | 2018-11-18 13:50 | 0.084119 | 208.393
4.8889 | 2018-11-18 14:00 | 0.18376 | 191.6157
4.8958 | 2018-11-18 14:10 | 0.18376 | 191.6157
4.9028 | 2018-11-18 14:20 | 0.33465 | 187.21
4.9097 | 2018-11-18 14:30 | 0.25794 | 184.8928
4.9167 | 2018-11-18 14:40 | 0.43757 | 175.1494
4.9236 | 2018-11-18 14:50 | 0.32692 | 196.1621
4.9306 | 2018-11-18 15:00 | 0.40949 | 182.7995
4.9375 | 2018-11-18 15:10 | 0.40949 | 182.7995
4.9444 | 2018-11-18 15:20 | 0.47824 | 181.7974
4.9514 | 2018-11-18 15:30 | 0.465 | 180.2464
4.9583 | 2018-11-18 15:40 | 0.42873 | 183.3429
4.9653 | 2018-11-18 15:50 | 0.60908 | 180.9407
4.9722 | 2018-11-18 16:00 | 0.64302 | 179.5545
4.9792 | 2018-11-18 16:10 | 0.64302 | 179.5545
4.9861 | 2018-11-18 16:20 | 0.70438 | 183.5814
4.9931 | 2018-11-18 16:30 | 0.6907 | 177.4276
5 | 2018-11-18 16:40 | 0.75773 | 187.05
5.0069 | 2018-11-18 16:50 | 0.69538 | 187.7689
5.0139 | 2018-11-18 17:00 | 0.65074 | 177.2695
5.0208 | 2018-11-18 17:10 | 0.65074 | 177.2695
5.0278 | 2018-11-18 17:20 | 0.6329 | 184.4404
5.0347 | 2018-11-18 17:30 | 0.69459 | 183.8799
5.0417 | 2018-11-18 17:40 | 0.58263 | 177.3439
5.0486 | 2018-11-18 17:50 | 0.59466 | 182.6988
5.0556 | 2018-11-18 18:00 | 0.61389 | 176.9185
5.0625 | 2018-11-18 18:10 | 0.61389 | 176.9185
5.0694 | 2018-11-18 18:20 | 0.4922 | 178.3701
5.0764 | 2018-11-18 18:30 | 0.543 | 180
5.0833 | 2018-11-18 18:40 | 0.43914 | 181.4354
5.0903 | 2018-11-18 18:50 | 0.42656 | 187.4082
5.0972 | 2018-11-18 19:00 | 0.4074 | 177.4677
5.1042 | 2018-11-18 19:10 | 0.4074 | 177.4677
5.1111 | 2018-11-18 19:20 | 0.43219 | 184.2462
5.1181 | 2018-11-18 19:30 | 0.30124 | 182.283
5.125 | 2018-11-18 19:40 | 0.20931 | 171.4828
5.1319 | 2018-11-18 19:50 | 0.2383 | 177.1136
5.1389 | 2018-11-18 20:00 | 0.21698 | 147.9946
5.1458 | 2018-11-18 20:10 | 0.21698 | 147.9946
5.1528 | 2018-11-18 20:20 | 0.07823 | 147.5288
5.1597 | 2018-11-18 20:30 | 0.13352 | 73.4652
5.1667 | 2018-11-18 20:40 | 0.087115 | 41.7428
5.1736 | 2018-11-18 20:50 | 0.10872 | 34.1285
5.1806 | 2018-11-18 21:00 | 0.21109 | 27.0506
5.1875 | 2018-11-18 21:10 | 0.21109 | 27.0506
5.1944 | 2018-11-18 21:20 | 0.31316 | 31.152
5.2014 | 2018-11-18 21:30 | 0.297 | 0.19291
5.2083 | 2018-11-18 21:40 | 0.34808 | 20.5175
5.2153 | 2018-11-18 21:50 | 0.34752 | 11.1159
5.2222 | 2018-11-18 22:00 | 0.50768 | 6.901
5.2292 | 2018-11-18 22:10 | 0.50768 | 6.901
5.2361 | 2018-11-18 22:20 | 0.42578 | 11.653
5.2431 | 2018-11-18 22:30 | 0.35411 | 14.3894
5.25 | 2018-11-18 22:40 | 0.44312 | 17.3309
5.2569 | 2018-11-18 22:50 | 0.37949 | 11.3988
5.2639 | 2018-11-18 23:00 | 0.42698 | 8.7564
5.2708 | 2018-11-18 23:10 | 0.42698 | 8.7564
5.2778 | 2018-11-18 23:20 | 0.42903 | 359.3322
5.2847 | 2018-11-18 23:30 | 0.42417 | 8.9516
5.2917 | 2018-11-18 23:40 | 0.43701 | 8.6864
5.2986 | 2018-11-18 23:50 | 0.36809 | 358.7546
5.3056 | 2018-11-19 | 0.31614 | 11.3099
5.3125 | 2018-11-19 00:10 | 0.31614 | 11.3099
5.3194 | 2018-11-19 00:20 | 0.25454 | 353.6847
5.3264 | 2018-11-19 00:30 | 0.25214 | 5.4619
5.3333 | 2018-11-19 00:40 | 0.372 | 0
5.3403 | 2018-11-19 00:50 | 0.2003 | 3.1481
5.3472 | 2018-11-19 01:00 | 0.26315 | 19.5367
5.3542 | 2018-11-19 01:10 | 0.26315 | 19.5367
5.3611 | 2018-11-19 01:20 | 0.13418 | 25.6102
5.3681 | 2018-11-19 01:30 | 0.1422 | 36.7087
5.375 | 2018-11-19 01:40 | 0.10183 | 342.2768
5.3819 | 2018-11-19 01:50 | 0.13885 | 78.3664
5.3889 | 2018-11-19 02:00 | 0.10102 | 111.4854
5.3958 | 2018-11-19 02:10 | 0.10102 | 111.4854
5.4028 | 2018-11-19 02:20 | 0.059135 | 161.2587
5.4097 | 2018-11-19 02:30 | 0.16787 | 188.5645
5.4167 | 2018-11-19 02:40 | 0.14697 | 170.6018
5.4236 | 2018-11-19 02:50 | 0.32976 | 174.0819
5.4306 | 2018-11-19 03:00 | 0.47301 | 180.3634
5.4375 | 2018-11-19 03:10 | 0.47301 | 180.3634
5.4444 | 2018-11-19 03:20 | 0.47261 | 184.7334
5.4514 | 2018-11-19 03:30 | 0.41588 | 183.7224
5.4583 | 2018-11-19 03:40 | 0.52345 | 184.2728
5.4653 | 2018-11-19 03:50 | 0.49192 | 176.5036
5.4722 | 2018-11-19 04:00 | 0.51252 | 182.5721
5.4792 | 2018-11-19 04:10 | 0.51252 | 182.5721
5.4861 | 2018-11-19 04:20 | 0.69049 | 182.1579
5.4931 | 2018-11-19 04:30 | 0.62901 | 180.2733
5.5 | 2018-11-19 04:40 | 0.70169 | 177.4679
5.5069 | 2018-11-19 04:50 | 0.66106 | 180.7801
5.5139 | 2018-11-19 05:00 | 0.576 | 180.0995
5.5208 | 2018-11-19 05:10 | 0.576 | 180.0995
5.5278 | 2018-11-19 05:20 | 0.66951 | 183.8539
5.5347 | 2018-11-19 05:30 | 0.65523 | 184.7273
5.5417 | 2018-11-19 05:40 | 0.65387 | 186.2337
5.5486 | 2018-11-19 05:50 | 0.64201 | 183.2145
5.5556 | 2018-11-19 06:00 | 0.53206 | 179.1385
5.5625 | 2018-11-19 06:10 | 0.53206 | 179.1385
5.5694 | 2018-11-19 06:20 | 0.58024 | 186.929
5.5764 | 2018-11-19 06:30 | 0.68329 | 185.6272
5.5833 | 2018-11-19 06:40 | 0.56166 | 186.543
5.5903 | 2018-11-19 06:50 | 0.46614 | 186.6524
5.5972 | 2018-11-19 07:00 | 0.55044 | 177.7094
5.6042 | 2018-11-19 07:10 | 0.55044 | 177.7094
5.6111 | 2018-11-19 07:20 | 0.50267 | 182.9649
5.6181 | 2018-11-19 07:30 | 0.397 | 180.1443
5.625 | 2018-11-19 07:40 | 0.22472 | 184.5943
5.6319 | 2018-11-19 07:50 | 0.20422 | 171.5525
5.6389 | 2018-11-19 08:00 | 0.16008 | 165.5297
5.6458 | 2018-11-19 08:10 | 0.16008 | 165.5297
5.6528 | 2018-11-19 08:20 | 0.087693 | 135.924
5.6597 | 2018-11-19 08:30 | 0.065192 | 122.4712
5.6667 | 2018-11-19 08:40 | 0.052345 | 43.4518
5.6736 | 2018-11-19 08:50 | 0.16002 | 59.5889
5.6806 | 2018-11-19 09:00 | 0.13039 | 23.0255
5.6875 | 2018-11-19 09:10 | 0.13039 | 23.0255
5.6944 | 2018-11-19 09:20 | 0.33101 | 359.4807
5.7014 | 2018-11-19 09:30 | 0.3798 | 20.8209
5.7083 | 2018-11-19 09:40 | 0.37401 | 22.3135
5.7153 | 2018-11-19 09:50 | 0.41967 | 21.6746
5.7222 | 2018-11-19 10:00 | 0.4791 | 12.905
5.7292 | 2018-11-19 10:10 | 0.4791 | 12.905
5.7361 | 2018-11-19 10:20 | 0.44684 | 17.9889
5.7431 | 2018-11-19 10:30 | 0.47829 | 6.7238
5.75 | 2018-11-19 10:40 | 0.42875 | 9.3964
5.7569 | 2018-11-19 10:50 | 0.47249 | 7.9072
5.7639 | 2018-11-19 11:00 | 0.54363 | 11.3513
5.7708 | 2018-11-19 11:10 | 0.54363 | 11.3513
5.7778 | 2018-11-19 11:20 | 0.63809 | 10.2004
5.7847 | 2018-11-19 11:30 | 0.70739 | 8.2905
5.7917 | 2018-11-19 11:40 | 0.63513 | 7.9642
5.7986 | 2018-11-19 11:50 | 0.58495 | 12.5394
5.8056 | 2018-11-19 12:00 | 0.49176 | 6.07
5.8125 | 2018-11-19 12:10 | 0.49176 | 6.07
5.8194 | 2018-11-19 12:20 | 0.5213 | 12.9699
5.8264 | 2018-11-19 12:30 | 0.43904 | 359.2169
5.8333 | 2018-11-19 12:40 | 0.42726 | 357.9881
5.8403 | 2018-11-19 12:50 | 0.39711 | 8.2525
5.8472 | 2018-11-19 13:00 | 0.28443 | 10.1247
5.8542 | 2018-11-19 13:10 | 0.28443 | 10.1247
5.8611 | 2018-11-19 13:20 | 0.26792 | 6.8598
5.8681 | 2018-11-19 13:30 | 0.23843 | 13.3368
5.875 | 2018-11-19 13:40 | 0.24417 | 357.8876
5.8819 | 2018-11-19 13:50 | 0.17928 | 356.8024
5.8889 | 2018-11-19 14:00 | 0.13375 | 11.646
5.8958 | 2018-11-19 14:10 | 0.13375 | 11.646
5.9028 | 2018-11-19 14:20 | 0.088119 | 297.7283
5.9097 | 2018-11-19 14:30 | 0.041049 | 55.9228
5.9167 | 2018-11-19 14:40 | 0.084149 | 135.4815
5.9236 | 2018-11-19 14:50 | 0.204 | 179.7191
5.9306 | 2018-11-19 15:00 | 0.17772 | 190.0453
5.9375 | 2018-11-19 15:10 | 0.17772 | 190.0453
5.9444 | 2018-11-19 15:20 | 0.34721 | 181.9806
5.9514 | 2018-11-19 15:30 | 0.39004 | 188.2547
5.9583 | 2018-11-19 15:40 | 0.4137 | 176.6742
5.9653 | 2018-11-19 15:50 | 0.51902 | 179.5584
5.9722 | 2018-11-19 16:00 | 0.48121 | 170.0679
5.9792 | 2018-11-19 16:10 | 0.48121 | 170.0679
5.9861 | 2018-11-19 16:20 | 0.58672 | 182.8331
5.9931 | 2018-11-19 16:30 | 0.65902 | 179.5653
6 | 2018-11-19 16:40 | 0.78976 | 185.5951
6.0069 | 2018-11-19 16:50 | 0.7473 | 181.6103
6.0139 | 2018-11-19 17:00 | 0.80539 | 181.7788
6.0208 | 2018-11-19 17:10 | 0.80539 | 181.7788
6.0278 | 2018-11-19 17:20 | 0.82583 | 176.1813
6.0347 | 2018-11-19 17:30 | 0.84703 | 179.5265
6.0417 | 2018-11-19 17:40 | 0.83441 | 181.7856
6.0486 | 2018-11-19 17:50 | 0.804 | 182.8517
6.0556 | 2018-11-19 18:00 | 0.79395 | 187.0176
6.0625 | 2018-11-19 18:10 | 0.79395 | 187.0176
6.0694 | 2018-11-19 18:20 | 0.72211 | 183.1754
6.0764 | 2018-11-19 18:30 | 0.78714 | 181.0919
6.0833 | 2018-11-19 18:40 | 0.83994 | 183.8912
6.0903 | 2018-11-19 18:50 | 0.61708 | 187.3553
6.0972 | 2018-11-19 19:00 | 0.80595 | 183.9843
6.1042 | 2018-11-19 19:10 | 0.80595 | 183.9843
6.1111 | 2018-11-19 19:20 | 0.69299 | 176.9394
6.1181 | 2018-11-19 19:30 | 0.58312 | 181.1792
6.125 | 2018-11-19 19:40 | 0.67431 | 176.429
6.1319 | 2018-11-19 19:50 | 0.50914 | 176.171
6.1389 | 2018-11-19 20:00 | 0.51344 | 185.5885
6.1458 | 2018-11-19 20:10 | 0.51344 | 185.5885
6.1528 | 2018-11-19 20:20 | 0.34889 | 168.5934
6.1597 | 2018-11-19 20:30 | 0.40312 | 181.4214
6.1667 | 2018-11-19 20:40 | 0.39201 | 180.4385
6.1736 | 2018-11-19 20:50 | 0.26982 | 162.9753
6.1806 | 2018-11-19 21:00 | 0.17714 | 182.2648
6.1875 | 2018-11-19 21:10 | 0.17714 | 182.2648
6.1944 | 2018-11-19 21:20 | 0.10475 | 110.6841
6.2014 | 2018-11-19 21:30 | 0.094641 | 164.0546
6.2083 | 2018-11-19 21:40 | 0.089811 | 37.7631
6.2153 | 2018-11-19 21:50 | 0.17088 | 32.5741
6.2222 | 2018-11-19 22:00 | 0.25543 | 42.9376
6.2292 | 2018-11-19 22:10 | 0.25543 | 42.9376
6.2361 | 2018-11-19 22:20 | 0.36018 | 28.3438
6.2431 | 2018-11-19 22:30 | 0.26476 | 26.9522
6.25 | 2018-11-19 22:40 | 0.38996 | 19.3178
6.2569 | 2018-11-19 22:50 | 0.3857 | 21.4428
6.2639 | 2018-11-19 23:00 | 0.48376 | 12.6573
6.2708 | 2018-11-19 23:10 | 0.48376 | 12.6573
6.2778 | 2018-11-19 23:20 | 0.41932 | 10.7204
6.2847 | 2018-11-19 23:30 | 0.43837 | 2.3533
6.2917 | 2018-11-19 23:40 | 0.43546 | 2.6324
6.2986 | 2018-11-19 23:50 | 0.55487 | 3.2027
6.3056 | 2018-11-20 | 0.54519 | 3.7861
6.3125 | 2018-11-20 00:10 | 0.54519 | 3.7861
6.3194 | 2018-11-20 00:20 | 0.45107 | 11.5092
6.3264 | 2018-11-20 00:30 | 0.49616 | 9.7471
6.3333 | 2018-11-20 00:40 | 0.41627 | 2.0651
6.3403 | 2018-11-20 00:50 | 0.38715 | 11.7743
6.3472 | 2018-11-20 01:00 | 0.42075 | 6.5507
6.3542 | 2018-11-20 01:10 | 0.42075 | 6.5507
6.3611 | 2018-11-20 01:20 | 0.33036 | 5.2101
6.3681 | 2018-11-20 01:30 | 0.3342 | 11.9152
6.375 | 2018-11-20 01:40 | 0.25487 | 355.2737
6.3819 | 2018-11-20 01:50 | 0.28936 | 14.6125
6.3889 | 2018-11-20 02:00 | 0.1641 | 46.4815
6.3958 | 2018-11-20 02:10 | 0.1641 | 46.4815
6.4028 | 2018-11-20 02:20 | 0.15418 | 30.3902
6.4097 | 2018-11-20 02:30 | 0.09434 | 122.0054
6.4167 | 2018-11-20 02:40 | 0.033541 | 79.6951
6.4236 | 2018-11-20 02:50 | 0.16502 | 123.8827
6.4306 | 2018-11-20 03:00 | 0.21333 | 152.9545
6.4375 | 2018-11-20 03:10 | 0.21333 | 152.9545
6.4444 | 2018-11-20 03:20 | 0.38407 | 164.444
6.4514 | 2018-11-20 03:30 | 0.35273 | 167.2245
6.4583 | 2018-11-20 03:40 | 0.46936 | 174.253
6.4653 | 2018-11-20 03:50 | 0.49323 | 178.2573
6.4722 | 2018-11-20 04:00 | 0.54982 | 183.1278
6.4792 | 2018-11-20 04:10 | 0.54982 | 183.1278
6.4861 | 2018-11-20 04:20 | 0.58573 | 175.5938
6.4931 | 2018-11-20 04:30 | 0.74867 | 174.3275
6.5 | 2018-11-20 04:40 | 0.72006 | 179.2838
6.5069 | 2018-11-20 04:50 | 0.75701 | 182.9531
6.5139 | 2018-11-20 05:00 | 0.84304 | 180.5437
6.5208 | 2018-11-20 05:10 | 0.84304 | 180.5437
6.5278 | 2018-11-20 05:20 | 0.88307 | 180.7137
6.5347 | 2018-11-20 05:30 | 0.78547 | 183.5035
6.5417 | 2018-11-20 05:40 | 0.66427 | 188.4839
6.5486 | 2018-11-20 05:50 | 0.80508 | 179.2171
6.5556 | 2018-11-20 06:00 | 0.844 | 179.8642
6.5625 | 2018-11-20 06:10 | 0.844 | 179.8642
6.5694 | 2018-11-20 06:20 | 0.70526 | 181.5438
6.5764 | 2018-11-20 06:30 | 0.722 | 180.1587
6.5833 | 2018-11-20 06:40 | 0.69288 | 175.7789
6.5903 | 2018-11-20 06:50 | 0.74595 | 172.7607
6.5972 | 2018-11-20 07:00 | 0.73403 | 180.5464
6.6042 | 2018-11-20 07:10 | 0.73403 | 180.5464
6.6111 | 2018-11-20 07:20 | 0.77183 | 175.0946
6.6181 | 2018-11-20 07:30 | 0.64935 | 186.6325
6.625 | 2018-11-20 07:40 | 0.62318 | 181.3792
6.6319 | 2018-11-20 07:50 | 0.58989 | 170.0427
6.6389 | 2018-11-20 08:00 | 0.52502 | 180.4365
6.6458 | 2018-11-20 08:10 | 0.52502 | 180.4365
6.6528 | 2018-11-20 08:20 | 0.40022 | 171.6674
6.6597 | 2018-11-20 08:30 | 0.42668 | 171.5091
6.6667 | 2018-11-20 08:40 | 0.42072 | 174.8179
6.6736 | 2018-11-20 08:50 | 0.38933 | 164.9643
6.6806 | 2018-11-20 09:00 | 0.27965 | 165.7153
6.6875 | 2018-11-20 09:10 | 0.27965 | 165.7153
6.6944 | 2018-11-20 09:20 | 0.20891 | 154.7843
6.7014 | 2018-11-20 09:30 | 0.204 | 118.0725
6.7083 | 2018-11-20 09:40 | 0.10302 | 91.1124
6.7153 | 2018-11-20 09:50 | 0.10024 | 71.3843
6.7222 | 2018-11-20 10:00 | 0.19444 | 56.9638
6.7292 | 2018-11-20 10:10 | 0.19444 | 56.9638
6.7361 | 2018-11-20 10:20 | 0.30454 | 34.1597
6.7431 | 2018-11-20 10:30 | 0.37698 | 19.204
6.75 | 2018-11-20 10:40 | 0.36736 | 28.4486
6.7569 | 2018-11-20 10:50 | 0.36746 | 18.7308
6.7639 | 2018-11-20 11:00 | 0.40167 | 11.9254
6.7708 | 2018-11-20 11:10 | 0.40167 | 11.9254
6.7778 | 2018-11-20 11:20 | 0.50836 | 2.142
6.7847 | 2018-11-20 11:30 | 0.47077 | 6.2192
6.7917 | 2018-11-20 11:40 | 0.55039 | 6.3632
6.7986 | 2018-11-20 11:50 | 0.66974 | 11.1925
6.8056 | 2018-11-20 12:00 | 0.67936 | 10.946
6.8125 | 2018-11-20 12:10 | 0.67936 | 10.946
6.8194 | 2018-11-20 12:20 | 0.70346 | 9.4088
6.8264 | 2018-11-20 12:30 | 0.70914 | 4.4483
6.8333 | 2018-11-20 12:40 | 0.74402 | 0.46205
6.8403 | 2018-11-20 12:50 | 0.63114 | 9.7608
6.8472 | 2018-11-20 13:00 | 0.53146 | 8.2216
6.8542 | 2018-11-20 13:10 | 0.53146 | 8.2216
6.8611 | 2018-11-20 13:20 | 0.53736 | 6.4108
6.8681 | 2018-11-20 13:30 | 0.44703 | 6.6799
6.875 | 2018-11-20 13:40 | 0.42081 | 5.3177
6.8819 | 2018-11-20 13:50 | 0.34307 | 1.1691
6.8889 | 2018-11-20 14:00 | 0.3457 | 3.6487
6.8958 | 2018-11-20 14:10 | 0.3457 | 3.6487
6.9028 | 2018-11-20 14:20 | 0.23612 | 5.5899
6.9097 | 2018-11-20 14:30 | 0.1964 | 24.9993
6.9167 | 2018-11-20 14:40 | 0.1771 | 26.8544
6.9236 | 2018-11-20 14:50 | 0.15403 | 50.0039
6.9306 | 2018-11-20 15:00 | 0.084386 | 40.6749
6.9375 | 2018-11-20 15:10 | 0.084386 | 40.6749
6.9444 | 2018-11-20 15:20 | 0.14648 | 145.008
6.9514 | 2018-11-20 15:30 | 0.19623 | 166.7428
6.9583 | 2018-11-20 15:40 | 0.29466 | 156.3929
6.9653 | 2018-11-20 15:50 | 0.28805 | 164.0819
6.9722 | 2018-11-20 16:00 | 0.35813 | 173.7481
6.9792 | 2018-11-20 16:10 | 0.35813 | 173.7481
6.9861 | 2018-11-20 16:20 | 0.521 | 179.89
6.9931 | 2018-11-20 16:30 | 0.55567 | 175.5618
7 | 2018-11-20 16:40 | 0.55336 | 177.9287
7.0069 | 2018-11-20 16:50 | 0.50716 | 165.4979
7.0139 | 2018-11-20 17:00 | 0.58659 | 170.1844
7.0208 | 2018-11-20 17:10 | 0.58659 | 170.1844
7.0278 | 2018-11-20 17:20 | 0.63603 | 180.5405
7.0347 | 2018-11-20 17:30 | 0.75 | 179.8472
7.0417 | 2018-11-20 17:40 | 0.73626 | 176.6518
7.0486 | 2018-11-20 17:50 | 0.76132 | 174.6489
7.0556 | 2018-11-20 18:00 | 0.78936 | 175.5679
7.0625 | 2018-11-20 18:10 | 0.78936 | 175.5679
7.0694 | 2018-11-20 18:20 | 0.77171 | 177.5491
7.0764 | 2018-11-20 18:30 | 0.75212 | 176.8751
7.0833 | 2018-11-20 18:40 | 0.856 | 180
7.0903 | 2018-11-20 18:50 | 0.78418 | 173.4097
7.0972 | 2018-11-20 19:00 | 0.75995 | 177.1338
7.1042 | 2018-11-20 19:10 | 0.75995 | 177.1338
7.1111 | 2018-11-20 19:20 | 0.68118 | 176.6335
7.1181 | 2018-11-20 19:30 | 0.71355 | 177.7511
7.125 | 2018-11-20 19:40 | 0.73201 | 171.5157
7.1319 | 2018-11-20 19:50 | 0.68511 | 176.7367
7.1389 | 2018-11-20 20:00 | 0.65741 | 176.2497
7.1458 | 2018-11-20 20:10 | 0.65741 | 176.2497
7.1528 | 2018-11-20 20:20 | 0.5325 | 175.6921
7.1597 | 2018-11-20 20:30 | 0.47202 | 176.2344
7.1667 | 2018-11-20 20:40 | 0.51679 | 175.2272
7.1736 | 2018-11-20 20:50 | 0.4476 | 171.7794
7.1806 | 2018-11-20 21:00 | 0.3614 | 154.4276
7.1875 | 2018-11-20 21:10 | 0.3614 | 154.4276
7.1944 | 2018-11-20 21:20 | 0.29008 | 165.6284
7.2014 | 2018-11-20 21:30 | 0.2391 | 141.4525
7.2083 | 2018-11-20 21:40 | 0.20475 | 129.0531
7.2153 | 2018-11-20 21:50 | 0.18886 | 114.3937
7.2222 | 2018-11-20 22:00 | 0.15042 | 127.7079
7.2292 | 2018-11-20 22:10 | 0.15042 | 127.7079
7.2361 | 2018-11-20 22:20 | 0.26528 | 54.5125
7.2431 | 2018-11-20 22:30 | 0.25928 | 39.5226
7.25 | 2018-11-20 22:40 | 0.33944 | 26.4141
7.2569 | 2018-11-20 22:50 | 0.49073 | 25.2073
7.2639 | 2018-11-20 23:00 | 0.49142 | 18.5087
7.2708 | 2018-11-20 23:10 | 0.49142 | 18.5087
7.2778 | 2018-11-20 23:20 | 0.39913 | 1.4357
7.2847 | 2018-11-20 23:30 | 0.57405 | 7.6078
7.2917 | 2018-11-20 23:40 | 0.5621 | 6.025
7.2986 | 2018-11-20 23:50 | 0.67296 | 3.0665
7.3056 | 2018-11-21 | 0.83022 | 5.0445
7.3125 | 2018-11-21 00:10 | 0.83022 | 5.0445
7.3194 | 2018-11-21 00:20 | 0.75472 | 10.5357
7.3264 | 2018-11-21 00:30 | 0.75942 | 5.4403
7.3333 | 2018-11-21 00:40 | 0.68854 | 3.8307
7.3403 | 2018-11-21 00:50 | 0.81271 | 2.3977
7.3472 | 2018-11-21 01:00 | 0.8534 | 4.3009
7.3542 | 2018-11-21 01:10 | 0.8534 | 4.3009
7.3611 | 2018-11-21 01:20 | 0.65428 | 1.6641
7.3681 | 2018-11-21 01:30 | 0.53502 | 359.4645
7.375 | 2018-11-21 01:40 | 0.52627 | 1.8511
7.3819 | 2018-11-21 01:50 | 0.55065 | 354.3722
7.3889 | 2018-11-21 02:00 | 0.4848 | 6.1575
7.3958 | 2018-11-21 02:10 | 0.4848 | 6.1575
7.4028 | 2018-11-21 02:20 | 0.42417 | 351.0484
7.4097 | 2018-11-21 02:30 | 0.32439 | 5.3064
7.4167 | 2018-11-21 02:40 | 0.38213 | 358.5005
7.4236 | 2018-11-21 02:50 | 0.35114 | 1.6319
7.4306 | 2018-11-21 03:00 | 0.30903 | 359.2584
7.4375 | 2018-11-21 03:10 | 0.30903 | 359.2584
7.4444 | 2018-11-21 03:20 | 0.17514 | 10.8608
7.4514 | 2018-11-21 03:30 | 0.029428 | 350.2176
7.4583 | 2018-11-21 03:40 | 0.12108 | 67.6713
7.4653 | 2018-11-21 03:50 | 0.093048 | 181.8476
7.4722 | 2018-11-21 04:00 | 0.18659 | 170.4367
7.4792 | 2018-11-21 04:10 | 0.18659 | 170.4367
7.4861 | 2018-11-21 04:20 | 0.34947 | 185.2538
7.4931 | 2018-11-21 04:30 | 0.4095 | 184.9031
7.5 | 2018-11-21 04:40 | 0.56315 | 187.756
7.5069 | 2018-11-21 04:50 | 0.46592 | 189.8869
7.5139 | 2018-11-21 05:00 | 0.44729 | 175.6406
7.5208 | 2018-11-21 05:10 | 0.44729 | 175.6406
7.5278 | 2018-11-21 05:20 | 0.4979 | 176.5457
7.5347 | 2018-11-21 05:30 | 0.55634 | 185.2597
7.5417 | 2018-11-21 05:40 | 0.60148 | 182.2868
7.5486 | 2018-11-21 05:50 | 0.61543 | 182.1418
7.5556 | 2018-11-21 06:00 | 0.642 | 180.1785
7.5625 | 2018-11-21 06:10 | 0.642 | 180.1785
7.5694 | 2018-11-21 06:20 | 0.59801 | 180.3832
7.5764 | 2018-11-21 06:30 | 0.65734 | 178.1693
7.5833 | 2018-11-21 06:40 | 0.67593 | 175.6728
7.5903 | 2018-11-21 06:50 | 0.60924 | 181.599
7.5972 | 2018-11-21 07:00 | 0.65056 | 182.3786
7.6042 | 2018-11-21 07:10 | 0.65056 | 182.3786
7.6111 | 2018-11-21 07:20 | 0.57109 | 181.0033
7.6181 | 2018-11-21 07:30 | 0.53524 | 178.287
7.625 | 2018-11-21 07:40 | 0.61994 | 175.4666
7.6319 | 2018-11-21 07:50 | 0.48682 | 175.0506
7.6389 | 2018-11-21 08:00 | 0.45705 | 179.1225
7.6458 | 2018-11-21 08:10 | 0.45705 | 179.1225
7.6528 | 2018-11-21 08:20 | 0.40052 | 169.644
7.6597 | 2018-11-21 08:30 | 0.41754 | 173.675
7.6667 | 2018-11-21 08:40 | 0.41932 | 169.2796
7.6736 | 2018-11-21 08:50 | 0.36401 | 164.0546
7.6806 | 2018-11-21 09:00 | 0.35461 | 170.7502
7.6875 | 2018-11-21 09:10 | 0.35461 | 170.7502
7.6944 | 2018-11-21 09:20 | 0.19773 | 167.4398
7.7014 | 2018-11-21 09:30 | 0.11512 | 147.4143
7.7083 | 2018-11-21 09:40 | 0.099005 | 113.1986
7.7153 | 2018-11-21 09:50 | 0.15915 | 87.4792
7.7222 | 2018-11-21 10:00 | 0.17963 | 17.8297
7.7292 | 2018-11-21 10:10 | 0.17963 | 17.8297
7.7361 | 2018-11-21 10:20 | 0.31945 | 17.3005
7.7431 | 2018-11-21 10:30 | 0.46229 | 9.4623
7.75 | 2018-11-21 10:40 | 0.56004 | 8.4195
7.7569 | 2018-11-21 10:50 | 0.584 | 0
7.7639 | 2018-11-21 11:00 | 0.51422 | 358.3284
7.7708 | 2018-11-21 11:10 | 0.51422 | 358.3284
7.7778 | 2018-11-21 11:20 | 0.86533 | 3.1798
7.7847 | 2018-11-21 11:30 | 0.78352 | 6.1545
7.7917 | 2018-11-21 11:40 | 0.89528 | 11.5986
7.7986 | 2018-11-21 11:50 | 0.84091 | 9.6527
7.8056 | 2018-11-21 12:00 | 0.86561 | 5.2364
7.8125 | 2018-11-21 12:10 | 0.86561 | 5.2364
7.8194 | 2018-11-21 12:20 | 0.89331 | 11.2973
7.8264 | 2018-11-21 12:30 | 0.88858 | 3.4195
7.8333 | 2018-11-21 12:40 | 0.87308 | 7.3041
7.8403 | 2018-11-21 12:50 | 0.76739 | 5.3837
7.8472 | 2018-11-21 13:00 | 0.76245 | 3.5341
7.8542 | 2018-11-21 13:10 | 0.76245 | 3.5341
7.8611 | 2018-11-21 13:20 | 0.73925 | 3.3346
7.8681 | 2018-11-21 13:30 | 0.69837 | 9.3949
7.875 | 2018-11-21 13:40 | 0.48234 | 357.8613
7.8819 | 2018-11-21 13:50 | 0.58986 | 354.3571
7.8889 | 2018-11-21 14:00 | 0.51582 | 3.223
7.8958 | 2018-11-21 14:10 | 0.51582 | 3.223
7.9028 | 2018-11-21 14:20 | 0.47245 | 4.4917
7.9097 | 2018-11-21 14:30 | 0.422 | 354.4245
7.9167 | 2018-11-21 14:40 | 0.35681 | 8.3799
7.9236 | 2018-11-21 14:50 | 0.37926 | 357.8845
7.9306 | 2018-11-21 15:00 | 0.30487 | 355.6734
7.9375 | 2018-11-21 15:10 | 0.30487 | 355.6734
7.9444 | 2018-11-21 15:20 | 0.26305 | 1.0891
7.9514 | 2018-11-21 15:30 | 0.17477 | 309.4278
7.9583 | 2018-11-21 15:40 | 0.091706 | 332.0378
7.9653 | 2018-11-21 15:50 | 0.14012 | 312.6863
7.9722 | 2018-11-21 16:00 | 0.17282 | 318.2839
7.9792 | 2018-11-21 16:10 | 0.17282 | 318.2839
7.9861 | 2018-11-21 16:20 | 0.15318 | 240.2551
7.9931 | 2018-11-21 16:30 | 0.2942 | 216.9868
8 | 2018-11-21 16:40 | 0.26707 | 221.5088
8.0069 | 2018-11-21 16:50 | 0.41208 | 196.06
8.0139 | 2018-11-21 17:00 | 0.39736 | 200.1679
8.0208 | 2018-11-21 17:10 | 0.39736 | 200.1679
8.0278 | 2018-11-21 17:20 | 0.64103 | 192.4319
8.0347 | 2018-11-21 17:30 | 0.63898 | 192.84
8.0417 | 2018-11-21 17:40 | 0.67862 | 193.811
8.0486 | 2018-11-21 17:50 | 0.72314 | 181.1093
8.0556 | 2018-11-21 18:00 | 0.59064 | 184.2722
8.0625 | 2018-11-21 18:10 | 0.59064 | 184.2722
8.0694 | 2018-11-21 18:20 | 0.71137 | 181.8528
8.0764 | 2018-11-21 18:30 | 0.64694 | 184.4327
8.0833 | 2018-11-21 18:40 | 0.79586 | 177.3353
8.0903 | 2018-11-21 18:50 | 0.78131 | 175.5957
8.0972 | 2018-11-21 19:00 | 0.82205 | 180.6273
8.1042 | 2018-11-21 19:10 | 0.82205 | 180.6273
8.1111 | 2018-11-21 19:20 | 0.78303 | 179.4878
8.1181 | 2018-11-21 19:30 | 0.75952 | 182.1127
8.125 | 2018-11-21 19:40 | 0.79716 | 181.1501
8.1319 | 2018-11-21 19:50 | 0.75614 | 185.9971
8.1389 | 2018-11-21 20:00 | 0.61403 | 180.5599
8.1458 | 2018-11-21 20:10 | 0.61403 | 180.5599
8.1528 | 2018-11-21 20:20 | 0.621 | 180.1845
8.1597 | 2018-11-21 20:30 | 0.6051 | 181.0416
8.1667 | 2018-11-21 20:40 | 0.52591 | 183.3793
8.1736 | 2018-11-21 20:50 | 0.38865 | 161.7049
8.1806 | 2018-11-21 21:00 | 0.39715 | 181.5871
8.1875 | 2018-11-21 21:10 | 0.39715 | 181.5871
8.1944 | 2018-11-21 21:20 | 0.32374 | 172.5457
8.2014 | 2018-11-21 21:30 | 0.35524 | 182.0972
8.2083 | 2018-11-21 21:40 | 0.20535 | 171.3175
8.2153 | 2018-11-21 21:50 | 0.186 | 133.9109
8.2222 | 2018-11-21 22:00 | 0.23629 | 128.4705
8.2292 | 2018-11-21 22:10 | 0.23629 | 128.4705
8.2361 | 2018-11-21 22:20 | 0.26369 | 23.9404
8.2431 | 2018-11-21 22:30 | 0.35296 | 19.359
8.25 | 2018-11-21 22:40 | 0.37511 | 29.0249
8.2569 | 2018-11-21 22:50 | 0.44849 | 9.7564
8.2639 | 2018-11-21 23:00 | 0.5295 | 17.1346
8.2708 | 2018-11-21 23:10 | 0.5295 | 17.1346
8.2778 | 2018-11-21 23:20 | 0.56371 | 8.1589
8.2847 | 2018-11-21 23:30 | 0.62423 | 8.1041
8.2917 | 2018-11-21 23:40 | 0.64874 | 9.9415
8.2986 | 2018-11-21 23:50 | 0.80409 | 0.8551
8.3056 | 2018-11-22 | 0.81565 | 6.123
8.3125 | 2018-11-22 00:10 | 0.81565 | 6.123
8.3194 | 2018-11-22 00:20 | 0.78362 | 7.9957
8.3264 | 2018-11-22 00:30 | 0.80863 | 2.268
8.3333 | 2018-11-22 00:40 | 0.67012 | 8.9282
8.3403 | 2018-11-22 00:50 | 0.83482 | 9.2367
8.3472 | 2018-11-22 01:00 | 0.76934 | 7.9195
8.3542 | 2018-11-22 01:10 | 0.76934 | 7.9195
8.3611 | 2018-11-22 01:20 | 0.83755 | 5.2749
8.3681 | 2018-11-22 01:30 | 0.67209 | 0.93779
8.375 | 2018-11-22 01:40 | 0.721 | 356.9789
8.3819 | 2018-11-22 01:50 | 0.63952 | 3.9452
8.3889 | 2018-11-22 02:00 | 0.65548 | 3.849
8.3958 | 2018-11-22 02:10 | 0.65548 | 3.849
8.4028 | 2018-11-22 02:20 | 0.50534 | 12.6887
8.4097 | 2018-11-22 02:30 | 0.46903 | 0.61081
8.4167 | 2018-11-22 02:40 | 0.42327 | 2.0309
8.4236 | 2018-11-22 02:50 | 0.4697 | 11.0468
8.4306 | 2018-11-22 03:00 | 0.33207 | 358.7921
8.4375 | 2018-11-22 03:10 | 0.33207 | 358.7921
8.4444 | 2018-11-22 03:20 | 0.28984 | 9.3323
8.4514 | 2018-11-22 03:30 | 0.1575 | 347.9052
8.4583 | 2018-11-22 03:40 | 0.2478 | 343.8323
8.4653 | 2018-11-22 03:50 | 0.07 | 0
8.4722 | 2018-11-22 04:00 | 0.077058 | 267.7688
8.4792 | 2018-11-22 04:10 | 0.077058 | 267.7688
8.4861 | 2018-11-22 04:20 | 0.13453 | 237.1368
8.4931 | 2018-11-22 04:30 | 0.21915 | 214.7778
8.5 | 2018-11-22 04:40 | 0.29903 | 214.6467
8.5069 | 2018-11-22 04:50 | 0.35293 | 197.8189
8.5139 | 2018-11-22 05:00 | 0.49604 | 200.0423
8.5208 | 2018-11-22 05:10 | 0.49604 | 200.0423
8.5278 | 2018-11-22 05:20 | 0.58793 | 188.8054
8.5347 | 2018-11-22 05:30 | 0.72672 | 190.3048
8.5417 | 2018-11-22 05:40 | 0.59821 | 183.6421
8.5486 | 2018-11-22 05:50 | 0.6432 | 178.5746
8.5556 | 2018-11-22 06:00 | 0.80971 | 182.4066
8.5625 | 2018-11-22 06:10 | 0.80971 | 182.4066
8.5694 | 2018-11-22 06:20 | 0.81579 | 183.7954
8.5764 | 2018-11-22 06:30 | 0.87574 | 182.356
8.5833 | 2018-11-22 06:40 | 0.86181 | 185.3931
8.5903 | 2018-11-22 06:50 | 0.7649 | 182.7726
8.5972 | 2018-11-22 07:00 | 0.82155 | 182.0927
8.6042 | 2018-11-22 07:10 | 0.82155 | 182.0927
8.6111 | 2018-11-22 07:20 | 0.75547 | 184.6314
8.6181 | 2018-11-22 07:30 | 0.87806 | 186.7365
8.625 | 2018-11-22 07:40 | 0.74932 | 178.3176
8.6319 | 2018-11-22 07:50 | 0.77681 | 183.9122
8.6389 | 2018-11-22 08:00 | 0.72607 | 179.2108
8.6458 | 2018-11-22 08:10 | 0.72607 | 179.2108
8.6528 | 2018-11-22 08:20 | 0.59654 | 185.2901
8.6597 | 2018-11-22 08:30 | 0.58834 | 181.9481
8.6667 | 2018-11-22 08:40 | 0.58174 | 175.5635
8.6736 | 2018-11-22 08:50 | 0.46452 | 182.7146
8.6806 | 2018-11-22 09:00 | 0.46279 | 170.1713
8.6875 | 2018-11-22 09:10 | 0.46279 | 170.1713
8.6944 | 2018-11-22 09:20 | 0.33718 | 178.1305
8.7014 | 2018-11-22 09:30 | 0.38733 | 177.6325
8.7083 | 2018-11-22 09:40 | 0.26189 | 170.1061
8.7153 | 2018-11-22 09:50 | 0.22543 | 171.5823
8.7222 | 2018-11-22 10:00 | 0.16553 | 168.147
8.7292 | 2018-11-22 10:10 | 0.16553 | 168.147
8.7361 | 2018-11-22 10:20 | 0.045222 | 341.9657
8.7431 | 2018-11-22 10:30 | 0.2327 | 4.4365
8.75 | 2018-11-22 10:40 | 0.40804 | 17.1027
8.7569 | 2018-11-22 10:50 | 0.42856 | 17.3779
8.7639 | 2018-11-22 11:00 | 0.54173 | 19.0704
8.7708 | 2018-11-22 11:10 | 0.54173 | 19.0704
8.7778 | 2018-11-22 11:20 | 0.5525 | 10.6388
8.7847 | 2018-11-22 11:30 | 0.62092 | 11.7081
8.7917 | 2018-11-22 11:40 | 0.61839 | 11.9459
8.7986 | 2018-11-22 11:50 | 0.73579 | 2.6485
8.8056 | 2018-11-22 12:00 | 0.81469 | 10.8962
8.8125 | 2018-11-22 12:10 | 0.81469 | 10.8962
8.8194 | 2018-11-22 12:20 | 0.73751 | 7.0094
8.8264 | 2018-11-22 12:30 | 0.77218 | 4.3077
8.8333 | 2018-11-22 12:40 | 0.88973 | 9.3141
8.8403 | 2018-11-22 12:50 | 0.86201 | 8.7411
8.8472 | 2018-11-22 13:00 | 0.94309 | 6.5146
8.8542 | 2018-11-22 13:10 | 0.94309 | 6.5146
8.8611 | 2018-11-22 13:20 | 0.77902 | 4.1223
8.8681 | 2018-11-22 13:30 | 0.74265 | 8.752
8.875 | 2018-11-22 13:40 | 0.79957 | 4.5911
8.8819 | 2018-11-22 13:50 | 0.64069 | 9.9769
8.8889 | 2018-11-22 14:00 | 0.7124 | 1.9306
8.8958 | 2018-11-22 14:10 | 0.7124 | 1.9306
8.9028 | 2018-11-22 14:20 | 0.68374 | 9.6827
8.9097 | 2018-11-22 14:30 | 0.59403 | 359.4213
8.9167 | 2018-11-22 14:40 | 0.53601 | 0.42757
8.9236 | 2018-11-22 14:50 | 0.47808 | 9.8761
8.9306 | 2018-11-22 15:00 | 0.41312 | 1.387
8.9375 | 2018-11-22 15:10 | 0.41312 | 1.387
8.9444 | 2018-11-22 15:20 | 0.31694 | 353.6598
8.9514 | 2018-11-22 15:30 | 0.24616 | 343.4791
8.9583 | 2018-11-22 15:40 | 0.26809 | 1.4962
8.9653 | 2018-11-22 15:50 | 0.24205 | 346.136
8.9722 | 2018-11-22 16:00 | 0.18502 | 0.92904
8.9792 | 2018-11-22 16:10 | 0.18502 | 0.92904
8.9861 | 2018-11-22 16:20 | 0.1053 | 274.357
8.9931 | 2018-11-22 16:30 | 0.047413 | 242.354
9 | 2018-11-22 16:40 | 0.12761 | 217.6781
9.0069 | 2018-11-22 16:50 | 0.26854 | 202.5542
9.0139 | 2018-11-22 17:00 | 0.39184 | 205.3879
9.0208 | 2018-11-22 17:10 | 0.39184 | 205.3879
9.0278 | 2018-11-22 17:20 | 0.45626 | 194.8586
9.0347 | 2018-11-22 17:30 | 0.53172 | 192.0496
9.0417 | 2018-11-22 17:40 | 0.60003 | 194.0826
9.0486 | 2018-11-22 17:50 | 0.66536 | 184.828
9.0556 | 2018-11-22 18:00 | 0.58488 | 185.6911
9.0625 | 2018-11-22 18:10 | 0.58488 | 185.6911
9.0694 | 2018-11-22 18:20 | 0.74813 | 181.0723
9.0764 | 2018-11-22 18:30 | 0.74185 | 187.2017
9.0833 | 2018-11-22 18:40 | 0.80787 | 183.9037
9.0903 | 2018-11-22 18:50 | 0.71245 | 184.7503
9.0972 | 2018-11-22 19:00 | 0.763 | 182.9299
9.1042 | 2018-11-22 19:10 | 0.763 | 182.9299
9.1111 | 2018-11-22 19:20 | 0.74204 | 180.6177
9.1181 | 2018-11-22 19:30 | 0.79711 | 183.0203
9.125 | 2018-11-22 19:40 | 0.87355 | 182.0337
9.1319 | 2018-11-22 19:50 | 0.79202 | 180.3617
9.1389 | 2018-11-22 20:00 | 0.76335 | 181.7266
9.1458 | 2018-11-22 20:10 | 0.76335 | 181.7266
9.1528 | 2018-11-22 20:20 | 0.73964 | 171.7603
9.1597 | 2018-11-22 20:30 | 0.68679 | 177.2459
9.1667 | 2018-11-22 20:40 | 0.58553 | 177.5529
9.1736 | 2018-11-22 20:50 | 0.69801 | 179.7537
9.1806 | 2018-11-22 21:00 | 0.56095 | 170.9743
9.1875 | 2018-11-22 21:10 | 0.56095 | 170.9743
9.1944 | 2018-11-22 21:20 | 0.6291 | 178.9981
9.2014 | 2018-11-22 21:30 | 0.46624 | 189.3815
9.2083 | 2018-11-22 21:40 | 0.51919 | 178.4548
9.2153 | 2018-11-22 21:50 | 0.39588 | 163.7166
9.2222 | 2018-11-22 22:00 | 0.40273 | 167.3786
9.2292 | 2018-11-22 22:10 | 0.40273 | 167.3786
9.2361 | 2018-11-22 22:20 | 0.34928 | 177.7028
9.2431 | 2018-11-22 22:30 | 0.14819 | 166.3389
9.25 | 2018-11-22 22:40 | 0.13685 | 153.9967
9.2569 | 2018-11-22 22:50 | 0.010296 | 119.0546
9.2639 | 2018-11-22 23:00 | 0.090802 | 36.4913
9.2708 | 2018-11-22 23:10 | 0.090802 | 36.4913
9.2778 | 2018-11-22 23:20 | 0.44055 | 15.2665
9.2847 | 2018-11-22 23:30 | 0.51893 | 18.1905
9.2917 | 2018-11-22 23:40 | 0.48036 | 16.3222
9.2986 | 2018-11-22 23:50 | 0.5179 | 15.1096
9.3056 | 2018-11-23 | 0.56032 | 7.8987
9.3125 | 2018-11-23 00:10 | 0.56032 | 7.8987
9.3194 | 2018-11-23 00:20 | 0.70678 | 5.9284
9.3264 | 2018-11-23 00:30 | 0.82592 | 6.2559
9.3333 | 2018-11-23 00:40 | 0.78712 | 7.1521
9.3403 | 2018-11-23 00:50 | 0.88005 | 9.0877
9.3472 | 2018-11-23 01:00 | 0.88178 | 4.5532
9.3542 | 2018-11-23 01:10 | 0.88178 | 4.5532
9.3611 | 2018-11-23 01:20 | 0.91873 | 6.9394
9.3681 | 2018-11-23 01:30 | 0.8713 | 6.3257
9.375 | 2018-11-23 01:40 | 0.78858 | 11.4097
9.3819 | 2018-11-23 01:50 | 0.90935 | 4.9206
9.3889 | 2018-11-23 02:00 | 0.79755 | 7.3478
9.3958 | 2018-11-23 02:10 | 0.79755 | 7.3478
9.4028 | 2018-11-23 02:20 | 0.75452 | 2.1267
9.4097 | 2018-11-23 02:30 | 0.66747 | 5.8473
9.4167 | 2018-11-23 02:40 | 0.68309 | 9.8622
9.4236 | 2018-11-23 02:50 | 0.59468 | 7.9257
9.4306 | 2018-11-23 03:00 | 0.48507 | 359.055
9.4375 | 2018-11-23 03:10 | 0.48507 | 359.055
9.4444 | 2018-11-23 03:20 | 0.4561 | 12.6651
9.4514 | 2018-11-23 03:30 | 0.38433 | 355.224
9.4583 | 2018-11-23 03:40 | 0.413 | 0.27746
9.4653 | 2018-11-23 03:50 | 0.29317 | 351.5659
9.4722 | 2018-11-23 04:00 | 0.33612 | 358.4657
9.4792 | 2018-11-23 04:10 | 0.33612 | 358.4657
9.4861 | 2018-11-23 04:20 | 0.056223 | 5.1022
9.4931 | 2018-11-23 04:30 | 0.090139 | 319.9503
9.5 | 2018-11-23 04:40 | 0.13153 | 298.1237
9.5069 | 2018-11-23 04:50 | 0.11927 | 213.0239
9.5139 | 2018-11-23 05:00 | 0.14903 | 215.7164
9.5208 | 2018-11-23 05:10 | 0.14903 | 215.7164
9.5278 | 2018-11-23 05:20 | 0.38509 | 207.3635
9.5347 | 2018-11-23 05:30 | 0.50948 | 200.5692
9.5417 | 2018-11-23 05:40 | 0.48437 | 196.6766
9.5486 | 2018-11-23 05:50 | 0.47974 | 188.8733
9.5556 | 2018-11-23 06:00 | 0.596 | 179.9039
9.5625 | 2018-11-23 06:10 | 0.596 | 179.9039
9.5694 | 2018-11-23 06:20 | 0.56769 | 182.8271
9.5764 | 2018-11-23 06:30 | 0.67419 | 181.3599
9.5833 | 2018-11-23 06:40 | 0.63448 | 185.0636
9.5903 | 2018-11-23 06:50 | 0.706 | 180.1623
9.5972 | 2018-11-23 07:00 | 0.7225 | 175.2364
9.6042 | 2018-11-23 07:10 | 0.7225 | 175.2364
9.6111 | 2018-11-23 07:20 | 0.83295 | 175.1792
9.6181 | 2018-11-23 07:30 | 0.89035 | 183.1548
9.625 | 2018-11-23 07:40 | 0.77219 | 181.2615
9.6319 | 2018-11-23 07:50 | 0.74604 | 189.4118
9.6389 | 2018-11-23 08:00 | 0.79905 | 180.6454
9.6458 | 2018-11-23 08:10 | 0.79905 | 180.6454
9.6528 | 2018-11-23 08:20 | 0.74539 | 185.4658
9.6597 | 2018-11-23 08:30 | 0.7631 | 185.9422
9.6667 | 2018-11-23 08:40 | 0.64319 | 185.7106
9.6736 | 2018-11-23 08:50 | 0.72716 | 184.4168
9.6806 | 2018-11-23 09:00 | 0.68162 | 177.5616
9.6875 | 2018-11-23 09:10 | 0.68162 | 177.5616
9.6944 | 2018-11-23 09:20 | 0.5226 | 177.258
9.7014 | 2018-11-23 09:30 | 0.61524 | 176.3656
9.7083 | 2018-11-23 09:40 | 0.44482 | 186.454
9.7153 | 2018-11-23 09:50 | 0.41018 | 187.1423
9.7222 | 2018-11-23 10:00 | 0.44047 | 184.688
9.7292 | 2018-11-23 10:10 | 0.44047 | 184.688
9.7361 | 2018-11-23 10:20 | 0.32489 | 173.8156
9.7431 | 2018-11-23 10:30 | 0.21115 | 157.4427
9.75 | 2018-11-23 10:40 | 0.12914 | 149.2645
9.7569 | 2018-11-23 10:50 | 0.13473 | 95.9645
9.7639 | 2018-11-23 11:00 | 0.12104 | 51.7098
9.7708 | 2018-11-23 11:10 | 0.12104 | 51.7098
9.7778 | 2018-11-23 11:20 | 0.432 | 20.7423
9.7847 | 2018-11-23 11:30 | 0.47919 | 24.8002
9.7917 | 2018-11-23 11:40 | 0.5605 | 13.9371
9.7986 | 2018-11-23 11:50 | 0.58349 | 2.3573
9.8056 | 2018-11-23 12:00 | 0.54096 | 4.878
9.8125 | 2018-11-23 12:10 | 0.54096 | 4.878
9.8194 | 2018-11-23 12:20 | 0.68364 | 5.0351
9.8264 | 2018-11-23 12:30 | 0.84765 | 7.1837
9.8333 | 2018-11-23 12:40 | 0.81317 | 8.1301
9.8403 | 2018-11-23 12:50 | 0.83449 | 9.5188
9.8472 | 2018-11-23 13:00 | 0.89429 | 13.3836
9.8542 | 2018-11-23 13:10 | 0.89429 | 13.3836
9.8611 | 2018-11-23 13:20 | 0.85751 | 9.3964
9.8681 | 2018-11-23 13:30 | 0.88186 | 9.003
9.875 | 2018-11-23 13:40 | 0.86722 | 3.0406
9.8819 | 2018-11-23 13:50 | 0.80103 | 12.1797
9.8889 | 2018-11-23 14:00 | 0.85693 | 5.491
9.8958 | 2018-11-23 14:10 | 0.85693 | 5.491
9.9028 | 2018-11-23 14:20 | 0.89464 | 7.9671
9.9097 | 2018-11-23 14:30 | 0.77954 | 6.186
9.9167 | 2018-11-23 14:40 | 0.74015 | 9.9587
9.9236 | 2018-11-23 14:50 | 0.72897 | 6.6961
9.9306 | 2018-11-23 15:00 | 0.65878 | 10.8494
9.9375 | 2018-11-23 15:10 | 0.65878 | 10.8494
9.9444 | 2018-11-23 15:20 | 0.53572 | 6.7536
9.9514 | 2018-11-23 15:30 | 0.46797 | 8.3552
9.9583 | 2018-11-23 15:40 | 0.436 | 0.26282
9.9653 | 2018-11-23 15:50 | 0.4616 | 8.095
9.9722 | 2018-11-23 16:00 | 0.43204 | 3.9817
9.9792 | 2018-11-23 16:10 | 0.43204 | 3.9817
9.9861 | 2018-11-23 16:20 | 0.3711 | 351.4769
9.9931 | 2018-11-23 16:30 | 0.32035 | 357.3162
10 | 2018-11-23 16:40 | 0.23368 | 6.8817
10.0069 | 2018-11-23 16:50 | 0.13553 | 332.3005
10.0139 | 2018-11-23 17:00 | 0.14632 | 335.3616
10.0208 | 2018-11-23 17:10 | 0.14632 | 335.3616
10.0278 | 2018-11-23 17:20 | 0.14036 | 229.0445
10.0347 | 2018-11-23 17:30 | 0.24784 | 215.8064
10.0417 | 2018-11-23 17:40 | 0.3286 | 216.835
10.0486 | 2018-11-23 17:50 | 0.39131 | 206.565
10.0556 | 2018-11-23 18:00 | 0.44724 | 193.9741
10.0625 | 2018-11-23 18:10 | 0.44724 | 193.9741
10.0694 | 2018-11-23 18:20 | 0.54187 | 189.132
10.0764 | 2018-11-23 18:30 | 0.55324 | 187.8958
10.0833 | 2018-11-23 18:40 | 0.69826 | 183.4484
10.0903 | 2018-11-23 18:50 | 0.68689 | 177.0793
10.0972 | 2018-11-23 19:00 | 0.64261 | 182.4973
10.1042 | 2018-11-23 19:10 | 0.64261 | 182.4973
10.1111 | 2018-11-23 19:20 | 0.73978 | 186.5198
10.1181 | 2018-11-23 19:30 | 0.70863 | 183.884
10.125 | 2018-11-23 19:40 | 0.85008 | 180.8088
10.1319 | 2018-11-23 19:50 | 0.75205 | 186.6431
10.1389 | 2018-11-23 20:00 | 0.81094 | 182.7566
10.1458 | 2018-11-23 20:10 | 0.81094 | 182.7566
10.1528 | 2018-11-23 20:20 | 0.7973 | 187.2052
10.1597 | 2018-11-23 20:30 | 0.963 | 183.6914
10.1667 | 2018-11-23 20:40 | 0.81448 | 181.9701
10.1736 | 2018-11-23 20:50 | 0.80496 | 184.9173
10.1806 | 2018-11-23 21:00 | 0.7087 | 183.9647
10.1875 | 2018-11-23 21:10 | 0.7087 | 183.9647
10.1944 | 2018-11-23 21:20 | 0.71681 | 177.2813
10.2014 | 2018-11-23 21:30 | 0.65601 | 179.738
10.2083 | 2018-11-23 21:40 | 0.68001 | 180.337
10.2153 | 2018-11-23 21:50 | 0.59016 | 176.4055
10.2222 | 2018-11-23 22:00 | 0.57315 | 173.991
10.2292 | 2018-11-23 22:10 | 0.57315 | 173.991
10.2361 | 2018-11-23 22:20 | 0.57377 | 175.5017
10.2431 | 2018-11-23 22:30 | 0.51487 | 183.3403
10.25 | 2018-11-23 22:40 | 0.44554 | 175.2364
10.2569 | 2018-11-23 22:50 | 0.23114 | 181.9835
10.2639 | 2018-11-23 23:00 | 0.26955 | 172.1104
10.2708 | 2018-11-23 23:10 | 0.26955 | 172.1104
10.2778 | 2018-11-23 23:20 | 0.10555 | 154.1632
10.2847 | 2018-11-23 23:30 | 0.049649 | 18.7999
10.2917 | 2018-11-23 23:40 | 0.19912 | 2.0146
10.2986 | 2018-11-23 23:50 | 0.32674 | 24.2117
10.3056 | 2018-11-24 | 0.43442 | 14.804
10.3125 | 2018-11-24 00:10 | 0.43442 | 14.804
10.3194 | 2018-11-24 00:20 | 0.5493 | 18.7978
10.3264 | 2018-11-24 00:30 | 0.62912 | 15.5826
10.3333 | 2018-11-24 00:40 | 0.61518 | 9.3551
10.3403 | 2018-11-24 00:50 | 0.73212 | 11.6629
10.3472 | 2018-11-24 01:00 | 0.81079 | 6.2309
10.3542 | 2018-11-24 01:10 | 0.81079 | 6.2309
10.3611 | 2018-11-24 01:20 | 0.70921 | 4.5288
10.3681 | 2018-11-24 01:30 | 0.77981 | 6.9974
10.375 | 2018-11-24 01:40 | 0.87457 | 12.1451
10.3819 | 2018-11-24 01:50 | 0.85177 | 9.1195
10.3889 | 2018-11-24 02:00 | 0.83627 | 13.8368
10.3958 | 2018-11-24 02:10 | 0.83627 | 13.8368
10.4028 | 2018-11-24 02:20 | 0.813 | 0
10.4097 | 2018-11-24 02:30 | 0.70323 | 6.2862
10.4167 | 2018-11-24 02:40 | 0.75556 | 2.1997
10.4236 | 2018-11-24 02:50 | 0.59065 | 7.1972
10.4306 | 2018-11-24 03:00 | 0.69572 | 7.3497
10.4375 | 2018-11-24 03:10 | 0.69572 | 7.3497
10.4444 | 2018-11-24 03:20 | 0.5891 | 358.9301
10.4514 | 2018-11-24 03:30 | 0.59698 | 8.7681
10.4583 | 2018-11-24 03:40 | 0.61988 | 3.0517
10.4653 | 2018-11-24 03:50 | 0.58541 | 357.8463
10.4722 | 2018-11-24 04:00 | 0.46824 | 358.1642
10.4792 | 2018-11-24 04:10 | 0.46824 | 358.1642
10.4861 | 2018-11-24 04:20 | 0.38034 | 2.411
10.4931 | 2018-11-24 04:30 | 0.38401 | 0.44761
10.5 | 2018-11-24 04:40 | 0.2939 | 355.5116
10.5069 | 2018-11-24 04:50 | 0.18118 | 357.4692
10.5139 | 2018-11-24 05:00 | 0.17214 | 357.6695
10.5208 | 2018-11-24 05:10 | 0.17214 | 357.6695
10.5278 | 2018-11-24 05:20 | 0.13238 | 296.9522
10.5347 | 2018-11-24 05:30 | 0.15121 | 230.0974
10.5417 | 2018-11-24 05:40 | 0.19387 | 213.854
10.5486 | 2018-11-24 05:50 | 0.25547 | 208.2704
10.5556 | 2018-11-24 06:00 | 0.44632 | 199.7747
10.5625 | 2018-11-24 06:10 | 0.44632 | 199.7747
10.5694 | 2018-11-24 06:20 | 0.69636 | 188.3396
10.5764 | 2018-11-24 06:30 | 0.61912 | 181.1106
10.5833 | 2018-11-24 06:40 | 0.61136 | 178.0315
10.5903 | 2018-11-24 06:50 | 0.60575 | 175.6448
10.5972 | 2018-11-24 07:00 | 0.64371 | 186.1534
10.6042 | 2018-11-24 07:10 | 0.64371 | 186.1534
10.6111 | 2018-11-24 07:20 | 0.84664 | 182.2338
10.6181 | 2018-11-24 07:30 | 0.78346 | 184.5389
10.625 | 2018-11-24 07:40 | 0.89615 | 183.9672
10.6319 | 2018-11-24 07:50 | 0.80704 | 179.432
10.6389 | 2018-11-24 08:00 | 0.80303 | 184.0704
10.6458 | 2018-11-24 08:10 | 0.80303 | 184.0704
10.6528 | 2018-11-24 08:20 | 0.92252 | 181.9257
10.6597 | 2018-11-24 08:30 | 0.87867 | 188.5082
10.6667 | 2018-11-24 08:40 | 0.91411 | 180.8775
10.6736 | 2018-11-24 08:50 | 0.7431 | 179.0747
10.6806 | 2018-11-24 09:00 | 0.71601 | 180.2401
10.6875 | 2018-11-24 09:10 | 0.71601 | 180.2401
10.6944 | 2018-11-24 09:20 | 0.81971 | 177.6228
10.7014 | 2018-11-24 09:30 | 0.77965 | 186.259
10.7083 | 2018-11-24 09:40 | 0.75702 | 180.4541
10.7153 | 2018-11-24 09:50 | 0.72031 | 174.5031
10.7222 | 2018-11-24 10:00 | 0.69878 | 182.7068
10.7292 | 2018-11-24 10:10 | 0.69878 | 182.7068
10.7361 | 2018-11-24 10:20 | 0.62396 | 172.0777
10.7431 | 2018-11-24 10:30 | 0.58017 | 193.5572
10.75 | 2018-11-24 10:40 | 0.57488 | 188.2006
10.7569 | 2018-11-24 10:50 | 0.49451 | 170.6901
10.7639 | 2018-11-24 11:00 | 0.44619 | 181.6696
10.7708 | 2018-11-24 11:10 | 0.44619 | 181.6696
10.7778 | 2018-11-24 11:20 | 0.24724 | 182.5499
10.7847 | 2018-11-24 11:30 | 0.1775 | 172.5547
10.7917 | 2018-11-24 11:40 | 0.098717 | 103.4732
10.7986 | 2018-11-24 11:50 | 0.14805 | 51.5819
10.8056 | 2018-11-24 12:00 | 0.26026 | 18.3653
10.8125 | 2018-11-24 12:10 | 0.26026 | 18.3653
10.8194 | 2018-11-24 12:20 | 0.46833 | 18.551
10.8264 | 2018-11-24 12:30 | 0.54616 | 16.3777
10.8333 | 2018-11-24 12:40 | 0.57462 | 8.7083
10.8403 | 2018-11-24 12:50 | 0.61265 | 8.4475
10.8472 | 2018-11-24 13:00 | 0.55764 | 9.4961
10.8542 | 2018-11-24 13:10 | 0.55764 | 9.4961
10.8611 | 2018-11-24 13:20 | 0.67972 | 7.4387
10.8681 | 2018-11-24 13:30 | 0.77303 | 12.4002
10.875 | 2018-11-24 13:40 | 0.91505 | 9.3079
10.8819 | 2018-11-24 13:50 | 0.83369 | 3.6449
10.8889 | 2018-11-24 14:00 | 0.77697 | 8.2135
10.8958 | 2018-11-24 14:10 | 0.77697 | 8.2135
10.9028 | 2018-11-24 14:20 | 0.77385 | 7.0515
10.9097 | 2018-11-24 14:30 | 0.81785 | 3.856
10.9167 | 2018-11-24 14:40 | 0.89912 | 9.0223
10.9236 | 2018-11-24 14:50 | 0.76043 | 6.1904
10.9306 | 2018-11-24 15:00 | 0.73993 | 7.8454
10.9375 | 2018-11-24 15:10 | 0.73993 | 7.8454
10.9444 | 2018-11-24 15:20 | 0.78907 | 5.819
10.9514 | 2018-11-24 15:30 | 0.733 | 0.078166
10.9583 | 2018-11-24 15:40 | 0.60604 | 359.3382
10.9653 | 2018-11-24 15:50 | 0.6823 | 5.6354
10.9722 | 2018-11-24 16:00 | 0.61783 | 2.9689
10.9792 | 2018-11-24 16:10 | 0.61783 | 2.9689
10.9861 | 2018-11-24 16:20 | 0.57206 | 359.1987
10.9931 | 2018-11-24 16:30 | 0.44002 | 0.52086
11 | 2018-11-24 16:40 | 0.391 | 0
11.0069 | 2018-11-24 16:50 | 0.36497 | 350.5377
11.0139 | 2018-11-24 17:00 | 0.30779 | 4.0989
11.0208 | 2018-11-24 17:10 | 0.30779 | 4.0989
11.0278 | 2018-11-24 17:20 | 0.21086 | 347.6775
11.0347 | 2018-11-24 17:30 | 0.14145 | 313.8542
11.0417 | 2018-11-24 17:40 | 0.13624 | 324.5601
11.0486 | 2018-11-24 17:50 | 0.15316 | 253.6949
11.0556 | 2018-11-24 18:00 | 0.15962 | 216.0802
11.0625 | 2018-11-24 18:10 | 0.15962 | 216.0802
11.0694 | 2018-11-24 18:20 | 0.36505 | 194.7595
11.0764 | 2018-11-24 18:30 | 0.44193 | 193.3445
11.0833 | 2018-11-24 18:40 | 0.4641 | 189.3
11.0903 | 2018-11-24 18:50 | 0.47718 | 187.5867
11.0972 | 2018-11-24 19:00 | 0.64844 | 182.1211
11.1042 | 2018-11-24 19:10 | 0.64844 | 182.1211
11.1111 | 2018-11-24 19:20 | 0.81434 | 185.9206
11.1181 | 2018-11-24 19:30 | 0.74897 | 191.475
11.125 | 2018-11-24 19:40 | 0.75068 | 182.4431
11.1319 | 2018-11-24 19:50 | 0.88608 | 180.776
11.1389 | 2018-11-24 20:00 | 0.88639 | 184.2054
11.1458 | 2018-11-24 20:10 | 0.88639 | 184.2054
11.1528 | 2018-11-24 20:20 | 0.79975 | 188.4847
11.1597 | 2018-11-24 20:30 | 0.85506 | 179.3299
11.1667 | 2018-11-24 20:40 | 0.8651 | 180.861
11.1736 | 2018-11-24 20:50 | 0.83713 | 178.9733
11.1806 | 2018-11-24 21:00 | 0.83607 | 179.2462
11.1875 | 2018-11-24 21:10 | 0.83607 | 179.2462
11.1944 | 2018-11-24 21:20 | 0.91903 | 183.8058
11.2014 | 2018-11-24 21:30 | 0.81106 | 187.0111
11.2083 | 2018-11-24 21:40 | 0.80241 | 186.6556
11.2153 | 2018-11-24 21:50 | 0.70083 | 182.7807
11.2222 | 2018-11-24 22:00 | 0.84957 | 182.0911
11.2292 | 2018-11-24 22:10 | 0.84957 | 182.0911
11.2361 | 2018-11-24 22:20 | 0.73898 | 184.1906
11.2431 | 2018-11-24 22:30 | 0.682 | 183.1099
11.25 | 2018-11-24 22:40 | 0.74378 | 182.6201
11.2569 | 2018-11-24 22:50 | 0.48308 | 178.9325
11.2639 | 2018-11-24 23:00 | 0.54303 | 179.3669
11.2708 | 2018-11-24 23:10 | 0.54303 | 179.3669
11.2778 | 2018-11-24 23:20 | 0.35411 | 178.5436
11.2847 | 2018-11-24 23:30 | 0.37245 | 169.3236
11.2917 | 2018-11-24 23:40 | 0.25809 | 178.4458
11.2986 | 2018-11-24 23:50 | 0.21074 | 172.6389
11.3056 | 2018-11-25 | 0.076026 | 144.6375
11.3125 | 2018-11-25 00:10 | 0.076026 | 144.6375
11.3194 | 2018-11-25 00:20 | 0.19578 | 23.1602
11.3264 | 2018-11-25 00:30 | 0.37188 | 18.3375
11.3333 | 2018-11-25 00:40 | 0.41934 | 13.9368
11.3403 | 2018-11-25 00:50 | 0.48717 | 23.7237
11.3472 | 2018-11-25 01:00 | 0.51754 | 9.1165
11.3542 | 2018-11-25 01:10 | 0.51754 | 9.1165
11.3611 | 2018-11-25 01:20 | 0.58399 | 5.7985
11.3681 | 2018-11-25 01:30 | 0.72155 | 7.7258
11.375 | 2018-11-25 01:40 | 0.70777 | 4.051
11.3819 | 2018-11-25 01:50 | 0.76242 | 6.1742
11.3889 | 2018-11-25 02:00 | 0.77461 | 7.492
11.3958 | 2018-11-25 02:10 | 0.77461 | 7.492
11.4028 | 2018-11-25 02:20 | 0.77942 | 9.3777
11.4097 | 2018-11-25 02:30 | 0.78715 | 8.2536
11.4167 | 2018-11-25 02:40 | 0.80165 | 6.8059
11.4236 | 2018-11-25 02:50 | 0.83107 | 8.9296
11.4306 | 2018-11-25 03:00 | 0.80072 | 4.728
11.4375 | 2018-11-25 03:10 | 0.80072 | 4.728
11.4444 | 2018-11-25 03:20 | 0.70238 | 1.8765
11.4514 | 2018-11-25 03:30 | 0.75544 | 5.4691
11.4583 | 2018-11-25 03:40 | 0.68507 | 359.1636
11.4653 | 2018-11-25 03:50 | 0.73315 | 3.2058
11.4722 | 2018-11-25 04:00 | 0.63982 | 5.3809
11.4792 | 2018-11-25 04:10 | 0.63982 | 5.3809
11.4861 | 2018-11-25 04:20 | 0.66078 | 2.7758
11.4931 | 2018-11-25 04:30 | 0.53726 | 8.0245
11.5 | 2018-11-25 04:40 | 0.54253 | 357.4646
11.5069 | 2018-11-25 04:50 | 0.41367 | 7.6404
11.5139 | 2018-11-25 05:00 | 0.43089 | 9.4842
11.5208 | 2018-11-25 05:10 | 0.43089 | 9.4842
11.5278 | 2018-11-25 05:20 | 0.27487 | 15.4014
11.5347 | 2018-11-25 05:30 | 0.30801 | 359.442
11.5417 | 2018-11-25 05:40 | 0.17472 | 344.0546
11.5486 | 2018-11-25 05:50 | 0.15954 | 337.1315
11.5556 | 2018-11-25 06:00 | 0.056036 | 325.1755
11.5625 | 2018-11-25 06:10 | 0.056036 | 325.1755
11.5694 | 2018-11-25 06:20 | 0.15629 | 224.2223
11.5764 | 2018-11-25 06:30 | 0.32743 | 211.8941
11.5833 | 2018-11-25 06:40 | 0.4293 | 196.7887
11.5903 | 2018-11-25 06:50 | 0.56098 | 190.2683
11.5972 | 2018-11-25 07:00 | 0.55643 | 190.5627
11.6042 | 2018-11-25 07:10 | 0.55643 | 190.5627
11.6111 | 2018-11-25 07:20 | 0.59501 | 179.6148
11.6181 | 2018-11-25 07:30 | 0.61503 | 180.559
11.625 | 2018-11-25 07:40 | 0.59349 | 184.0581
11.6319 | 2018-11-25 07:50 | 0.72402 | 179.5252
11.6389 | 2018-11-25 08:00 | 0.73783 | 177.2811
11.6458 | 2018-11-25 08:10 | 0.73783 | 177.2811
11.6528 | 2018-11-25 08:20 | 0.85952 | 182.0002
11.6597 | 2018-11-25 08:30 | 0.84116 | 186.3477
11.6667 | 2018-11-25 08:40 | 0.85426 | 181.4086
11.6736 | 2018-11-25 08:50 | 0.81167 | 182.3301
11.6806 | 2018-11-25 09:00 | 0.91977 | 183.553
11.6875 | 2018-11-25 09:10 | 0.91977 | 183.553
11.6944 | 2018-11-25 09:20 | 0.8791 | 182.8689
11.7014 | 2018-11-25 09:30 | 0.86694 | 183.8361
11.7083 | 2018-11-25 09:40 | 0.8648 | 185.3744
11.7153 | 2018-11-25 09:50 | 0.78643 | 181.8946
11.7222 | 2018-11-25 10:00 | 0.72722 | 181.4183
11.7292 | 2018-11-25 10:10 | 0.72722 | 181.4183
11.7361 | 2018-11-25 10:20 | 0.67962 | 182.4456
11.7431 | 2018-11-25 10:30 | 0.77509 | 183.0322
11.75 | 2018-11-25 10:40 | 0.60823 | 184.9044
11.7569 | 2018-11-25 10:50 | 0.55681 | 183.0885
11.7639 | 2018-11-25 11:00 | 0.53906 | 172.9673
11.7708 | 2018-11-25 11:10 | 0.53906 | 172.9673
11.7778 | 2018-11-25 11:20 | 0.45154 | 182.7927
11.7847 | 2018-11-25 11:30 | 0.44861 | 175.1409
11.7917 | 2018-11-25 11:40 | 0.4396 | 182.9991
11.7986 | 2018-11-25 11:50 | 0.34828 | 166.0435
11.8056 | 2018-11-25 12:00 | 0.18097 | 150.1766
11.8125 | 2018-11-25 12:10 | 0.18097 | 150.1766
11.8194 | 2018-11-25 12:20 | 0.016125 | 277.125
11.8264 | 2018-11-25 12:30 | 0.18639 | 34.2869
11.8333 | 2018-11-25 12:40 | 0.23332 | 51.2635
11.8403 | 2018-11-25 12:50 | 0.46106 | 18.5921
11.8472 | 2018-11-25 13:00 | 0.42186 | 18.9503
11.8542 | 2018-11-25 13:10 | 0.42186 | 18.9503
11.8611 | 2018-11-25 13:20 | 0.56815 | 12.8132
11.8681 | 2018-11-25 13:30 | 0.5409 | 10.9776
11.875 | 2018-11-25 13:40 | 0.69826 | 6.3311
11.8819 | 2018-11-25 13:50 | 0.65464 | 9.3184
11.8889 | 2018-11-25 14:00 | 0.7533 | 9.9375
11.8958 | 2018-11-25 14:10 | 0.7533 | 9.9375
11.9028 | 2018-11-25 14:20 | 0.77723 | 6.6495
11.9097 | 2018-11-25 14:30 | 0.88277 | 8.534
11.9167 | 2018-11-25 14:40 | 0.80945 | 7.2392
11.9236 | 2018-11-25 14:50 | 0.85221 | 7.959
11.9306 | 2018-11-25 15:00 | 0.91608 | 10.0587
11.9375 | 2018-11-25 15:10 | 0.91608 | 10.0587
11.9444 | 2018-11-25 15:20 | 0.72835 | 7.5739
11.9514 | 2018-11-25 15:30 | 0.71388 | 11.7192
11.9583 | 2018-11-25 15:40 | 0.68442 | 3.686
11.9653 | 2018-11-25 15:50 | 0.67035 | 8.4927
11.9722 | 2018-11-25 16:00 | 0.6418 | 2.8579
11.9792 | 2018-11-25 16:10 | 0.6418 | 2.8579
11.9861 | 2018-11-25 16:20 | 0.67425 | 3.4862
11.9931 | 2018-11-25 16:30 | 0.57781 | 10.5709
12 | 2018-11-25 16:40 | 0.57625 | 358.3095
12.0069 | 2018-11-25 16:50 | 0.62551 | 5.1364
12.0139 | 2018-11-25 17:00 | 0.47501 | 3.7419
12.0208 | 2018-11-25 17:10 | 0.47501 | 3.7419
12.0278 | 2018-11-25 17:20 | 0.42172 | 12.3225
12.0347 | 2018-11-25 17:30 | 0.35629 | 14.4653
12.0417 | 2018-11-25 17:40 | 0.24026 | 12.0115
12.0486 | 2018-11-25 17:50 | 0.2263 | 14.5889
12.0556 | 2018-11-25 18:00 | 0.227 | 359.7476
12.0625 | 2018-11-25 18:10 | 0.227 | 359.7476
12.0694 | 2018-11-25 18:20 | 0.050537 | 27.0721
12.0764 | 2018-11-25 18:30 | 0.12806 | 218.6598
12.0833 | 2018-11-25 18:40 | 0.11261 | 199.7223
12.0903 | 2018-11-25 18:50 | 0.29248 | 190.042
12.0972 | 2018-11-25 19:00 | 0.41992 | 196.3202
12.1042 | 2018-11-25 19:10 | 0.41992 | 196.3202
12.1111 | 2018-11-25 19:20 | 0.5253 | 190.1975
12.1181 | 2018-11-25 19:30 | 0.51114 | 181.3452
12.125 | 2018-11-25 19:40 | 0.57404 | 179.3013
12.1319 | 2018-11-25 19:50 | 0.602 | 180.1904
12.1389 | 2018-11-25 20:00 | 0.642 | 180
12.1458 | 2018-11-25 20:10 | 0.642 | 180
12.1528 | 2018-11-25 20:20 | 0.73315 | 181.1723
12.1597 | 2018-11-25 20:30 | 0.72516 | 176.7588
12.1667 | 2018-11-25 20:40 | 0.80568 | 183.7005
12.1736 | 2018-11-25 20:50 | 0.9247 | 183.472
12.1806 | 2018-11-25 21:00 | 0.73112 | 178.9812
12.1875 | 2018-11-25 21:10 | 0.73112 | 178.9812
12.1944 | 2018-11-25 21:20 | 0.87443 | 183.278
12.2014 | 2018-11-25 21:30 | 0.72439 | 185.5453
12.2083 | 2018-11-25 21:40 | 0.831 | 180.1379
12.2153 | 2018-11-25 21:50 | 0.81741 | 181.8228
12.2222 | 2018-11-25 22:00 | 0.83139 | 176.6902
12.2292 | 2018-11-25 22:10 | 0.83139 | 176.6902
12.2361 | 2018-11-25 22:20 | 0.83915 | 181.0925
12.2431 | 2018-11-25 22:30 | 0.82107 | 182.9321
12.25 | 2018-11-25 22:40 | 0.79301 | 184.9917
12.2569 | 2018-11-25 22:50 | 0.77325 | 183.262
12.2639 | 2018-11-25 23:00 | 0.63732 | 183.6885
12.2708 | 2018-11-25 23:10 | 0.63732 | 183.6885
12.2778 | 2018-11-25 23:20 | 0.61045 | 176.0548
12.2847 | 2018-11-25 23:30 | 0.66917 | 181.2844
12.2917 | 2018-11-25 23:40 | 0.57912 | 176.436
12.2986 | 2018-11-25 23:50 | 0.52526 | 170.4659
12.3056 | 2018-11-26 | 0.46867 | 188.0955
12.3125 | 2018-11-26 00:10 | 0.46867 | 188.0955
12.3194 | 2018-11-26 00:20 | 0.41089 | 176.2323
12.3264 | 2018-11-26 00:30 | 0.27577 | 171.8699
12.3333 | 2018-11-26 00:40 | 0.12462 | 162.7283
12.3403 | 2018-11-26 00:50 | 0.01077 | 201.8014
12.3472 | 2018-11-26 01:00 | 0.063411 | 52.0458
12.3542 | 2018-11-26 01:10 | 0.063411 | 52.0458
12.3611 | 2018-11-26 01:20 | 0.36715 | 18.0895
12.3681 | 2018-11-26 01:30 | 0.49001 | 15.1423
12.375 | 2018-11-26 01:40 | 0.46762 | 14.3631
12.3819 | 2018-11-26 01:50 | 0.56092 | 10.7891
12.3889 | 2018-11-26 02:00 | 0.54565 | 6.6301
12.3958 | 2018-11-26 02:10 | 0.54565 | 6.6301
12.4028 | 2018-11-26 02:20 | 0.66885 | 10.3355
12.4097 | 2018-11-26 02:30 | 0.69958 | 4.9201
12.4167 | 2018-11-26 02:40 | 0.73547 | 6.323
12.4236 | 2018-11-26 02:50 | 0.91154 | 6.8677
12.4306 | 2018-11-26 03:00 | 0.88235 | 6.3115
12.4375 | 2018-11-26 03:10 | 0.88235 | 6.3115
12.4444 | 2018-11-26 03:20 | 0.83984 | 4.7127
12.4514 | 2018-11-26 03:30 | 0.93827 | 8.8901
12.4583 | 2018-11-26 03:40 | 0.82116 | 5.0302
12.4653 | 2018-11-26 03:50 | 0.79494 | 5.7034
12.4722 | 2018-11-26 04:00 | 0.79864 | 6.1817
12.4792 | 2018-11-26 04:10 | 0.79864 | 6.1817
12.4861 | 2018-11-26 04:20 | 0.67056 | 5.9061
12.4931 | 2018-11-26 04:30 | 0.7456 | 2.306
12.5 | 2018-11-26 04:40 | 0.70363 | 9.4891
12.5069 | 2018-11-26 04:50 | 0.60682 | 4.4422
12.5139 | 2018-11-26 05:00 | 0.68599 | 5.3532
12.5208 | 2018-11-26 05:10 | 0.68599 | 5.3532
12.5278 | 2018-11-26 05:20 | 0.52025 | 358.2376
12.5347 | 2018-11-26 05:30 | 0.463 | 0
12.5417 | 2018-11-26 05:40 | 0.39137 | 2.4896
12.5486 | 2018-11-26 05:50 | 0.3884 | 4.8739
12.5556 | 2018-11-26 06:00 | 0.38419 | 348.8948
12.5625 | 2018-11-26 06:10 | 0.38419 | 348.8948
12.5694 | 2018-11-26 06:20 | 0.2012 | 357.4362
12.5764 | 2018-11-26 06:30 | 0.10539 | 326.6115
12.5833 | 2018-11-26 06:40 | 0.03891 | 334.0935
12.5903 | 2018-11-26 06:50 | 0.089051 | 304.9393
12.5972 | 2018-11-26 07:00 | 0.11302 | 210.8768
12.6042 | 2018-11-26 07:10 | 0.11302 | 210.8768
12.6111 | 2018-11-26 07:20 | 0.35427 | 205.4077
12.6181 | 2018-11-26 07:30 | 0.4231 | 200.6194
12.625 | 2018-11-26 07:40 | 0.50071 | 191.871
12.6319 | 2018-11-26 07:50 | 0.61675 | 188.4848
12.6389 | 2018-11-26 08:00 | 0.57098 | 188.9674
12.6458 | 2018-11-26 08:10 | 0.57098 | 188.9674
12.6528 | 2018-11-26 08:20 | 0.67202 | 179.5737
12.6597 | 2018-11-26 08:30 | 0.78258 | 177.803
12.6667 | 2018-11-26 08:40 | 0.82635 | 178.3357
12.6736 | 2018-11-26 08:50 | 0.76909 | 183.0559
12.6806 | 2018-11-26 09:00 | 0.70359 | 185.7916
12.6875 | 2018-11-26 09:10 | 0.70359 | 185.7916
12.6944 | 2018-11-26 09:20 | 0.82792 | 182.7
12.7014 | 2018-11-26 09:30 | 0.75881 | 182.6437
12.7083 | 2018-11-26 09:40 | 0.83616 | 183.0164
12.7153 | 2018-11-26 09:50 | 0.82355 | 182.0876
12.7222 | 2018-11-26 10:00 | 0.87955 | 182.0198
12.7292 | 2018-11-26 10:10 | 0.87955 | 182.0198
12.7361 | 2018-11-26 10:20 | 0.79578 | 188.0181
12.7431 | 2018-11-26 10:30 | 0.7639 | 182.7763
12.75 | 2018-11-26 10:40 | 0.7343 | 181.6388
12.7569 | 2018-11-26 10:50 | 0.78559 | 176.3509
12.7639 | 2018-11-26 11:00 | 0.63835 | 181.8852
12.7708 | 2018-11-26 11:10 | 0.63835 | 181.8852
12.7778 | 2018-11-26 11:20 | 0.61 | 180.1879
12.7847 | 2018-11-26 11:30 | 0.61281 | 184.3987
12.7917 | 2018-11-26 11:40 | 0.6251 | 183.3934
12.7986 | 2018-11-26 11:50 | 0.59762 | 175.7778
12.8056 | 2018-11-26 12:00 | 0.54231 | 185.2901
12.8125 | 2018-11-26 12:10 | 0.54231 | 185.2901
12.8194 | 2018-11-26 12:20 | 0.40789 | 171.115
12.8264 | 2018-11-26 12:30 | 0.29106 | 181.1812
12.8333 | 2018-11-26 12:40 | 0.33601 | 179.659
12.8403 | 2018-11-26 12:50 | 0.19025 | 167.8632
12.8472 | 2018-11-26 13:00 | 0.13824 | 151.9519
12.8542 | 2018-11-26 13:10 | 0.13824 | 151.9519
12.8611 | 2018-11-26 13:20 | 0.1597 | 22.0679
12.8681 | 2018-11-26 13:30 | 0.30353 | 29.183
12.875 | 2018-11-26 13:40 | 0.37286 | 9.2602
12.8819 | 2018-11-26 13:50 | 0.44991 | 13.7583
12.8889 | 2018-11-26 14:00 | 0.58825 | 15.0757
12.8958 | 2018-11-26 14:10 | 0.58825 | 15.0757
12.9028 | 2018-11-26 14:20 | 0.4883 | 1.9952
12.9097 | 2018-11-26 14:30 | 0.64151 | 5.995
12.9167 | 2018-11-26 14:40 | 0.67949 | 16.9415
12.9236 | 2018-11-26 14:50 | 0.74044 | 6.2804
12.9306 | 2018-11-26 15:00 | 0.83674 | 3.7002
12.9375 | 2018-11-26 15:10 | 0.83674 | 3.7002
12.9444 | 2018-11-26 15:20 | 0.81167 | 3.6732
12.9514 | 2018-11-26 15:30 | 0.8008 | 10.6504
12.9583 | 2018-11-26 15:40 | 0.83541 | 7.6354
12.9653 | 2018-11-26 15:50 | 0.89956 | 3.3777
12.9722 | 2018-11-26 16:00 | 0.84267 | 4.5604
12.9792 | 2018-11-26 16:10 | 0.84267 | 4.5604
12.9861 | 2018-11-26 16:20 | 0.8518 | 2.4896
12.9931 | 2018-11-26 16:30 | 0.59464 | 5.4038
13 | 2018-11-26 16:40 | 0.69742 | 4.7705
13.0069 | 2018-11-26 16:50 | 0.48545 | 2.4793
13.0139 | 2018-11-26 17:00 | 0.64438 | 6.6839
13.0208 | 2018-11-26 17:10 | 0.64438 | 6.6839
13.0278 | 2018-11-26 17:20 | 0.57783 | 3.0753
13.0347 | 2018-11-26 17:30 | 0.53038 | 7.3662
13.0417 | 2018-11-26 17:40 | 0.52277 | 4.7181
13.0486 | 2018-11-26 17:50 | 0.51406 | 356.3194
13.0556 | 2018-11-26 18:00 | 0.43 | 359.7335
13.0625 | 2018-11-26 18:10 | 0.43 | 359.7335
13.0694 | 2018-11-26 18:20 | 0.30187 | 10.3049
13.0764 | 2018-11-26 18:30 | 0.2585 | 349.2986
13.0833 | 2018-11-26 18:40 | 0.19067 | 344.7976
13.0903 | 2018-11-26 18:50 | 0.18484 | 351.9137
13.0972 | 2018-11-26 19:00 | 0.027514 | 289.0935
13.1042 | 2018-11-26 19:10 | 0.027514 | 289.0935
13.1111 | 2018-11-26 19:20 | 0.087658 | 242.8503
13.1181 | 2018-11-26 19:30 | 0.31741 | 216.545
13.125 | 2018-11-26 19:40 | 0.27857 | 201.0375
13.1319 | 2018-11-26 19:50 | 0.40288 | 198.0752
13.1389 | 2018-11-26 20:00 | 0.46556 | 206.1247
13.1458 | 2018-11-26 20:10 | 0.46556 | 206.1247
13.1528 | 2018-11-26 20:20 | 0.57366 | 187.3108
13.1597 | 2018-11-26 20:30 | 0.649 | 183.1798
13.1667 | 2018-11-26 20:40 | 0.6256 | 185.2276
13.1736 | 2018-11-26 20:50 | 0.7045 | 183.7437
13.1806 | 2018-11-26 21:00 | 0.77488 | 176.0039
13.1875 | 2018-11-26 21:10 | 0.77488 | 176.0039
13.1944 | 2018-11-26 21:20 | 0.78314 | 178.9025
13.2014 | 2018-11-26 21:30 | 0.65669 | 182.6184
13.2083 | 2018-11-26 21:40 | 0.70847 | 185.6704
13.2153 | 2018-11-26 21:50 | 0.84446 | 187.6216
13.2222 | 2018-11-26 22:00 | 0.78501 | 180.219
13.2292 | 2018-11-26 22:10 | 0.78501 | 180.219
13.2361 | 2018-11-26 22:20 | 0.75104 | 179.3897
13.2431 | 2018-11-26 22:30 | 0.73746 | 182.0204
13.25 | 2018-11-26 22:40 | 0.78005 | 179.3389
13.2569 | 2018-11-26 22:50 | 0.75408 | 180.8358
13.2639 | 2018-11-26 23:00 | 0.64824 | 183.5377
13.2708 | 2018-11-26 23:10 | 0.64824 | 183.5377
13.2778 | 2018-11-26 23:20 | 0.58458 | 177.4509
13.2847 | 2018-11-26 23:30 | 0.6613 | 178.2669
13.2917 | 2018-11-26 23:40 | 0.64579 | 175.7374
13.2986 | 2018-11-26 23:50 | 0.61723 | 181.5782
13.3056 | 2018-11-27 | 0.595 | 179.8074
13.3125 | 2018-11-27 00:10 | 0.595 | 179.8074
13.3194 | 2018-11-27 00:20 | 0.639 | 180
13.3264 | 2018-11-27 00:30 | 0.45047 | 192.9565
13.3333 | 2018-11-27 00:40 | 0.37019 | 181.8576
13.3403 | 2018-11-27 00:50 | 0.35809 | 171.3268
13.3472 | 2018-11-27 01:00 | 0.30637 | 172.875
13.3542 | 2018-11-27 01:10 | 0.30637 | 172.875
13.3611 | 2018-11-27 01:20 | 0.094244 | 160.796
13.3681 | 2018-11-27 01:30 | 0.043932 | 101.8215
13.375 | 2018-11-27 01:40 | 0.15338 | 34.1045
13.3819 | 2018-11-27 01:50 | 0.24878 | 24.7108
13.3889 | 2018-11-27 02:00 | 0.36137 | 23.6566
13.3958 | 2018-11-27 02:10 | 0.36137 | 23.6566
13.4028 | 2018-11-27 02:20 | 0.49908 | 17.491
13.4097 | 2018-11-27 02:30 | 0.52864 | 8.3753
13.4167 | 2018-11-27 02:40 | 0.61566 | 6.2477
13.4236 | 2018-11-27 02:50 | 0.61474 | 10.2132
13.4306 | 2018-11-27 03:00 | 0.76986 | 5.7402
13.4375 | 2018-11-27 03:10 | 0.76986 | 5.7402
13.4444 | 2018-11-27 03:20 | 0.84416 | 4.9609
13.4514 | 2018-11-27 03:30 | 0.72221 | 9.6449
13.4583 | 2018-11-27 03:40 | 0.85518 | 8.4049
13.4653 | 2018-11-27 03:50 | 0.9643 | 6.0121
13.4722 | 2018-11-27 04:00 | 0.88973 | 7.5563
13.4792 | 2018-11-27 04:10 | 0.88973 | 7.5563
13.4861 | 2018-11-27 04:20 | 0.73007 | 4.3205
13.4931 | 2018-11-27 04:30 | 0.70798 | 6.081
13.5 | 2018-11-27 04:40 | 0.77588 | 2.7333
13.5069 | 2018-11-27 04:50 | 0.78332 | 5.2739
13.5139 | 2018-11-27 05:00 | 0.71696 | 4.2393
13.5208 | 2018-11-27 05:10 | 0.71696 | 4.2393
13.5278 | 2018-11-27 05:20 | 0.67134 | 11.8623
13.5347 | 2018-11-27 05:30 | 0.61932 | 6.7693
13.5417 | 2018-11-27 05:40 | 0.53956 | 4.358
13.5486 | 2018-11-27 05:50 | 0.53407 | 5.0487
13.5556 | 2018-11-27 06:00 | 0.46813 | 6.624
13.5625 | 2018-11-27 06:10 | 0.46813 | 6.624
13.5694 | 2018-11-27 06:20 | 0.37845 | 9.7361
13.5764 | 2018-11-27 06:30 | 0.46971 | 4.8852
13.5833 | 2018-11-27 06:40 | 0.3281 | 1.3972
13.5903 | 2018-11-27 06:50 | 0.37483 | 356.1758
13.5972 | 2018-11-27 07:00 | 0.24749 | 351.8699
13.6042 | 2018-11-27 07:10 | 0.24749 | 351.8699
13.6111 | 2018-11-27 07:20 | 0.26573 | 351.7784
13.6181 | 2018-11-27 07:30 | 0.15508 | 324.9777
13.625 | 2018-11-27 07:40 | 0.051039 | 2.2457
13.6319 | 2018-11-27 07:50 | 0.15154 | 247.4965
13.6389 | 2018-11-27 08:00 | 0.18139 | 235.7843
13.6458 | 2018-11-27 08:10 | 0.18139 | 235.7843
13.6528 | 2018-11-27 08:20 | 0.36368 | 197.9367
13.6597 | 2018-11-27 08:30 | 0.49322 | 200.1618
13.6667 | 2018-11-27 08:40 | 0.43997 | 187.7065
13.6736 | 2018-11-27 08:50 | 0.56208 | 192.8494
13.6806 | 2018-11-27 09:00 | 0.52834 | 182.0609
13.6875 | 2018-11-27 09:10 | 0.52834 | 182.0609
13.6944 | 2018-11-27 09:20 | 0.61805 | 176.6608
13.7014 | 2018-11-27 09:30 | 0.69235 | 184.7224
13.7083 | 2018-11-27 09:40 | 0.79812 | 178.9949
13.7153 | 2018-11-27 09:50 | 0.69893 | 186.0777
13.7222 | 2018-11-27 10:00 | 0.76502 | 180.3745
13.7292 | 2018-11-27 10:10 | 0.76502 | 180.3745
13.7361 | 2018-11-27 10:20 | 0.794 | 180.0722
13.7431 | 2018-11-27 10:30 | 0.72432 | 186.2616
13.75 | 2018-11-27 10:40 | 0.74817 | 178.7746
13.7569 | 2018-11-27 10:50 | 0.71525 | 178.4778
13.7639 | 2018-11-27 11:00 | 0.762 | 182.9337
13.7708 | 2018-11-27 11:10 | 0.762 | 182.9337
13.7778 | 2018-11-27 11:20 | 0.66213 | 178.875
13.7847 | 2018-11-27 11:30 | 0.76205 | 180.6767
13.7917 | 2018-11-27 11:40 | 0.66662 | 185.0777
13.7986 | 2018-11-27 11:50 | 0.637 | 180.09
13.8056 | 2018-11-27 12:00 | 0.67523 | 174.3907
13.8125 | 2018-11-27 12:10 | 0.67523 | 174.3907
13.8194 | 2018-11-27 12:20 | 0.54355 | 175.6741
13.8264 | 2018-11-27 12:30 | 0.53341 | 182.2563
13.8333 | 2018-11-27 12:40 | 0.46761 | 169.6513
13.8403 | 2018-11-27 12:50 | 0.49379 | 183.2506
13.8472 | 2018-11-27 13:00 | 0.38819 | 178.2285
13.8542 | 2018-11-27 13:10 | 0.38819 | 178.2285
13.8611 | 2018-11-27 13:20 | 0.18603 | 194.6338
13.8681 | 2018-11-27 13:30 | 0.18604 | 153.1595
13.875 | 2018-11-27 13:40 | 0.11735 | 122.4712
13.8819 | 2018-11-27 13:50 | 0.10179 | 56.6222
13.8889 | 2018-11-27 14:00 | 0.21112 | 55.0302
13.8958 | 2018-11-27 14:10 | 0.21112 | 55.0302
13.9028 | 2018-11-27 14:20 | 0.44253 | 17.0837
13.9097 | 2018-11-27 14:30 | 0.52752 | 13.9309
13.9167 | 2018-11-27 14:40 | 0.55153 | 14.0614
13.9236 | 2018-11-27 14:50 | 0.55233 | 13.0801
13.9306 | 2018-11-27 15:00 | 0.57888 | 10.0481
13.9375 | 2018-11-27 15:10 | 0.57888 | 10.0481
13.9444 | 2018-11-27 15:20 | 0.90422 | 7.2429
13.9514 | 2018-11-27 15:30 | 0.74254 | 6.3402
13.9583 | 2018-11-27 15:40 | 0.7916 | 7.4033
13.9653 | 2018-11-27 15:50 | 0.88319 | 7.809
13.9722 | 2018-11-27 16:00 | 0.98612 | 10.045
13.9792 | 2018-11-27 16:10 | 0.98612 | 10.045
13.9861 | 2018-11-27 16:20 | 0.89244 | 7.4037
13.9931 | 2018-11-27 16:30 | 0.9641 | 2.7348
14 | 2018-11-27 16:40 | 0.85015 | 7.4343
14.0069 | 2018-11-27 16:50 | 1.0194 | 8.5752
14.0139 | 2018-11-27 17:00 | 0.89129 | 6.2479
14.0208 | 2018-11-27 17:10 | 0.89129 | 6.2479
14.0278 | 2018-11-27 17:20 | 0.82088 | 2.6533
14.0347 | 2018-11-27 17:30 | 0.74574 | 7.7063
14.0417 | 2018-11-27 17:40 | 0.77664 | 4.7269
14.0486 | 2018-11-27 17:50 | 0.74992 | 13.888
14.0556 | 2018-11-27 18:00 | 0.73532 | 3.4305
14.0625 | 2018-11-27 18:10 | 0.73532 | 3.4305
14.0694 | 2018-11-27 18:20 | 0.50906 | 0.90045
14.0764 | 2018-11-27 18:30 | 0.54163 | 4.4474
14.0833 | 2018-11-27 18:40 | 0.4773 | 17.1822
14.0903 | 2018-11-27 18:50 | 0.55939 | 357.8486
14.0972 | 2018-11-27 19:00 | 0.51487 | 7.0284
14.1042 | 2018-11-27 19:10 | 0.51487 | 7.0284
14.1111 | 2018-11-27 19:20 | 0.46743 | 357.5477
14.1181 | 2018-11-27 19:30 | 0.49631 | 4.1596
14.125 | 2018-11-27 19:40 | 0.33104 | 0.86543
14.1319 | 2018-11-27 19:50 | 0.27354 | 353.9142
14.1389 | 2018-11-27 20:00 | 0.23623 | 345.7873
14.1458 | 2018-11-27 20:10 | 0.23623 | 345.7873
14.1528 | 2018-11-27 20:20 | 0.143 | 359.5993
14.1597 | 2018-11-27 20:30 | 0.024331 | 99.4623
14.1667 | 2018-11-27 20:40 | 0.055444 | 172.7468
14.1736 | 2018-11-27 20:50 | 0.12557 | 185.4836
14.1806 | 2018-11-27 21:00 | 0.24788 | 193.5317
14.1875 | 2018-11-27 21:10 | 0.24788 | 193.5317
14.1944 | 2018-11-27 21:20 | 0.34304 | 180.8352
14.2014 | 2018-11-27 21:30 | 0.37519 | 181.8328
14.2083 | 2018-11-27 21:40 | 0.46166 | 172.7826
14.2153 | 2018-11-27 21:50 | 0.44529 | 186.9654
14.2222 | 2018-11-27 22:00 | 0.45007 | 181.0185
14.2292 | 2018-11-27 22:10 | 0.45007 | 181.0185
14.2361 | 2018-11-27 22:20 | 0.44487 | 189.3141
14.2431 | 2018-11-27 22:30 | 0.5392 | 176.1718
14.25 | 2018-11-27 22:40 | 0.5625 | 174.5935
14.2569 | 2018-11-27 22:50 | 0.51105 | 179.2152
14.2639 | 2018-11-27 23:00 | 0.53568 | 177.1109
14.2708 | 2018-11-27 23:10 | 0.53568 | 177.1109
14.2778 | 2018-11-27 23:20 | 0.54667 | 177.169
14.2847 | 2018-11-27 23:30 | 0.60421 | 178.4826
14.2917 | 2018-11-27 23:40 | 0.59301 | 179.6135
14.2986 | 2018-11-27 23:50 | 0.61873 | 182.7792
14.3056 | 2018-11-28 | 0.65802 | 180.4354
14.3125 | 2018-11-28 00:10 | 0.65802 | 180.4354
14.3194 | 2018-11-28 00:20 | 0.49579 | 176.7625
14.3264 | 2018-11-28 00:30 | 0.53526 | 173.6716
14.3333 | 2018-11-28 00:40 | 0.36549 | 174.8198
14.3403 | 2018-11-28 00:50 | 0.43898 | 172.276
14.3472 | 2018-11-28 01:00 | 0.33505 | 178.9739
14.3542 | 2018-11-28 01:10 | 0.33505 | 178.9739
14.3611 | 2018-11-28 01:20 | 0.26717 | 187.3112
14.3681 | 2018-11-28 01:30 | 0.18655 | 187.3917
14.375 | 2018-11-28 01:40 | 0.11868 | 159.2744
14.3819 | 2018-11-28 01:50 | 0.11893 | 132.2737
14.3889 | 2018-11-28 02:00 | 0.098489 | 119.1676
14.3958 | 2018-11-28 02:10 | 0.098489 | 119.1676
14.4028 | 2018-11-28 02:20 | 0.25303 | 37.7757
14.4097 | 2018-11-28 02:30 | 0.20969 | 17.4844
14.4167 | 2018-11-28 02:40 | 0.40959 | 17.329
14.4236 | 2018-11-28 02:50 | 0.42692 | 21.5771
14.4306 | 2018-11-28 03:00 | 0.44096 | 13.3744
14.4375 | 2018-11-28 03:10 | 0.44096 | 13.3744
14.4444 | 2018-11-28 03:20 | 0.54861 | 7.4359
14.4514 | 2018-11-28 03:30 | 0.74448 | 7.5641
14.4583 | 2018-11-28 03:40 | 0.82577 | 7.8652
14.4653 | 2018-11-28 03:50 | 0.97809 | 11.9188
14.4722 | 2018-11-28 04:00 | 0.83295 | 5.5805
14.4792 | 2018-11-28 04:10 | 0.83295 | 5.5805
14.4861 | 2018-11-28 04:20 | 0.88616 | 7.7826
14.4931 | 2018-11-28 04:30 | 0.8646 | 8.983
14.5 | 2018-11-28 04:40 | 0.84792 | 6.773
14.5069 | 2018-11-28 04:50 | 1.0053 | 8.9845
14.5139 | 2018-11-28 05:00 | 0.81209 | 14.8405
14.5208 | 2018-11-28 05:10 | 0.81209 | 14.8405
14.5278 | 2018-11-28 05:20 | 0.87243 | 3.2855
14.5347 | 2018-11-28 05:30 | 0.89874 | 7.9949
14.5417 | 2018-11-28 05:40 | 0.71214 | 1.1265
14.5486 | 2018-11-28 05:50 | 0.90867 | 9.9495
14.5556 | 2018-11-28 06:00 | 0.77386 | 8.172
14.5625 | 2018-11-28 06:10 | 0.77386 | 8.172
14.5694 | 2018-11-28 06:20 | 0.77515 | 9.28
14.5764 | 2018-11-28 06:30 | 0.68802 | 8.189
14.5833 | 2018-11-28 06:40 | 0.70755 | 2.268
14.5903 | 2018-11-28 06:50 | 0.63101 | 359.6368
14.5972 | 2018-11-28 07:00 | 0.75646 | 4.6253
14.6042 | 2018-11-28 07:10 | 0.75646 | 4.6253
14.6111 | 2018-11-28 07:20 | 0.58677 | 357.0693
14.6181 | 2018-11-28 07:30 | 0.54148 | 4.2364
14.625 | 2018-11-28 07:40 | 0.4475 | 9.7781
14.6319 | 2018-11-28 07:50 | 0.59024 | 1.6504
14.6389 | 2018-11-28 08:00 | 0.36809 | 358.7546
14.6458 | 2018-11-28 08:10 | 0.36809 | 358.7546
14.6528 | 2018-11-28 08:20 | 0.37171 | 347.5715
14.6597 | 2018-11-28 08:30 | 0.22511 | 358.218
14.6667 | 2018-11-28 08:40 | 0.26916 | 342.7095
14.6736 | 2018-11-28 08:50 | 0.17777 | 8.0845
14.6806 | 2018-11-28 09:00 | 0.071568 | 344.6045
14.6875 | 2018-11-28 09:10 | 0.071568 | 344.6045
14.6944 | 2018-11-28 09:20 | 0.24367 | 184.2364
14.7014 | 2018-11-28 09:30 | 0.23033 | 207.1213
14.7083 | 2018-11-28 09:40 | 0.32098 | 184.4672
14.7153 | 2018-11-28 09:50 | 0.36916 | 178.2925
14.7222 | 2018-11-28 10:00 | 0.48011 | 185.3781
14.7292 | 2018-11-28 10:10 | 0.48011 | 185.3781
14.7361 | 2018-11-28 10:20 | 0.4114 | 188.3862
14.7431 | 2018-11-28 10:30 | 0.45316 | 178.4826
14.75 | 2018-11-28 10:40 | 0.52875 | 184.6647
14.7569 | 2018-11-28 10:50 | 0.58938 | 189.0788
14.7639 | 2018-11-28 11:00 | 0.50514 | 181.3612
14.7708 | 2018-11-28 11:10 | 0.50514 | 181.3612
14.7778 | 2018-11-28 11:20 | 0.49215 | 178.6028
14.7847 | 2018-11-28 11:30 | 0.49658 | 182.7702
14.7917 | 2018-11-28 11:40 | 0.54271 | 184.5444
14.7986 | 2018-11-28 11:50 | 0.60047 | 175.9892
14.8056 | 2018-11-28 12:00 | 0.61416 | 181.3062
14.8125 | 2018-11-28 12:10 | 0.61416 | 181.3062
14.8194 | 2018-11-28 12:20 | 0.54483 | 183.1565
14.8264 | 2018-11-28 12:30 | 0.54305 | 180.7386
14.8333 | 2018-11-28 12:40 | 0.5502 | 181.5622
14.8403 | 2018-11-28 12:50 | 0.57768 | 175.6317
14.8472 | 2018-11-28 13:00 | 0.43655 | 168.6386
14.8542 | 2018-11-28 13:10 | 0.43655 | 168.6386
14.8611 | 2018-11-28 13:20 | 0.44084 | 186.5124
14.8681 | 2018-11-28 13:30 | 0.33961 | 187.1041
14.875 | 2018-11-28 13:40 | 0.29901 | 179.6168
14.8819 | 2018-11-28 13:50 | 0.19702 | 180.8725
14.8889 | 2018-11-28 14:00 | 0.10733 | 206.565
14.8958 | 2018-11-28 14:10 | 0.10733 | 206.565
14.9028 | 2018-11-28 14:20 | 0.09981 | 52.3264
14.9097 | 2018-11-28 14:30 | 0.1514 | 36.9456
14.9167 | 2018-11-28 14:40 | 0.18118 | 27.9795
14.9236 | 2018-11-28 14:50 | 0.31835 | 12.3336
14.9306 | 2018-11-28 15:00 | 0.42083 | 14.7297
14.9375 | 2018-11-28 15:10 | 0.42083 | 14.7297
14.9444 | 2018-11-28 15:20 | 0.5086 | 14.2275
14.9514 | 2018-11-28 15:30 | 0.52879 | 14.9035
14.9583 | 2018-11-28 15:40 | 0.68905 | 14.1976
14.9653 | 2018-11-28 15:50 | 0.75903 | 9.3258
14.9722 | 2018-11-28 16:00 | 0.84228 | 10.1892
14.9792 | 2018-11-28 16:10 | 0.84228 | 10.1892
14.9861 | 2018-11-28 16:20 | 0.76135 | 9.9077
14.9931 | 2018-11-28 16:30 | 1.0083 | 4.6645
15 | 2018-11-28 16:40 | 0.82008 | 2.9357
15.0069 | 2018-11-28 16:50 | 0.80631 | 3.2705
15.0139 | 2018-11-28 17:00 | 0.80233 | 5.2203
15.0208 | 2018-11-28 17:10 | 0.80233 | 5.2203
15.0278 | 2018-11-28 17:20 | 0.95892 | 2.5103
15.0347 | 2018-11-28 17:30 | 0.87077 | 5.9987
15.0417 | 2018-11-28 17:40 | 0.98737 | 13.7688
15.0486 | 2018-11-28 17:50 | 0.97695 | 2.5227
15.0556 | 2018-11-28 18:00 | 0.81327 | 13.4382
15.0625 | 2018-11-28 18:10 | 0.81327 | 13.4382
15.0694 | 2018-11-28 18:20 | 0.96552 | 6.6613
15.0764 | 2018-11-28 18:30 | 0.88478 | 6.5547
15.0833 | 2018-11-28 18:40 | 0.72492 | 5.1443
15.0903 | 2018-11-28 18:50 | 0.85834 | 3.2057
15.0972 | 2018-11-28 19:00 | 0.89352 | 4.3003
15.1042 | 2018-11-28 19:10 | 0.89352 | 4.3003
15.1111 | 2018-11-28 19:20 | 0.74781 | 3.9874
15.1181 | 2018-11-28 19:30 | 0.50904 | 7.2227
15.125 | 2018-11-28 19:40 | 0.60177 | 14.729
15.1319 | 2018-11-28 19:50 | 0.57407 | 359.1017
15.1389 | 2018-11-28 20:00 | 0.52727 | 10.1591
15.1458 | 2018-11-28 20:10 | 0.52727 | 10.1591
15.1528 | 2018-11-28 20:20 | 0.41249 | 4.8675
15.1597 | 2018-11-28 20:30 | 0.348 | 0
15.1667 | 2018-11-28 20:40 | 0.39074 | 356.4785
15.1736 | 2018-11-28 20:50 | 0.18439 | 347.4712
15.1806 | 2018-11-28 21:00 | 0.23336 | 3.1934
15.1875 | 2018-11-28 21:10 | 0.23336 | 3.1934
15.1944 | 2018-11-28 21:20 | 0.19892 | 340.9275
15.2014 | 2018-11-28 21:30 | 0.050488 | 262.0304
15.2083 | 2018-11-28 21:40 | 0.066483 | 226.2189
15.2153 | 2018-11-28 21:50 | 0.125 | 203.0782
15.2222 | 2018-11-28 22:00 | 0.1789 | 207.2812
15.2292 | 2018-11-28 22:10 | 0.1789 | 207.2812
15.2361 | 2018-11-28 22:20 | 0.4113 | 187.2632
15.2431 | 2018-11-28 22:30 | 0.47577 | 189.6801
15.25 | 2018-11-28 22:40 | 0.46631 | 182.0893
15.2569 | 2018-11-28 22:50 | 0.50668 | 185.8906
15.2639 | 2018-11-28 23:00 | 0.41764 | 185.0826
15.2708 | 2018-11-28 23:10 | 0.41764 | 185.0826
15.2778 | 2018-11-28 23:20 | 0.57151 | 188.6547
15.2847 | 2018-11-28 23:30 | 0.499 | 179.8852
15.2917 | 2018-11-28 23:40 | 0.56762 | 186.474
15.2986 | 2018-11-28 23:50 | 0.41652 | 187.4492
15.3056 | 2018-11-29 | 0.48349 | 185.8167
15.3125 | 2018-11-29 00:10 | 0.48349 | 185.8167
15.3194 | 2018-11-29 00:20 | 0.50106 | 179.0852
15.3264 | 2018-11-29 00:30 | 0.53995 | 183.3976
15.3333 | 2018-11-29 00:40 | 0.49076 | 186.0823
15.3403 | 2018-11-29 00:50 | 0.42844 | 170.054
15.3472 | 2018-11-29 01:00 | 0.50836 | 182.142
15.3542 | 2018-11-29 01:10 | 0.50836 | 182.142
15.3611 | 2018-11-29 01:20 | 0.46119 | 188.6045
15.3681 | 2018-11-29 01:30 | 0.3883 | 166.1427
15.375 | 2018-11-29 01:40 | 0.33804 | 180.8475
15.3819 | 2018-11-29 01:50 | 0.278 | 180
15.3889 | 2018-11-29 02:00 | 0.29498 | 175.3331
15.3958 | 2018-11-29 02:10 | 0.29498 | 175.3331
15.4028 | 2018-11-29 02:20 | 0.28668 | 163.5879
15.4097 | 2018-11-29 02:30 | 0.1242 | 176.769
15.4167 | 2018-11-29 02:40 | 0.047539 | 104.6209
15.4236 | 2018-11-29 02:50 | 0.097082 | 78.1113
15.4306 | 2018-11-29 03:00 | 0.14264 | 17.5457
15.4375 | 2018-11-29 03:10 | 0.14264 | 17.5457
15.4444 | 2018-11-29 03:20 | 0.29202 | 20.2345
15.4514 | 2018-11-29 03:30 | 0.3737 | 22.9973
15.4583 | 2018-11-29 03:40 | 0.40261 | 13.7946
15.4653 | 2018-11-29 03:50 | 0.39493 | 12.875
15.4722 | 2018-11-29 04:00 | 0.51658 | 11.0489
15.4792 | 2018-11-29 04:10 | 0.51658 | 11.0489
15.4861 | 2018-11-29 04:20 | 0.61316 | 1.3083
15.4931 | 2018-11-29 04:30 | 0.73227 | 10.0669
15.5 | 2018-11-29 04:40 | 0.75153 | 6.9548
15.5069 | 2018-11-29 04:50 | 0.86659 | 2.1162
15.5139 | 2018-11-29 05:00 | 0.83925 | 10.5735
15.5208 | 2018-11-29 05:10 | 0.83925 | 10.5735
15.5278 | 2018-11-29 05:20 | 0.86131 | 7.4716
15.5347 | 2018-11-29 05:30 | 0.76357 | 3.6793
15.5417 | 2018-11-29 05:40 | 0.8968 | 9.6934
15.5486 | 2018-11-29 05:50 | 0.86184 | 2.5271
15.5556 | 2018-11-29 06:00 | 0.95746 | 6.6574
15.5625 | 2018-11-29 06:10 | 0.95746 | 6.6574
15.5694 | 2018-11-29 06:20 | 0.7967 | 3.7423
15.5764 | 2018-11-29 06:30 | 0.84742 | 11.2967
15.5833 | 2018-11-29 06:40 | 0.80689 | 9.8476
15.5903 | 2018-11-29 06:50 | 0.59841 | 3.9287
15.5972 | 2018-11-29 07:00 | 0.7663 | 6.7448
15.6042 | 2018-11-29 07:10 | 0.7663 | 6.7448
15.6111 | 2018-11-29 07:20 | 0.77631 | 1.6239
15.6181 | 2018-11-29 07:30 | 0.5362 | 7.178
15.625 | 2018-11-29 07:40 | 0.68058 | 357.6421
15.6319 | 2018-11-29 07:50 | 0.43657 | 8.2971
15.6389 | 2018-11-29 08:00 | 0.61158 | 4.1257
15.6458 | 2018-11-29 08:10 | 0.61158 | 4.1257
15.6528 | 2018-11-29 08:20 | 0.52493 | 4.9177
15.6597 | 2018-11-29 08:30 | 0.46018 | 4.1122
15.6667 | 2018-11-29 08:40 | 0.474 | 0.12088
15.6736 | 2018-11-29 08:50 | 0.32069 | 356.2454
15.6806 | 2018-11-29 09:00 | 0.40415 | 358.4403
15.6875 | 2018-11-29 09:10 | 0.40415 | 358.4403
15.6944 | 2018-11-29 09:20 | 0.33494 | 346.0052
15.7014 | 2018-11-29 09:30 | 0.18651 | 346.0383
15.7083 | 2018-11-29 09:40 | 0.10469 | 17.2234
15.7153 | 2018-11-29 09:50 | 0.11642 | 13.9169
15.7222 | 2018-11-29 10:00 | 0.11166 | 231.1799
15.7292 | 2018-11-29 10:10 | 0.11166 | 231.1799
15.7361 | 2018-11-29 10:20 | 0.22737 | 183.2777
15.7431 | 2018-11-29 10:30 | 0.3028 | 191.2357
15.75 | 2018-11-29 10:40 | 0.36345 | 182.8388
15.7569 | 2018-11-29 10:50 | 0.36173 | 183.6455
15.7639 | 2018-11-29 11:00 | 0.41362 | 195.2794
15.7708 | 2018-11-29 11:10 | 0.41362 | 195.2794
15.7778 | 2018-11-29 11:20 | 0.46552 | 182.7088
15.7847 | 2018-11-29 11:30 | 0.56496 | 183.3486
15.7917 | 2018-11-29 11:40 | 0.56295 | 190.232
15.7986 | 2018-11-29 11:50 | 0.5638 | 192.7052
15.8056 | 2018-11-29 12:00 | 0.54179 | 186.784
15.8125 | 2018-11-29 12:10 | 0.54179 | 186.784
15.8194 | 2018-11-29 12:20 | 0.506 | 179.8868
15.8264 | 2018-11-29 12:30 | 0.54302 | 180.5276
15.8333 | 2018-11-29 12:40 | 0.51095 | 189.4623
15.8403 | 2018-11-29 12:50 | 0.44196 | 187.6718
15.8472 | 2018-11-29 13:00 | 0.47187 | 185.1065
15.8542 | 2018-11-29 13:10 | 0.47187 | 185.1065
15.8611 | 2018-11-29 13:20 | 0.41395 | 183.8785
15.8681 | 2018-11-29 13:30 | 0.45497 | 172.422
15.875 | 2018-11-29 13:40 | 0.32559 | 172.7659
15.8819 | 2018-11-29 13:50 | 0.33838 | 177.2898
15.8889 | 2018-11-29 14:00 | 0.28106 | 186.948
15.8958 | 2018-11-29 14:10 | 0.28106 | 186.948
15.9028 | 2018-11-29 14:20 | 0.25916 | 181.9902
15.9097 | 2018-11-29 14:30 | 0.23929 | 187.9269
15.9167 | 2018-11-29 14:40 | 0.13732 | 154.5546
15.9236 | 2018-11-29 14:50 | 0.10728 | 191.8336
15.9306 | 2018-11-29 15:00 | 0.1058 | 143.455
15.9375 | 2018-11-29 15:10 | 0.1058 | 143.455
15.9444 | 2018-11-29 15:20 | 0.14375 | 78.7682
15.9514 | 2018-11-29 15:30 | 0.17871 | 66.5909
15.9583 | 2018-11-29 15:40 | 0.28718 | 17.4254
15.9653 | 2018-11-29 15:50 | 0.27893 | 14.5345
15.9722 | 2018-11-29 16:00 | 0.38172 | 15.966
15.9792 | 2018-11-29 16:10 | 0.38172 | 15.966
15.9861 | 2018-11-29 16:20 | 0.43841 | 17.1123
15.9931 | 2018-11-29 16:30 | 0.35526 | 16.8537
16 | 2018-11-29 16:40 | 0.64722 | 7.2787
16.0069 | 2018-11-29 16:50 | 0.7336 | 6.4178
16.0139 | 2018-11-29 17:00 | 0.62576 | 7.0682
16.0208 | 2018-11-29 17:10 | 0.62576 | 7.0682
16.0278 | 2018-11-29 17:20 | 0.80964 | 7.8799
16.0347 | 2018-11-29 17:30 | 0.75648 | 13.6872
16.0417 | 2018-11-29 17:40 | 0.75803 | 7.8094
16.0486 | 2018-11-29 17:50 | 0.78946 | 358.0401
16.0556 | 2018-11-29 18:00 | 0.86819 | 8.3448
16.0625 | 2018-11-29 18:10 | 0.86819 | 8.3448
16.0694 | 2018-11-29 18:20 | 0.78583 | 9.5223
16.0764 | 2018-11-29 18:30 | 0.69993 | 2.9483
16.0833 | 2018-11-29 18:40 | 0.64054 | 5.1053
16.0903 | 2018-11-29 18:50 | 0.72716 | 4.4168
16.0972 | 2018-11-29 19:00 | 0.64545 | 8.105
16.1042 | 2018-11-29 19:10 | 0.64545 | 8.105
16.1111 | 2018-11-29 19:20 | 0.68789 | 5.2548
16.1181 | 2018-11-29 19:30 | 0.73267 | 7.1347
16.125 | 2018-11-29 19:40 | 0.55832 | 9.901
16.1319 | 2018-11-29 19:50 | 0.525 | 6.1233
16.1389 | 2018-11-29 20:00 | 0.64395 | 9.5647
16.1458 | 2018-11-29 20:10 | 0.64395 | 9.5647
16.1528 | 2018-11-29 20:20 | 0.42696 | 11.7573
16.1597 | 2018-11-29 20:30 | 0.48774 | 11.4712
16.1667 | 2018-11-29 20:40 | 0.38042 | 9.6852
16.1736 | 2018-11-29 20:50 | 0.28752 | 352.4054
16.1806 | 2018-11-29 21:00 | 0.28211 | 9.7962
16.1875 | 2018-11-29 21:10 | 0.28211 | 9.7962
16.1944 | 2018-11-29 21:20 | 0.27259 | 3.7861
16.2014 | 2018-11-29 21:30 | 0.22429 | 353.8573
16.2083 | 2018-11-29 21:40 | 0.21246 | 345.8329
16.2153 | 2018-11-29 21:50 | 0.14765 | 331.6992
16.2222 | 2018-11-29 22:00 | 0.095273 | 339.092
16.2292 | 2018-11-29 22:10 | 0.095273 | 339.092
16.2361 | 2018-11-29 22:20 | 0.069065 | 235.6197
16.2431 | 2018-11-29 22:30 | 0.14109 | 196.8937
16.25 | 2018-11-29 22:40 | 0.2388 | 213.557
16.2569 | 2018-11-29 22:50 | 0.332 | 196.0876
16.2639 | 2018-11-29 23:00 | 0.47456 | 187.0202
16.2708 | 2018-11-29 23:10 | 0.47456 | 187.0202
16.2778 | 2018-11-29 23:20 | 0.43196 | 194.0684
16.2847 | 2018-11-29 23:30 | 0.40363 | 191.8667
16.2917 | 2018-11-29 23:40 | 0.44421 | 187.893
16.2986 | 2018-11-29 23:50 | 0.48421 | 191.1939
16.3056 | 2018-11-30 | 0.47012 | 190.6646
16.3125 | 2018-11-30 00:10 | 0.47012 | 190.6646
16.3194 | 2018-11-30 00:20 | 0.47344 | 185.819
16.3264 | 2018-11-30 00:30 | 0.51405 | 191.9001
16.3333 | 2018-11-30 00:40 | 0.54833 | 181.9857
16.3403 | 2018-11-30 00:50 | 0.45471 | 187.3282
16.3472 | 2018-11-30 01:00 | 0.5 | 180
16.3542 | 2018-11-30 01:10 | 0.5 | 180
16.3611 | 2018-11-30 01:20 | 0.42806 | 180.937
16.3681 | 2018-11-30 01:30 | 0.58577 | 182.9357
16.375 | 2018-11-30 01:40 | 0.56601 | 180.4049
16.3819 | 2018-11-30 01:50 | 0.43325 | 187.0266
16.3889 | 2018-11-30 02:00 | 0.49961 | 189.3304
16.3958 | 2018-11-30 02:10 | 0.49961 | 189.3304
16.4028 | 2018-11-30 02:20 | 0.38316 | 181.6451
16.4097 | 2018-11-30 02:30 | 0.33676 | 187.336
16.4167 | 2018-11-30 02:40 | 0.26554 | 176.3295
16.4236 | 2018-11-30 02:50 | 0.22011 | 181.8224
16.4306 | 2018-11-30 03:00 | 0.28911 | 181.5856
16.4375 | 2018-11-30 03:10 | 0.28911 | 181.5856
16.4444 | 2018-11-30 03:20 | 0.1416 | 132.1376
16.4514 | 2018-11-30 03:30 | 0.10944 | 167.8687
16.4583 | 2018-11-30 03:40 | 0.072471 | 207.9795
16.4653 | 2018-11-30 03:50 | 0.11531 | 46.757
16.4722 | 2018-11-30 04:00 | 0.24742 | 14.9911
16.4792 | 2018-11-30 04:10 | 0.24742 | 14.9911
16.4861 | 2018-11-30 04:20 | 0.43673 | 18.9743
16.4931 | 2018-11-30 04:30 | 0.38359 | 18.8601
16.5 | 2018-11-30 04:40 | 0.49419 | 9.0811
16.5069 | 2018-11-30 04:50 | 0.50642 | 13.707
16.5139 | 2018-11-30 05:00 | 0.53606 | 5.0299
16.5208 | 2018-11-30 05:10 | 0.53606 | 5.0299
16.5278 | 2018-11-30 05:20 | 0.75049 | 6.2727
16.5347 | 2018-11-30 05:30 | 0.72378 | 14.7274
16.5417 | 2018-11-30 05:40 | 0.8269 | 8.4143
16.5486 | 2018-11-30 05:50 | 0.72818 | 11.3254
16.5556 | 2018-11-30 06:00 | 0.81484 | 4.787
16.5625 | 2018-11-30 06:10 | 0.81484 | 4.787
16.5694 | 2018-11-30 06:20 | 0.77605 | 11.6719
16.5764 | 2018-11-30 06:30 | 0.73721 | 4.4345
16.5833 | 2018-11-30 06:40 | 0.71244 | 2.011
16.5903 | 2018-11-30 06:50 | 0.70814 | 358.8672
16.5972 | 2018-11-30 07:00 | 0.79147 | 6.0924
16.6042 | 2018-11-30 07:10 | 0.79147 | 6.0924
16.6111 | 2018-11-30 07:20 | 0.77889 | 4.9347
16.6181 | 2018-11-30 07:30 | 0.78021 | 6.624
16.625 | 2018-11-30 07:40 | 0.71461 | 4.8968
16.6319 | 2018-11-30 07:50 | 0.69014 | 11.6193
16.6389 | 2018-11-30 08:00 | 0.677 | 9.351
16.6458 | 2018-11-30 08:10 | 0.677 | 9.351
16.6528 | 2018-11-30 08:20 | 0.65309 | 8.4527
16.6597 | 2018-11-30 08:30 | 0.5343 | 1.9306
16.6667 | 2018-11-30 08:40 | 0.53682 | 5.8805
16.6736 | 2018-11-30 08:50 | 0.52133 | 8.9383
16.6806 | 2018-11-30 09:00 | 0.37893 | 7.125
16.6875 | 2018-11-30 09:10 | 0.37893 | 7.125
16.6944 | 2018-11-30 09:20 | 0.40336 | 2.4155
16.7014 | 2018-11-30 09:30 | 0.35304 | 0.8115
16.7083 | 2018-11-30 09:40 | 0.34232 | 354.9723
16.7153 | 2018-11-30 09:50 | 0.3167 | 3.802
16.7222 | 2018-11-30 10:00 | 0.18764 | 16.4068
16.7292 | 2018-11-30 10:10 | 0.18764 | 16.4068
16.7361 | 2018-11-30 10:20 | 0.13534 | 351.9298
16.7431 | 2018-11-30 10:30 | 0.1156 | 307.2664
16.75 | 2018-11-30 10:40 | 0.12847 | 328.0419
16.7569 | 2018-11-30 10:50 | 0.13185 | 279.6052
16.7639 | 2018-11-30 11:00 | 0.14831 | 251.9315
16.7708 | 2018-11-30 11:10 | 0.14831 | 251.9315
16.7778 | 2018-11-30 11:20 | 0.25287 | 228.3665
16.7847 | 2018-11-30 11:30 | 0.29879 | 202.0151
16.7917 | 2018-11-30 11:40 | 0.34763 | 202.1381
16.7986 | 2018-11-30 11:50 | 0.3839 | 200.7482
16.8056 | 2018-11-30 12:00 | 0.45318 | 195.3549
16.8125 | 2018-11-30 12:10 | 0.45318 | 195.3549
16.8194 | 2018-11-30 12:20 | 0.53954 | 190.7893
16.8264 | 2018-11-30 12:30 | 0.63732 | 185.8537
16.8333 | 2018-11-30 12:40 | 0.5804 | 187.823
16.8403 | 2018-11-30 12:50 | 0.60995 | 188.0105
16.8472 | 2018-11-30 13:00 | 0.58398 | 190.0591
16.8542 | 2018-11-30 13:10 | 0.58398 | 190.0591
16.8611 | 2018-11-30 13:20 | 0.59066 | 185.4403
16.8681 | 2018-11-30 13:30 | 0.67266 | 186.7447
16.875 | 2018-11-30 13:40 | 0.65429 | 183.5927
16.8819 | 2018-11-30 13:50 | 0.71444 | 184.737
16.8889 | 2018-11-30 14:00 | 0.553 | 179.8964
16.8958 | 2018-11-30 14:10 | 0.553 | 179.8964
16.9028 | 2018-11-30 14:20 | 0.63985 | 182.9563
16.9097 | 2018-11-30 14:30 | 0.61143 | 182.1558
16.9167 | 2018-11-30 14:40 | 0.51638 | 186.5607
16.9236 | 2018-11-30 14:50 | 0.50562 | 177.1659
16.9306 | 2018-11-30 15:00 | 0.61555 | 185.2197
16.9375 | 2018-11-30 15:10 | 0.61555 | 185.2197
16.9444 | 2018-11-30 15:20 | 0.42851 | 184.8192
16.9514 | 2018-11-30 15:30 | 0.3899 | 188.1093
16.9583 | 2018-11-30 15:40 | 0.36572 | 183.6057
16.9653 | 2018-11-30 15:50 | 0.30595 | 189.216
16.9722 | 2018-11-30 16:00 | 0.2822 | 174.7137
16.9792 | 2018-11-30 16:10 | 0.2822 | 174.7137
16.9861 | 2018-11-30 16:20 | 0.10608 | 177.8389
16.9931 | 2018-11-30 16:30 | 0.038079 | 330.0685
17 | 2018-11-30 16:40 | 0.097406 | 109.179
17.0069 | 2018-11-30 16:50 | 0.11273 | 64.7989
17.0139 | 2018-11-30 17:00 | 0.14276 | 50.4
17.0208 | 2018-11-30 17:10 | 0.14276 | 50.4
17.0278 | 2018-11-30 17:20 | 0.3246 | 15.3635
17.0347 | 2018-11-30 17:30 | 0.36063 | 21.2999
17.0417 | 2018-11-30 17:40 | 0.38524 | 8.5087
17.0486 | 2018-11-30 17:50 | 0.42967 | 3.202
17.0556 | 2018-11-30 18:00 | 0.46815 | 10.7099
17.0625 | 2018-11-30 18:10 | 0.46815 | 10.7099
17.0694 | 2018-11-30 18:20 | 0.55724 | 17.6546
17.0764 | 2018-11-30 18:30 | 0.5832 | 6.0039
17.0833 | 2018-11-30 18:40 | 0.57699 | 11.6994
17.0903 | 2018-11-30 18:50 | 0.64909 | 10.1154
17.0972 | 2018-11-30 19:00 | 0.62961 | 8.3103
17.1042 | 2018-11-30 19:10 | 0.62961 | 8.3103
17.1111 | 2018-11-30 19:20 | 0.66058 | 8.0933
17.1181 | 2018-11-30 19:30 | 0.72 | 3.0253
17.125 | 2018-11-30 19:40 | 0.5829 | 10.5774
17.1319 | 2018-11-30 19:50 | 0.59152 | 9.1438
17.1389 | 2018-11-30 20:00 | 0.62504 | 359.3583
17.1458 | 2018-11-30 20:10 | 0.62504 | 359.3583
17.1528 | 2018-11-30 20:20 | 0.56549 | 5.3779
17.1597 | 2018-11-30 20:30 | 0.53131 | 1.9415
17.1667 | 2018-11-30 20:40 | 0.44571 | 354.9801
17.1736 | 2018-11-30 20:50 | 0.45178 | 9.9419
17.1806 | 2018-11-30 21:00 | 0.45439 | 7.9696
17.1875 | 2018-11-30 21:10 | 0.45439 | 7.9696
17.1944 | 2018-11-30 21:20 | 0.43852 | 11.3099
17.2014 | 2018-11-30 21:30 | 0.36552 | 16.2038
17.2083 | 2018-11-30 21:40 | 0.31331 | 353.0338
17.2153 | 2018-11-30 21:50 | 0.22621 | 350.3295
17.2222 | 2018-11-30 22:00 | 0.20695 | 12.5588
17.2292 | 2018-11-30 22:10 | 0.20695 | 12.5588
17.2361 | 2018-11-30 22:20 | 0.18228 | 343.7524
17.2431 | 2018-11-30 22:30 | 0.1332 | 339.7964
17.25 | 2018-11-30 22:40 | 0.12902 | 307.7581
17.2569 | 2018-11-30 22:50 | 0.026571 | 289.7989
17.2639 | 2018-11-30 23:00 | 0.068029 | 204.3046
17.2708 | 2018-11-30 23:10 | 0.068029 | 204.3046
17.2778 | 2018-11-30 23:20 | 0.21225 | 231.8883
17.2847 | 2018-11-30 23:30 | 0.2342 | 200.7565
17.2917 | 2018-11-30 23:40 | 0.30317 | 194.1279
17.2986 | 2018-11-30 23:50 | 0.28497 | 190.7185
17.3056 | 2018-12-01 | 0.39538 | 193.1575
17.3125 | 2018-12-01 00:10 | 0.39538 | 193.1575
17.3194 | 2018-12-01 00:20 | 0.45252 | 184.69
17.3264 | 2018-12-01 00:30 | 0.4598 | 198.1197
17.3333 | 2018-12-01 00:40 | 0.50274 | 192.4052
17.3403 | 2018-12-01 00:50 | 0.48622 | 190.5473
17.3472 | 2018-12-01 01:00 | 0.49809 | 183.7988
17.3542 | 2018-12-01 01:10 | 0.49809 | 183.7988
17.3611 | 2018-12-01 01:20 | 0.56703 | 189.0304
17.3681 | 2018-12-01 01:30 | 0.49422 | 191.6737
17.375 | 2018-12-01 01:40 | 0.62056 | 190.5856
17.3819 | 2018-12-01 01:50 | 0.63538 | 181.9843
17.3889 | 2018-12-01 02:00 | 0.53059 | 175.5682
17.3958 | 2018-12-01 02:10 | 0.53059 | 175.5682
17.4028 | 2018-12-01 02:20 | 0.50483 | 183.2932
17.4097 | 2018-12-01 02:30 | 0.59482 | 188.0211
17.4167 | 2018-12-01 02:40 | 0.64105 | 179.285
17.4236 | 2018-12-01 02:50 | 0.58161 | 185.4263
17.4306 | 2018-12-01 03:00 | 0.54702 | 175.0711
17.4375 | 2018-12-01 03:10 | 0.54702 | 175.0711
17.4444 | 2018-12-01 03:20 | 0.64245 | 174.9994
17.4514 | 2018-12-01 03:30 | 0.41006 | 179.0219
17.4583 | 2018-12-01 03:40 | 0.57463 | 182.6931
17.4653 | 2018-12-01 03:50 | 0.4577 | 189.8122
17.4722 | 2018-12-01 04:00 | 0.51614 | 185.2246
17.4792 | 2018-12-01 04:10 | 0.51614 | 185.2246
17.4861 | 2018-12-01 04:20 | 0.30616 | 181.8717
17.4931 | 2018-12-01 04:30 | 0.25301 | 180.4529
17.5 | 2018-12-01 04:40 | 0.18559 | 164.6907
17.5069 | 2018-12-01 04:50 | 0.11404 | 178.4926
17.5139 | 2018-12-01 05:00 | 0.036878 | 167.4712
17.5208 | 2018-12-01 05:10 | 0.036878 | 167.4712
17.5278 | 2018-12-01 05:20 | 0.051 | 0
17.5347 | 2018-12-01 05:30 | 0.1287 | 44.3704
17.5417 | 2018-12-01 05:40 | 0.27924 | 19.0189
17.5486 | 2018-12-01 05:50 | 0.33097 | 27.3393
17.5556 | 2018-12-01 06:00 | 0.34027 | 11.0127
17.5625 | 2018-12-01 06:10 | 0.34027 | 11.0127
17.5694 | 2018-12-01 06:20 | 0.43903 | 3.9182
17.5764 | 2018-12-01 06:30 | 0.5205 | 9.0642
17.5833 | 2018-12-01 06:40 | 0.53738 | 11.8118
17.5903 | 2018-12-01 06:50 | 0.67905 | 10.3501
17.5972 | 2018-12-01 07:00 | 0.70613 | 3.2473
17.6042 | 2018-12-01 07:10 | 0.70613 | 3.2473
17.6111 | 2018-12-01 07:20 | 0.71013 | 4.442
17.6181 | 2018-12-01 07:30 | 0.78251 | 5.4264
17.625 | 2018-12-01 07:40 | 0.67307 | 11.3099
17.6319 | 2018-12-01 07:50 | 0.76133 | 11.5166
17.6389 | 2018-12-01 08:00 | 0.72567 | 14.0362
17.6458 | 2018-12-01 08:10 | 0.72567 | 14.0362
17.6528 | 2018-12-01 08:20 | 0.74308 | 9.4496
17.6597 | 2018-12-01 08:30 | 0.7231 | 11.7295
17.6667 | 2018-12-01 08:40 | 0.72995 | 11.2176
17.6736 | 2018-12-01 08:50 | 0.66009 | 10.0331
17.6806 | 2018-12-01 09:00 | 0.75909 | 7.2654
17.6875 | 2018-12-01 09:10 | 0.75909 | 7.2654
17.6944 | 2018-12-01 09:20 | 0.67771 | 2.6218
17.7014 | 2018-12-01 09:30 | 0.57239 | 15.7117
17.7083 | 2018-12-01 09:40 | 0.70867 | 7.8671
17.7153 | 2018-12-01 09:50 | 0.59833 | 6.0441
17.7222 | 2018-12-01 10:00 | 0.47855 | 14.6461
17.7292 | 2018-12-01 10:10 | 0.47855 | 14.6461
17.7361 | 2018-12-01 10:20 | 0.50619 | 1.5849
17.7431 | 2018-12-01 10:30 | 0.37864 | 3.3309
17.75 | 2018-12-01 10:40 | 0.33624 | 12.7136
17.7569 | 2018-12-01 10:50 | 0.37387 | 19.6951
17.7639 | 2018-12-01 11:00 | 0.41059 | 356.9285
17.7708 | 2018-12-01 11:10 | 0.41059 | 356.9285
17.7778 | 2018-12-01 11:20 | 0.29044 | 3.1579
17.7847 | 2018-12-01 11:30 | 0.31305 | 10.3049
17.7917 | 2018-12-01 11:40 | 0.24836 | 16.6109
17.7986 | 2018-12-01 11:50 | 0.2081 | 346.0973
17.8056 | 2018-12-01 12:00 | 0.12028 | 47.0214
17.8125 | 2018-12-01 12:10 | 0.12028 | 47.0214
17.8194 | 2018-12-01 12:20 | 0.037162 | 23.8059
17.8264 | 2018-12-01 12:30 | 0.009 | 90
17.8333 | 2018-12-01 12:40 | 0.043566 | 189.2461
17.8403 | 2018-12-01 12:50 | 0.16528 | 201.2864
17.8472 | 2018-12-01 13:00 | 0.20407 | 208.7001
17.8542 | 2018-12-01 13:10 | 0.20407 | 208.7001
17.8611 | 2018-12-01 13:20 | 0.35902 | 179.3616
17.8681 | 2018-12-01 13:30 | 0.35364 | 193.4075
17.875 | 2018-12-01 13:40 | 0.41791 | 187.8393
17.8819 | 2018-12-01 13:50 | 0.48889 | 185.0459
17.8889 | 2018-12-01 14:00 | 0.50163 | 187.7909
17.8958 | 2018-12-01 14:10 | 0.50163 | 187.7909
17.9028 | 2018-12-01 14:20 | 0.42699 | 183.8944
17.9097 | 2018-12-01 14:30 | 0.39189 | 195.845
17.9167 | 2018-12-01 14:40 | 0.54903 | 179.3738
17.9236 | 2018-12-01 14:50 | 0.51471 | 176.9931
17.9306 | 2018-12-01 15:00 | 0.46613 | 178.6478
17.9375 | 2018-12-01 15:10 | 0.46613 | 178.6478
17.9444 | 2018-12-01 15:20 | 0.45803 | 180.6255
17.9514 | 2018-12-01 15:30 | 0.46922 | 190.0646
17.9583 | 2018-12-01 15:40 | 0.46579 | 191.7683
17.9653 | 2018-12-01 15:50 | 0.44734 | 191.0839
17.9722 | 2018-12-01 16:00 | 0.50267 | 182.9649
17.9792 | 2018-12-01 16:10 | 0.50267 | 182.9649
17.9861 | 2018-12-01 16:20 | 0.40618 | 175.6229
17.9931 | 2018-12-01 16:30 | 0.35217 | 173.6418
18 | 2018-12-01 16:40 | 0.37209 | 178.768
18.0069 | 2018-12-01 16:50 | 0.233 | 180
18.0139 | 2018-12-01 17:00 | 0.25948 | 163.6603
18.0208 | 2018-12-01 17:10 | 0.25948 | 163.6603
18.0278 | 2018-12-01 17:20 | 0.13809 | 182.075
18.0347 | 2018-12-01 17:30 | 0.15498 | 162.7342
18.0417 | 2018-12-01 17:40 | 0.11732 | 161.1017
18.0486 | 2018-12-01 17:50 | 0.073055 | 109.179
18.0556 | 2018-12-01 18:00 | 0.08 | 90
18.0625 | 2018-12-01 18:10 | 0.08 | 90
18.0694 | 2018-12-01 18:20 | 0.12369 | 22.8336
18.0764 | 2018-12-01 18:30 | 0.23646 | 38.13
18.0833 | 2018-12-01 18:40 | 0.38598 | 27.2953
18.0903 | 2018-12-01 18:50 | 0.39761 | 21.0789
18.0972 | 2018-12-01 19:00 | 0.42657 | 10.8094
18.1042 | 2018-12-01 19:10 | 0.42657 | 10.8094
18.1111 | 2018-12-01 19:20 | 0.37814 | 13.3012
18.1181 | 2018-12-01 19:30 | 0.39415 | 16.9638
18.125 | 2018-12-01 19:40 | 0.35902 | 4.313
18.1319 | 2018-12-01 19:50 | 0.38937 | 2.5023
18.1389 | 2018-12-01 20:00 | 0.53649 | 4.2758
18.1458 | 2018-12-01 20:10 | 0.53649 | 4.2758
18.1528 | 2018-12-01 20:20 | 0.69462 | 13.9962
18.1597 | 2018-12-01 20:30 | 0.7513 | 9.4999
18.1667 | 2018-12-01 20:40 | 0.6358 | 7.0468
18.1736 | 2018-12-01 20:50 | 0.685 | 359.9164
18.1806 | 2018-12-01 21:00 | 0.59973 | 9.211
18.1875 | 2018-12-01 21:10 | 0.59973 | 9.211
18.1944 | 2018-12-01 21:20 | 0.60133 | 6.8768
18.2014 | 2018-12-01 21:30 | 0.73677 | 3.9693
18.2083 | 2018-12-01 21:40 | 0.61881 | 12.1271
18.2153 | 2018-12-01 21:50 | 0.6624 | 12.3787
18.2222 | 2018-12-01 22:00 | 0.47156 | 2.7957
18.2292 | 2018-12-01 22:10 | 0.47156 | 2.7957
18.2361 | 2018-12-01 22:20 | 0.55227 | 8.6436
18.2431 | 2018-12-01 22:30 | 0.4825 | 2.6133
18.25 | 2018-12-01 22:40 | 0.38369 | 356.5634
18.2569 | 2018-12-01 22:50 | 0.39714 | 11.6212
18.2639 | 2018-12-01 23:00 | 0.33743 | 2.8878
18.2708 | 2018-12-01 23:10 | 0.33743 | 2.8878
18.2778 | 2018-12-01 23:20 | 0.27735 | 8.9189
18.2847 | 2018-12-01 23:30 | 0.23902 | 359.2809
18.2917 | 2018-12-01 23:40 | 0.22241 | 353.546
18.2986 | 2018-12-01 23:50 | 0.13871 | 5.7928
18.3056 | 2018-12-02 | 0.11229 | 4.0856
18.3125 | 2018-12-02 00:10 | 0.11229 | 4.0856
18.3194 | 2018-12-02 00:20 | 0.12398 | 204.291
18.3264 | 2018-12-02 00:30 | 0.13027 | 204.0071
18.3333 | 2018-12-02 00:40 | 0.14004 | 204.918
18.3403 | 2018-12-02 00:50 | 0.27983 | 209.3131
18.3472 | 2018-12-02 01:00 | 0.25028 | 203.7998
18.3542 | 2018-12-02 01:10 | 0.25028 | 203.7998
18.3611 | 2018-12-02 01:20 | 0.36053 | 189.0966
18.3681 | 2018-12-02 01:30 | 0.42109 | 191.9237
18.375 | 2018-12-02 01:40 | 0.43245 | 194.3255
18.3819 | 2018-12-02 01:50 | 0.50393 | 192.4918
18.3889 | 2018-12-02 02:00 | 0.46515 | 181.4783
18.3958 | 2018-12-02 02:10 | 0.46515 | 181.4783
18.4028 | 2018-12-02 02:20 | 0.57067 | 188.7691
18.4097 | 2018-12-02 02:30 | 0.60379 | 185.5123
18.4167 | 2018-12-02 02:40 | 0.6038 | 187.2309
18.4236 | 2018-12-02 02:50 | 0.48084 | 185.011
18.4306 | 2018-12-02 03:00 | 0.60896 | 185.6544
18.4375 | 2018-12-02 03:10 | 0.60896 | 185.6544
18.4444 | 2018-12-02 03:20 | 0.53428 | 183.971
18.4514 | 2018-12-02 03:30 | 0.61503 | 180.559
18.4583 | 2018-12-02 03:40 | 0.65734 | 181.8307
18.4653 | 2018-12-02 03:50 | 0.70996 | 182.9873
18.4722 | 2018-12-02 04:00 | 0.646 | 180
18.4792 | 2018-12-02 04:10 | 0.646 | 180
18.4861 | 2018-12-02 04:20 | 0.6324 | 183.808
18.4931 | 2018-12-02 04:30 | 0.50554 | 195.1358
18.5 | 2018-12-02 04:40 | 0.40942 | 171.573
18.5069 | 2018-12-02 04:50 | 0.45052 | 175.2892
18.5139 | 2018-12-02 05:00 | 0.45926 | 175.7544
18.5208 | 2018-12-02 05:10 | 0.45926 | 175.7544
18.5278 | 2018-12-02 05:20 | 0.38722 | 178.0761
18.5347 | 2018-12-02 05:30 | 0.41208 | 178.8876
18.5417 | 2018-12-02 05:40 | 0.264 | 180
18.5486 | 2018-12-02 05:50 | 0.23675 | 171.2538
18.5556 | 2018-12-02 06:00 | 0.15602 | 189.2208
18.5625 | 2018-12-02 06:10 | 0.15602 | 189.2208
18.5694 | 2018-12-02 06:20 | 0.12346 | 125.1061
18.5764 | 2018-12-02 06:30 | 0.10971 | 47.5858
18.5833 | 2018-12-02 06:40 | 0.16053 | 4.6451
18.5903 | 2018-12-02 06:50 | 0.24584 | 7.0094
18.5972 | 2018-12-02 07:00 | 0.35109 | 27.2949
18.6042 | 2018-12-02 07:10 | 0.35109 | 27.2949
18.6111 | 2018-12-02 07:20 | 0.46167 | 11.748
18.6181 | 2018-12-02 07:30 | 0.54936 | 17.4785
18.625 | 2018-12-02 07:40 | 0.4859 | 6.2621
18.6319 | 2018-12-02 07:50 | 0.48849 | 8.5946
18.6389 | 2018-12-02 08:00 | 0.67218 | 8.3832
18.6458 | 2018-12-02 08:10 | 0.67218 | 8.3832
18.6528 | 2018-12-02 08:20 | 0.69418 | 4.5443
18.6597 | 2018-12-02 08:30 | 0.80514 | 7.637
18.6667 | 2018-12-02 08:40 | 0.765 | 8.7974
18.6736 | 2018-12-02 08:50 | 0.73206 | 6.0377
18.6806 | 2018-12-02 09:00 | 0.75571 | 4.8581
18.6875 | 2018-12-02 09:10 | 0.75571 | 4.8581
18.6944 | 2018-12-02 09:20 | 0.77519 | 358.7434
18.7014 | 2018-12-02 09:30 | 0.7985 | 3.5181
18.7083 | 2018-12-02 09:40 | 0.7264 | 14.2658
18.7153 | 2018-12-02 09:50 | 0.60981 | 7.9175
18.7222 | 2018-12-02 10:00 | 0.71701 | 3.038
18.7292 | 2018-12-02 10:10 | 0.71701 | 3.038
18.7361 | 2018-12-02 10:20 | 0.58993 | 6.6191
18.7431 | 2018-12-02 10:30 | 0.66627 | 4.7351
18.75 | 2018-12-02 10:40 | 0.72997 | 6.6869
18.7569 | 2018-12-02 10:50 | 0.59227 | 1.7416
18.7639 | 2018-12-02 11:00 | 0.508 | 0.11279
18.7708 | 2018-12-02 11:10 | 0.508 | 0.11279
18.7778 | 2018-12-02 11:20 | 0.56079 | 8.9248
18.7847 | 2018-12-02 11:30 | 0.46615 | 358.5249
18.7917 | 2018-12-02 11:40 | 0.496 | 0.23103
18.7986 | 2018-12-02 11:50 | 0.36572 | 3.6057
18.8056 | 2018-12-02 12:00 | 0.37819 | 352.5555
18.8125 | 2018-12-02 12:10 | 0.37819 | 352.5555
18.8194 | 2018-12-02 12:20 | 0.36025 | 355.2231
18.8264 | 2018-12-02 12:30 | 0.33155 | 346.2152
18.8333 | 2018-12-02 12:40 | 0.24502 | 0.70155
18.8403 | 2018-12-02 12:50 | 0.19059 | 355.486
18.8472 | 2018-12-02 13:00 | 0.16341 | 338.459
18.8542 | 2018-12-02 13:10 | 0.16341 | 338.459
18.8611 | 2018-12-02 13:20 | 0.11628 | 333.4349
18.8681 | 2018-12-02 13:30 | 0.14717 | 267.2737
18.875 | 2018-12-02 13:40 | 0.23012 | 227.9943
18.8819 | 2018-12-02 13:50 | 0.20647 | 231.6869
18.8889 | 2018-12-02 14:00 | 0.35954 | 203.7845
18.8958 | 2018-12-02 14:10 | 0.35954 | 203.7845
18.9028 | 2018-12-02 14:20 | 0.42832 | 193.7767
18.9097 | 2018-12-02 14:30 | 0.40874 | 201.2287
18.9167 | 2018-12-02 14:40 | 0.45664 | 192.3927
18.9236 | 2018-12-02 14:50 | 0.46841 | 190.2064
18.9306 | 2018-12-02 15:00 | 0.48978 | 188.8084
18.9375 | 2018-12-02 15:10 | 0.48978 | 188.8084
18.9444 | 2018-12-02 15:20 | 0.53615 | 188.6893
18.9514 | 2018-12-02 15:30 | 0.68306 | 186.9794
18.9583 | 2018-12-02 15:40 | 0.59818 | 184.8909
18.9653 | 2018-12-02 15:50 | 0.59091 | 187.3896
18.9722 | 2018-12-02 16:00 | 0.56303 | 179.3894
18.9792 | 2018-12-02 16:10 | 0.56303 | 179.3894
18.9861 | 2018-12-02 16:20 | 0.62548 | 183.942
18.9931 | 2018-12-02 16:30 | 0.6906 | 183.9024
19 | 2018-12-02 16:40 | 0.58045 | 184.0504
19.0069 | 2018-12-02 16:50 | 0.6631 | 185.5386
19.0139 | 2018-12-02 17:00 | 0.60836 | 178.0218
19.0208 | 2018-12-02 17:10 | 0.60836 | 178.0218
19.0278 | 2018-12-02 17:20 | 0.56657 | 188.7308
19.0347 | 2018-12-02 17:30 | 0.56097 | 183.3725
19.0417 | 2018-12-02 17:40 | 0.526 | 180.1089
19.0486 | 2018-12-02 17:50 | 0.56301 | 180.3053
19.0556 | 2018-12-02 18:00 | 0.45705 | 183.8891
19.0625 | 2018-12-02 18:10 | 0.45705 | 183.8891
19.0694 | 2018-12-02 18:20 | 0.31676 | 176.0175
19.0764 | 2018-12-02 18:30 | 0.37677 | 183.6522
19.0833 | 2018-12-02 18:40 | 0.28056 | 162.7922
19.0903 | 2018-12-02 18:50 | 0.18089 | 161.9657
19.0972 | 2018-12-02 19:00 | 0.105 | 160.5297
19.1042 | 2018-12-02 19:10 | 0.105 | 160.5297
19.1111 | 2018-12-02 19:20 | 0.10671 | 79.7432
19.1181 | 2018-12-02 19:30 | 0.16003 | 19.3407
19.125 | 2018-12-02 19:40 | 0.22547 | 28.0426
19.1319 | 2018-12-02 19:50 | 0.2755 | 27.2161
19.1389 | 2018-12-02 20:00 | 0.39195 | 13.5753
19.1458 | 2018-12-02 20:10 | 0.39195 | 13.5753
19.1528 | 2018-12-02 20:20 | 0.52855 | 10.906
19.1597 | 2018-12-02 20:30 | 0.46226 | 10.8481
19.1667 | 2018-12-02 20:40 | 0.46946 | 4.5204
19.1736 | 2018-12-02 20:50 | 0.62999 | 9.1334
19.1806 | 2018-12-02 21:00 | 0.55862 | 5.5473
19.1875 | 2018-12-02 21:10 | 0.55862 | 5.5473
19.1944 | 2018-12-02 21:20 | 0.72217 | 4.4474
19.2014 | 2018-12-02 21:30 | 0.68628 | 5.6026
19.2083 | 2018-12-02 21:40 | 0.74078 | 9.3225
19.2153 | 2018-12-02 21:50 | 0.73206 | 7.3774
19.2222 | 2018-12-02 22:00 | 0.70378 | 7.3472
19.2292 | 2018-12-02 22:10 | 0.70378 | 7.3472
19.2361 | 2018-12-02 22:20 | 0.59549 | 7.0415
19.2431 | 2018-12-02 22:30 | 0.79246 | 1.9525
19.25 | 2018-12-02 22:40 | 0.73986 | 5.0402
19.2569 | 2018-12-02 22:50 | 0.60804 | 359.3404
19.2639 | 2018-12-02 23:00 | 0.62412 | 358.8983
19.2708 | 2018-12-02 23:10 | 0.62412 | 358.8983
19.2778 | 2018-12-02 23:20 | 0.62351 | 10.535
19.2847 | 2018-12-02 23:30 | 0.58032 | 6.133
19.2917 | 2018-12-02 23:40 | 0.57489 | 3.1909
19.2986 | 2018-12-02 23:50 | 0.41041 | 4.752
19.3056 | 2018-12-03 | 0.40106 | 11.5061
19.3125 | 2018-12-03 00:10 | 0.40106 | 11.5061
19.3194 | 2018-12-03 00:20 | 0.38542 | 4.9118
19.3264 | 2018-12-03 00:30 | 0.37764 | 356.6603
19.3333 | 2018-12-03 00:40 | 0.28257 | 7.7286
19.3403 | 2018-12-03 00:50 | 0.24399 | 5.1732
19.3472 | 2018-12-03 01:00 | 0.23509 | 350.6979
19.3542 | 2018-12-03 01:10 | 0.23509 | 350.6979
19.3611 | 2018-12-03 01:20 | 0.13059 | 333.6312
19.3681 | 2018-12-03 01:30 | 0.18174 | 314.3312
19.375 | 2018-12-03 01:40 | 0.032573 | 342.1213
19.3819 | 2018-12-03 01:50 | 0.021213 | 188.1301
19.3889 | 2018-12-03 02:00 | 0.18786 | 215.4668
19.3958 | 2018-12-03 02:10 | 0.18786 | 215.4668
19.4028 | 2018-12-03 02:20 | 0.27412 | 212.1826
19.4097 | 2018-12-03 02:30 | 0.35041 | 216.4121
19.4167 | 2018-12-03 02:40 | 0.44165 | 191.3608
19.4236 | 2018-12-03 02:50 | 0.39023 | 198.5278
19.4306 | 2018-12-03 03:00 | 0.45618 | 190.8665
19.4375 | 2018-12-03 03:10 | 0.45618 | 190.8665
19.4444 | 2018-12-03 03:20 | 0.55057 | 189.5136
19.4514 | 2018-12-03 03:30 | 0.53208 | 185.0677
19.4583 | 2018-12-03 03:40 | 0.55372 | 192.3043
19.4653 | 2018-12-03 03:50 | 0.57267 | 187.3236
19.4722 | 2018-12-03 04:00 | 0.5722 | 183.7075
19.4792 | 2018-12-03 04:10 | 0.5722 | 183.7075
19.4861 | 2018-12-03 04:20 | 0.51994 | 190.64
19.4931 | 2018-12-03 04:30 | 0.60882 | 187.9305
19.5 | 2018-12-03 04:40 | 0.56564 | 182.7359
19.5069 | 2018-12-03 04:50 | 0.59797 | 183.2596
19.5139 | 2018-12-03 05:00 | 0.43604 | 179.2116
19.5208 | 2018-12-03 05:10 | 0.43604 | 179.2116
19.5278 | 2018-12-03 05:20 | 0.44029 | 177.9174
19.5347 | 2018-12-03 05:30 | 0.54388 | 183.2675
19.5417 | 2018-12-03 05:40 | 0.5297 | 189.1245
19.5486 | 2018-12-03 05:50 | 0.53749 | 184.2679
19.5556 | 2018-12-03 06:00 | 0.48948 | 184.4526
19.5625 | 2018-12-03 06:10 | 0.48948 | 184.4526
19.5694 | 2018-12-03 06:20 | 0.30667 | 174.0106
19.5764 | 2018-12-03 06:30 | 0.40401 | 180.4255
19.5833 | 2018-12-03 06:40 | 0.27365 | 172.0179
19.5903 | 2018-12-03 06:50 | 0.32191 | 190.0183
19.5972 | 2018-12-03 07:00 | 0.25739 | 167.2056
19.6042 | 2018-12-03 07:10 | 0.25739 | 167.2056
19.6111 | 2018-12-03 07:20 | 0.050537 | 117.0721
19.6181 | 2018-12-03 07:30 | 0.123 | 115.5234
19.625 | 2018-12-03 07:40 | 0.14012 | 42.6863
19.6319 | 2018-12-03 07:50 | 0.24331 | 27.4076
19.6389 | 2018-12-03 08:00 | 0.30836 | 19.3163
19.6458 | 2018-12-03 08:10 | 0.30836 | 19.3163
19.6528 | 2018-12-03 08:20 | 0.3702 | 12.7974
19.6597 | 2018-12-03 08:30 | 0.47052 | 14.2725
19.6667 | 2018-12-03 08:40 | 0.50348 | 10.5288
19.6736 | 2018-12-03 08:50 | 0.49326 | 1.8588
19.6806 | 2018-12-03 09:00 | 0.61074 | 13.4446
19.6875 | 2018-12-03 09:10 | 0.61074 | 13.4446
19.6944 | 2018-12-03 09:20 | 0.66796 | 7.657
19.7014 | 2018-12-03 09:30 | 0.79209 | 7.1071
19.7083 | 2018-12-03 09:40 | 0.55625 | 6.1923
19.7153 | 2018-12-03 09:50 | 0.80676 | 2.4865
19.7222 | 2018-12-03 10:00 | 0.68309 | 7.6556
19.7292 | 2018-12-03 10:10 | 0.68309 | 7.6556
19.7361 | 2018-12-03 10:20 | 0.77109 | 3.0479
19.7431 | 2018-12-03 10:30 | 0.71988 | 13.4957
19.75 | 2018-12-03 10:40 | 0.70824 | 9.2628
19.7569 | 2018-12-03 10:50 | 0.7569 | 2.8019
19.7639 | 2018-12-03 11:00 | 0.73813 | 6.0659
19.7708 | 2018-12-03 11:10 | 0.73813 | 6.0659
19.7778 | 2018-12-03 11:20 | 0.72567 | 10.7215
19.7847 | 2018-12-03 11:30 | 0.69572 | 7.3497
19.7917 | 2018-12-03 11:40 | 0.60325 | 4.9451
19.7986 | 2018-12-03 11:50 | 0.66747 | 5.8473
19.8056 | 2018-12-03 12:00 | 0.64023 | 10.2568
19.8125 | 2018-12-03 12:10 | 0.64023 | 10.2568
19.8194 | 2018-12-03 12:20 | 0.54379 | 5.8049
19.8264 | 2018-12-03 12:30 | 0.54951 | 6.4784
19.8333 | 2018-12-03 12:40 | 0.4443 | 4.3888
19.8403 | 2018-12-03 12:50 | 0.40512 | 1.4144
19.8472 | 2018-12-03 13:00 | 0.42163 | 5.0345
19.8542 | 2018-12-03 13:10 | 0.42163 | 5.0345
19.8611 | 2018-12-03 13:20 | 0.27563 | 7.9243
19.8681 | 2018-12-03 13:30 | 0.29942 | 7.2912
19.875 | 2018-12-03 13:40 | 0.25035 | 354.0389
19.8819 | 2018-12-03 13:50 | 0.13513 | 2.5448
19.8889 | 2018-12-03 14:00 | 0.13333 | 338.438
19.8958 | 2018-12-03 14:10 | 0.13333 | 338.438
19.9028 | 2018-12-03 14:20 | 0.12474 | 257.9694
19.9097 | 2018-12-03 14:30 | 0.11328 | 222.1376
19.9167 | 2018-12-03 14:40 | 0.36557 | 214.2986
19.9236 | 2018-12-03 14:50 | 0.24958 | 205.641
19.9306 | 2018-12-03 15:00 | 0.41637 | 190.7972
19.9375 | 2018-12-03 15:10 | 0.41637 | 190.7972
19.9444 | 2018-12-03 15:20 | 0.47449 | 195.1492
19.9514 | 2018-12-03 15:30 | 0.47422 | 184.1114
19.9583 | 2018-12-03 15:40 | 0.50515 | 183.8593
19.9653 | 2018-12-03 15:50 | 0.6135 | 187.681
19.9722 | 2018-12-03 16:00 | 0.64265 | 184.1047
19.9792 | 2018-12-03 16:10 | 0.64265 | 184.1047
19.9861 | 2018-12-03 16:20 | 0.69009 | 186.2393
19.9931 | 2018-12-03 16:30 | 0.721 | 183.0211
20 | 2018-12-03 16:40 | 0.76759 | 184.7079
20.0069 | 2018-12-03 16:50 | 0.79518 | 181.225
20.0139 | 2018-12-03 17:00 | 0.93746 | 187.2311
20.0208 | 2018-12-03 17:10 | 0.93746 | 187.2311
20.0278 | 2018-12-03 17:20 | 0.70003 | 186.1504
20.0347 | 2018-12-03 17:30 | 0.86726 | 187.42
20.0417 | 2018-12-03 17:40 | 0.81988 | 186.865
20.0486 | 2018-12-03 17:50 | 0.75082 | 187.7308
20.0556 | 2018-12-03 18:00 | 0.76976 | 187.0142
20.0625 | 2018-12-03 18:10 | 0.76976 | 187.0142
20.0694 | 2018-12-03 18:20 | 0.72804 | 180.6296
20.0764 | 2018-12-03 18:30 | 0.67256 | 189.6724
20.0833 | 2018-12-03 18:40 | 0.57942 | 192.3572
20.0903 | 2018-12-03 18:50 | 0.61634 | 186.8022
20.0972 | 2018-12-03 19:00 | 0.51216 | 178.5455
20.1042 | 2018-12-03 19:10 | 0.51216 | 178.5455
20.1111 | 2018-12-03 19:20 | 0.46157 | 184.7224
20.1181 | 2018-12-03 19:30 | 0.40379 | 174.6
20.125 | 2018-12-03 19:40 | 0.32601 | 179.4727
20.1319 | 2018-12-03 19:50 | 0.2908 | 165.8682
20.1389 | 2018-12-03 20:00 | 0.12768 | 168.25
20.1458 | 2018-12-03 20:10 | 0.12768 | 168.25
20.1528 | 2018-12-03 20:20 | 0.11604 | 128.3513
20.1597 | 2018-12-03 20:30 | 0.11896 | 63.0042
20.1667 | 2018-12-03 20:40 | 0.112 | 37.3815
20.1736 | 2018-12-03 20:50 | 0.23471 | 35.112
20.1806 | 2018-12-03 21:00 | 0.24919 | 7.6098
20.1875 | 2018-12-03 21:10 | 0.24919 | 7.6098
20.1944 | 2018-12-03 21:20 | 0.36844 | 17.6973
20.2014 | 2018-12-03 21:30 | 0.49118 | 13.3006
20.2083 | 2018-12-03 21:40 | 0.49813 | 9.7081
20.2153 | 2018-12-03 21:50 | 0.51859 | 10.4432
20.2222 | 2018-12-03 22:00 | 0.5445 | 12.3005
20.2292 | 2018-12-03 22:10 | 0.5445 | 12.3005
20.2361 | 2018-12-03 22:20 | 0.76208 | 0.82705
20.2431 | 2018-12-03 22:30 | 0.58488 | 356.8636
20.25 | 2018-12-03 22:40 | 0.60472 | 6.3611
20.2569 | 2018-12-03 22:50 | 0.72201 | 359.6826
20.2639 | 2018-12-03 23:00 | 0.77039 | 7.3833
20.2708 | 2018-12-03 23:10 | 0.77039 | 7.3833
20.2778 | 2018-12-03 23:20 | 0.75551 | 7.5295
20.2847 | 2018-12-03 23:30 | 0.69255 | 5.8011
20.2917 | 2018-12-03 23:40 | 0.72845 | 3.6205
20.2986 | 2018-12-03 23:50 | 0.70486 | 8.5669
20.3056 | 2018-12-04 | 0.74782 | 2.6826
20.3125 | 2018-12-04 00:10 | 0.74782 | 2.6826
20.3194 | 2018-12-04 00:20 | 0.5473 | 1.8847
20.3264 | 2018-12-04 00:30 | 0.48636 | 8.5133
20.3333 | 2018-12-04 00:40 | 0.53185 | 5.9357
20.3403 | 2018-12-04 00:50 | 0.47477 | 3.2602
20.3472 | 2018-12-04 01:00 | 0.38542 | 4.9118
20.3542 | 2018-12-04 01:10 | 0.38542 | 4.9118
20.3611 | 2018-12-04 01:20 | 0.28245 | 356.7527
20.3681 | 2018-12-04 01:30 | 0.29482 | 355.7206
20.375 | 2018-12-04 01:40 | 0.21435 | 6.4287
20.3819 | 2018-12-04 01:50 | 0.22314 | 346.5242
20.3889 | 2018-12-04 02:00 | 0.17511 | 346.1225
20.3958 | 2018-12-04 02:10 | 0.17511 | 346.1225
20.4028 | 2018-12-04 02:20 | 0.124 | 0
20.4097 | 2018-12-04 02:30 | 0.052202 | 16.6992
20.4167 | 2018-12-04 02:40 | 0.1319 | 252.8015
20.4236 | 2018-12-04 02:50 | 0.12031 | 207.204
20.4306 | 2018-12-04 03:00 | 0.27965 | 208.3979
20.4375 | 2018-12-04 03:10 | 0.27965 | 208.3979
20.4444 | 2018-12-04 03:20 | 0.28692 | 194.3268
20.4514 | 2018-12-04 03:30 | 0.38617 | 212.4143
20.4583 | 2018-12-04 03:40 | 0.42231 | 202.5573
20.4653 | 2018-12-04 03:50 | 0.46725 | 190.1074
20.4722 | 2018-12-04 04:00 | 0.53733 | 185.3392
20.4792 | 2018-12-04 04:10 | 0.53733 | 185.3392
20.4861 | 2018-12-04 04:20 | 0.51141 | 192.6503
20.4931 | 2018-12-04 04:30 | 0.61477 | 186.3505
20.5 | 2018-12-04 04:40 | 0.53 | 187.0446
20.5069 | 2018-12-04 04:50 | 0.58134 | 181.9715
20.5139 | 2018-12-04 05:00 | 0.66226 | 186.5026
20.5208 | 2018-12-04 05:10 | 0.66226 | 186.5026
20.5278 | 2018-12-04 05:20 | 0.70881 | 185.0993
20.5347 | 2018-12-04 05:30 | 0.70681 | 185.1137
20.5417 | 2018-12-04 05:40 | 0.60532 | 185.023
20.5486 | 2018-12-04 05:50 | 0.77808 | 183.0205
20.5556 | 2018-12-04 06:00 | 0.71201 | 179.6781
20.5625 | 2018-12-04 06:10 | 0.71201 | 179.6781
20.5694 | 2018-12-04 06:20 | 0.60143 | 185.1513
20.5764 | 2018-12-04 06:30 | 0.61213 | 184.7792
20.5833 | 2018-12-04 06:40 | 0.57638 | 182.088
20.5903 | 2018-12-04 06:50 | 0.62826 | 173.3275
20.5972 | 2018-12-04 07:00 | 0.54882 | 183.1335
20.6042 | 2018-12-04 07:10 | 0.54882 | 183.1335
20.6111 | 2018-12-04 07:20 | 0.48402 | 180.4735
20.6181 | 2018-12-04 07:30 | 0.43533 | 177.762
20.625 | 2018-12-04 07:40 | 0.45939 | 177.6296
20.6319 | 2018-12-04 07:50 | 0.36003 | 179.2043
20.6389 | 2018-12-04 08:00 | 0.37501 | 180.4584
20.6458 | 2018-12-04 08:10 | 0.37501 | 180.4584
20.6528 | 2018-12-04 08:20 | 0.24824 | 161.93
20.6597 | 2018-12-04 08:30 | 0.11389 | 163.1562
20.6667 | 2018-12-04 08:40 | 0.10955 | 123.8351
20.6736 | 2018-12-04 08:50 | 0.15135 | 43.9292
20.6806 | 2018-12-04 09:00 | 0.13624 | 35.4399
20.6875 | 2018-12-04 09:10 | 0.13624 | 35.4399
20.6944 | 2018-12-04 09:20 | 0.42474 | 19.2455
20.7014 | 2018-12-04 09:30 | 0.50787 | 18.7204
20.7083 | 2018-12-04 09:40 | 0.57111 | 10.7984
20.7153 | 2018-12-04 09:50 | 0.55738 | 19.9304
20.7222 | 2018-12-04 10:00 | 0.51835 | 2.1006
20.7292 | 2018-12-04 10:10 | 0.51835 | 2.1006
20.7361 | 2018-12-04 10:20 | 0.66454 | 5.0071
20.7431 | 2018-12-04 10:30 | 0.77352 | 9.9007
20.75 | 2018-12-04 10:40 | 0.67807 | 10.3653
20.7569 | 2018-12-04 10:50 | 0.78986 | 5.6673
20.7639 | 2018-12-04 11:00 | 0.86192 | 6.1273
20.7708 | 2018-12-04 11:10 | 0.86192 | 6.1273
20.7778 | 2018-12-04 11:20 | 0.85422 | 9.7049
20.7847 | 2018-12-04 11:30 | 0.71225 | 5.4785
20.7917 | 2018-12-04 11:40 | 0.84861 | 11.6939
20.7986 | 2018-12-04 11:50 | 0.76423 | 13.8544
20.8056 | 2018-12-04 12:00 | 0.7952 | 9.6282
20.8125 | 2018-12-04 12:10 | 0.7952 | 9.6282
20.8194 | 2018-12-04 12:20 | 0.8876 | 9.2713
20.8264 | 2018-12-04 12:30 | 0.80555 | 7.8485
20.8333 | 2018-12-04 12:40 | 0.70807 | 9.6752
20.8403 | 2018-12-04 12:50 | 0.6285 | 15.0312
20.8472 | 2018-12-04 13:00 | 0.63654 | 6.042
20.8542 | 2018-12-04 13:10 | 0.63654 | 6.042
20.8611 | 2018-12-04 13:20 | 0.51394 | 3.4581
20.8681 | 2018-12-04 13:30 | 0.40188 | 6.8598
20.875 | 2018-12-04 13:40 | 0.47574 | 353.846
20.8819 | 2018-12-04 13:50 | 0.3846 | 5.2214
20.8889 | 2018-12-04 14:00 | 0.31815 | 355.1317
20.8958 | 2018-12-04 14:10 | 0.31815 | 355.1317
20.9028 | 2018-12-04 14:20 | 0.32822 | 2.0953
20.9097 | 2018-12-04 14:30 | 0.21908 | 358.4306
20.9167 | 2018-12-04 14:40 | 0.25829 | 348.3855
20.9236 | 2018-12-04 14:50 | 0.10804 | 358.4089
20.9306 | 2018-12-04 15:00 | 0.052431 | 325.0975
20.9375 | 2018-12-04 15:10 | 0.052431 | 325.0975
20.9444 | 2018-12-04 15:20 | 0.16561 | 227.4471
20.9514 | 2018-12-04 15:30 | 0.19244 | 219.7293
20.9583 | 2018-12-04 15:40 | 0.28432 | 197.6065
20.9653 | 2018-12-04 15:50 | 0.33616 | 198.92
20.9722 | 2018-12-04 16:00 | 0.36893 | 193.3206
20.9792 | 2018-12-04 16:10 | 0.36893 | 193.3206
20.9861 | 2018-12-04 16:20 | 0.52362 | 189.1205
20.9931 | 2018-12-04 16:30 | 0.50308 | 176.239
21 | 2018-12-04 16:40 | 0.506 | 185.1022
21.0069 | 2018-12-04 16:50 | 0.54886 | 185.856
21.0139 | 2018-12-04 17:00 | 0.58207 | 180.8859
21.0208 | 2018-12-04 17:10 | 0.58207 | 180.8859
21.0278 | 2018-12-04 17:20 | 0.60333 | 185.0397
21.0347 | 2018-12-04 17:30 | 0.62716 | 184.7561
21.0417 | 2018-12-04 17:40 | 0.68645 | 184.8468
21.0486 | 2018-12-04 17:50 | 0.74592 | 177.1568
21.0556 | 2018-12-04 18:00 | 0.666 | 180.086
21.0625 | 2018-12-04 18:10 | 0.666 | 180.086
21.0694 | 2018-12-04 18:20 | 0.77974 | 183.8239
21.0764 | 2018-12-04 18:30 | 0.76238 | 178.196
21.0833 | 2018-12-04 18:40 | 0.78441 | 183.4351
21.0903 | 2018-12-04 18:50 | 0.64181 | 185.3642
21.0972 | 2018-12-04 19:00 | 0.62732 | 181.827
21.1042 | 2018-12-04 19:10 | 0.62732 | 181.827
21.1111 | 2018-12-04 19:20 | 0.69725 | 184.6067
21.1181 | 2018-12-04 19:30 | 0.546 | 180.2099
21.125 | 2018-12-04 19:40 | 0.57407 | 176.5046
21.1319 | 2018-12-04 19:50 | 0.53165 | 185.7213
21.1389 | 2018-12-04 20:00 | 0.4783 | 177.9632
21.1458 | 2018-12-04 20:10 | 0.4783 | 177.9632
21.1528 | 2018-12-04 20:20 | 0.34875 | 171.5911
21.1597 | 2018-12-04 20:30 | 0.29553 | 185.8263
21.1667 | 2018-12-04 20:40 | 0.27381 | 184.3987
21.1736 | 2018-12-04 20:50 | 0.20839 | 173.3865
21.1806 | 2018-12-04 21:00 | 0.17403 | 180.9878
21.1875 | 2018-12-04 21:10 | 0.17403 | 180.9878
21.1944 | 2018-12-04 21:20 | 0.055902 | 153.435
21.2014 | 2018-12-04 21:30 | 0.13998 | 26.7481
21.2083 | 2018-12-04 21:40 | 0.30528 | 28.9999
21.2153 | 2018-12-04 21:50 | 0.41257 | 20.2797
21.2222 | 2018-12-04 22:00 | 0.48142 | 17.1552
21.2292 | 2018-12-04 22:10 | 0.48142 | 17.1552
21.2361 | 2018-12-04 22:20 | 0.52778 | 18.332
21.2431 | 2018-12-04 22:30 | 0.50403 | 10.8641
21.25 | 2018-12-04 22:40 | 0.61919 | 13.924
21.2569 | 2018-12-04 22:50 | 0.65113 | 1.144
21.2639 | 2018-12-04 23:00 | 0.77349 | 4.5975
21.2708 | 2018-12-04 23:10 | 0.77349 | 4.5975
21.2778 | 2018-12-04 23:20 | 0.8458 | 6.1083
21.2847 | 2018-12-04 23:30 | 0.76314 | 9.3512
21.2917 | 2018-12-04 23:40 | 0.81867 | 10.4864
21.2986 | 2018-12-04 23:50 | 0.84537 | 8.9832
21.3056 | 2018-12-05 | 0.89497 | 10.4938
21.3125 | 2018-12-05 00:10 | 0.89497 | 10.4938
21.3194 | 2018-12-05 00:20 | 0.75835 | 1.738
21.3264 | 2018-12-05 00:30 | 0.76569 | 8.6381
21.3333 | 2018-12-05 00:40 | 0.71018 | 358.709
21.3403 | 2018-12-05 00:50 | 0.78887 | 2.6883
21.3472 | 2018-12-05 01:00 | 0.62293 | 4.5116
21.3542 | 2018-12-05 01:10 | 0.62293 | 4.5116
21.3611 | 2018-12-05 01:20 | 0.58263 | 357.3438
21.3681 | 2018-12-05 01:30 | 0.651 | 3.1701
21.375 | 2018-12-05 01:40 | 0.45428 | 357.9816
21.3819 | 2018-12-05 01:50 | 0.45286 | 10.6896
21.3889 | 2018-12-05 02:00 | 0.42251 | 6.2503
21.3958 | 2018-12-05 02:10 | 0.42251 | 6.2503
21.4028 | 2018-12-05 02:20 | 0.353 | 0
21.4097 | 2018-12-05 02:30 | 0.27002 | 7.0197
21.4167 | 2018-12-05 02:40 | 0.17214 | 2.3305
21.4236 | 2018-12-05 02:50 | 0.22005 | 11.0035
21.4306 | 2018-12-05 03:00 | 0.23342 | 347.631
21.4375 | 2018-12-05 03:10 | 0.23342 | 347.631
21.4444 | 2018-12-05 03:20 | 0.076942 | 8.9726
21.4514 | 2018-12-05 03:30 | 0.07311 | 229.9937
21.4583 | 2018-12-05 03:40 | 0.18065 | 215.5377
21.4653 | 2018-12-05 03:50 | 0.21185 | 209.7113
21.4722 | 2018-12-05 04:00 | 0.31988 | 200.3045
21.4792 | 2018-12-05 04:10 | 0.31988 | 200.3045
21.4861 | 2018-12-05 04:20 | 0.47885 | 188.1639
21.4931 | 2018-12-05 04:30 | 0.4859 | 186.2621
21.5 | 2018-12-05 04:40 | 0.53714 | 186.1988
21.5069 | 2018-12-05 04:50 | 0.57807 | 180.8921
21.5139 | 2018-12-05 05:00 | 0.64636 | 194.0577
21.5208 | 2018-12-05 05:10 | 0.64636 | 194.0577
21.5278 | 2018-12-05 05:20 | 0.64729 | 187.9924
21.5347 | 2018-12-05 05:30 | 0.51241 | 175.7471
21.5417 | 2018-12-05 05:40 | 0.70051 | 185.735
21.5486 | 2018-12-05 05:50 | 0.72341 | 184.6781
21.5556 | 2018-12-05 06:00 | 0.72195 | 182.9377
21.5625 | 2018-12-05 06:10 | 0.72195 | 182.9377
21.5694 | 2018-12-05 06:20 | 0.67006 | 179.2304
21.5764 | 2018-12-05 06:30 | 0.78308 | 180.8049
21.5833 | 2018-12-05 06:40 | 0.67701 | 179.6615
21.5903 | 2018-12-05 06:50 | 0.74611 | 179.0016
21.5972 | 2018-12-05 07:00 | 0.52691 | 183.3728
21.6042 | 2018-12-05 07:10 | 0.52691 | 183.3728
21.6111 | 2018-12-05 07:20 | 0.55133 | 178.0251
21.6181 | 2018-12-05 07:30 | 0.59561 | 177.4018
21.625 | 2018-12-05 07:40 | 0.62021 | 181.4783
21.6319 | 2018-12-05 07:50 | 0.53002 | 180.4324
21.6389 | 2018-12-05 08:00 | 0.58651 | 175.8935
21.6458 | 2018-12-05 08:10 | 0.58651 | 175.8935
21.6528 | 2018-12-05 08:20 | 0.50375 | 172.1273
21.6597 | 2018-12-05 08:30 | 0.40972 | 171.2964
21.6667 | 2018-12-05 08:40 | 0.29851 | 168.0125
21.6736 | 2018-12-05 08:50 | 0.27464 | 172.0469
21.6806 | 2018-12-05 09:00 | 0.23261 | 165.3066
21.6875 | 2018-12-05 09:10 | 0.23261 | 165.3066
21.6944 | 2018-12-05 09:20 | 0.16832 | 134.0371
21.7014 | 2018-12-05 09:30 | 0.17614 | 83.4802
21.7083 | 2018-12-05 09:40 | 0.09626 | 42.4739
21.7153 | 2018-12-05 09:50 | 0.27337 | 24.8776
21.7222 | 2018-12-05 10:00 | 0.32088 | 16.2888
21.7292 | 2018-12-05 10:10 | 0.32088 | 16.2888
21.7361 | 2018-12-05 10:20 | 0.52315 | 22.5946
21.7431 | 2018-12-05 10:30 | 0.47565 | 14.7374
21.75 | 2018-12-05 10:40 | 0.6325 | 11.8607
21.7569 | 2018-12-05 10:50 | 0.68039 | 4.8056
21.7639 | 2018-12-05 11:00 | 0.65956 | 5.045
21.7708 | 2018-12-05 11:10 | 0.65956 | 5.045
21.7778 | 2018-12-05 11:20 | 0.99406 | 4.5004
21.7847 | 2018-12-05 11:30 | 0.95894 | 9.423
21.7917 | 2018-12-05 11:40 | 0.91484 | 4.514
21.7986 | 2018-12-05 11:50 | 1.0132 | 5.2098
21.8056 | 2018-12-05 12:00 | 1.0426 | 9.2726
21.8125 | 2018-12-05 12:10 | 1.0426 | 9.2726
21.8194 | 2018-12-05 12:20 | 0.92894 | 3.7033
21.8264 | 2018-12-05 12:30 | 0.98639 | 5.9938
21.8333 | 2018-12-05 12:40 | 0.86285 | 10.2811
21.8403 | 2018-12-05 12:50 | 0.86918 | 7.8691
21.8472 | 2018-12-05 13:00 | 0.70602 | 14.0166
21.8542 | 2018-12-05 13:10 | 0.70602 | 14.0166
21.8611 | 2018-12-05 13:20 | 0.81278 | 6.2156
21.8681 | 2018-12-05 13:30 | 0.79483 | 7.5184
21.875 | 2018-12-05 13:40 | 0.67649 | 4.9184
21.8819 | 2018-12-05 13:50 | 0.69848 | 6.4942
21.8889 | 2018-12-05 14:00 | 0.71007 | 0.80693
21.8958 | 2018-12-05 14:10 | 0.71007 | 0.80693
21.9028 | 2018-12-05 14:20 | 0.60665 | 7.1016
21.9097 | 2018-12-05 14:30 | 0.54811 | 1.1499
21.9167 | 2018-12-05 14:40 | 0.49819 | 12.167
21.9236 | 2018-12-05 14:50 | 0.39501 | 359.7099
21.9306 | 2018-12-05 15:00 | 0.38422 | 1.939
21.9375 | 2018-12-05 15:10 | 0.38422 | 1.939
21.9444 | 2018-12-05 15:20 | 0.22441 | 349.992
21.9514 | 2018-12-05 15:30 | 0.25068 | 353.3569
21.9583 | 2018-12-05 15:40 | 0.12856 | 354.6442
21.9653 | 2018-12-05 15:50 | 0.16515 | 2.4293
21.9722 | 2018-12-05 16:00 | 0.13288 | 325.114
21.9792 | 2018-12-05 16:10 | 0.13288 | 325.114
21.9861 | 2018-12-05 16:20 | 0.20182 | 196.9984
21.9931 | 2018-12-05 16:30 | 0.21151 | 201.3487
22 | 2018-12-05 16:40 | 0.34379 | 191.408
22.0069 | 2018-12-05 16:50 | 0.38252 | 182.997
22.0139 | 2018-12-05 17:00 | 0.45213 | 187.7538
22.0208 | 2018-12-05 17:10 | 0.45213 | 187.7538
22.0278 | 2018-12-05 17:20 | 0.46491 | 183.5763
22.0347 | 2018-12-05 17:30 | 0.53537 | 182.1409
22.0417 | 2018-12-05 17:40 | 0.53573 | 184.6038
22.0486 | 2018-12-05 17:50 | 0.62393 | 183.1238
22.0556 | 2018-12-05 18:00 | 0.71459 | 182.3259
22.0625 | 2018-12-05 18:10 | 0.71459 | 182.3259
22.0694 | 2018-12-05 18:20 | 0.61568 | 177.3002
22.0764 | 2018-12-05 18:30 | 0.73701 | 179.7668
22.0833 | 2018-12-05 18:40 | 0.65437 | 181.9267
22.0903 | 2018-12-05 18:50 | 0.65167 | 188.2047
22.0972 | 2018-12-05 19:00 | 0.76055 | 177.8148
22.1042 | 2018-12-05 19:10 | 0.76055 | 177.8148
22.1111 | 2018-12-05 19:20 | 0.66617 | 181.2902
22.1181 | 2018-12-05 19:30 | 0.68729 | 184.6736
22.125 | 2018-12-05 19:40 | 0.65029 | 176.3852
22.1319 | 2018-12-05 19:50 | 0.56911 | 178.8925
22.1389 | 2018-12-05 20:00 | 0.56513 | 178.7833
22.1458 | 2018-12-05 20:10 | 0.56513 | 178.7833
22.1528 | 2018-12-05 20:20 | 0.55902 | 179.4875
22.1597 | 2018-12-05 20:30 | 0.53076 | 188.4507
22.1667 | 2018-12-05 20:40 | 0.54923 | 178.3306
22.1736 | 2018-12-05 20:50 | 0.44251 | 188.185
22.1806 | 2018-12-05 21:00 | 0.42109 | 168.0763
22.1875 | 2018-12-05 21:10 | 0.42109 | 168.0763
22.1944 | 2018-12-05 21:20 | 0.29362 | 176.2898
22.2014 | 2018-12-05 21:30 | 0.21829 | 159.9048
22.2083 | 2018-12-05 21:40 | 0.21991 | 174.782
22.2153 | 2018-12-05 21:50 | 0.16847 | 156.9354
22.2222 | 2018-12-05 22:00 | 0.13471 | 108.166
22.2292 | 2018-12-05 22:10 | 0.13471 | 108.166
22.2361 | 2018-12-05 22:20 | 0.32827 | 23.5194
22.2431 | 2018-12-05 22:30 | 0.40576 | 33.8467
22.25 | 2018-12-05 22:40 | 0.44737 | 23.5854
22.2569 | 2018-12-05 22:50 | 0.55995 | 16.8168
22.2639 | 2018-12-05 23:00 | 0.51202 | 13.4391
22.2708 | 2018-12-05 23:10 | 0.51202 | 13.4391
22.2778 | 2018-12-05 23:20 | 0.57491 | 7.4959
22.2847 | 2018-12-05 23:30 | 0.50906 | 359.0995
22.2917 | 2018-12-05 23:40 | 0.71011 | 6.8748
22.2986 | 2018-12-05 23:50 | 0.73814 | 5.2858
22.3056 | 2018-12-06 | 0.88847 | 8.805
22.3125 | 2018-12-06 00:10 | 0.88847 | 8.805
22.3194 | 2018-12-06 00:20 | 0.6419 | 5.453
22.3264 | 2018-12-06 00:30 | 0.74619 | 6.0773
22.3333 | 2018-12-06 00:40 | 0.90652 | 9.9091
22.3403 | 2018-12-06 00:50 | 0.79531 | 7.2233
22.3472 | 2018-12-06 01:00 | 0.74954 | 6.9733
22.3542 | 2018-12-06 01:10 | 0.74954 | 6.9733
22.3611 | 2018-12-06 01:20 | 0.74974 | 3.9005
22.3681 | 2018-12-06 01:30 | 0.72976 | 5.82
22.375 | 2018-12-06 01:40 | 0.77231 | 3.3403
22.3819 | 2018-12-06 01:50 | 0.74098 | 8.9284
22.3889 | 2018-12-06 02:00 | 0.6617 | 11.242
22.3958 | 2018-12-06 02:10 | 0.6617 | 11.242
22.4028 | 2018-12-06 02:20 | 0.67792 | 4.3144
22.4097 | 2018-12-06 02:30 | 0.50521 | 8.9962
22.4167 | 2018-12-06 02:40 | 0.39126 | 11.0515
22.4236 | 2018-12-06 02:50 | 0.50502 | 8.082
22.4306 | 2018-12-06 03:00 | 0.36155 | 356.8289
22.4375 | 2018-12-06 03:10 | 0.36155 | 356.8289
22.4444 | 2018-12-06 03:20 | 0.34406 | 4.5009
22.4514 | 2018-12-06 03:30 | 0.3264 | 351.7209
22.4583 | 2018-12-06 03:40 | 0.28284 | 351.8699
22.4653 | 2018-12-06 03:50 | 0.24792 | 18.5811
22.4722 | 2018-12-06 04:00 | 0.20344 | 343.4356
22.4792 | 2018-12-06 04:10 | 0.20344 | 343.4356
22.4861 | 2018-12-06 04:20 | 0.061294 | 208.2374
22.4931 | 2018-12-06 04:30 | 0.22731 | 201.1461
22.5 | 2018-12-06 04:40 | 0.29349 | 199.2993
22.5069 | 2018-12-06 04:50 | 0.34707 | 201.4642
22.5139 | 2018-12-06 05:00 | 0.41239 | 192.8905
22.5208 | 2018-12-06 05:10 | 0.41239 | 192.8905
22.5278 | 2018-12-06 05:20 | 0.49526 | 192.2402
22.5347 | 2018-12-06 05:30 | 0.49116 | 188.3116
22.5417 | 2018-12-06 05:40 | 0.56189 | 184.6959
22.5486 | 2018-12-06 05:50 | 0.53609 | 178.9312
22.5556 | 2018-12-06 06:00 | 0.68047 | 189.047
22.5625 | 2018-12-06 06:10 | 0.68047 | 189.047
22.5694 | 2018-12-06 06:20 | 0.75241 | 187.4839
22.5764 | 2018-12-06 06:30 | 0.79264 | 183.6891
22.5833 | 2018-12-06 06:40 | 0.69429 | 188.8654
22.5903 | 2018-12-06 06:50 | 0.7181 | 180.9575
22.5972 | 2018-12-06 07:00 | 0.82874 | 182.4205
22.6042 | 2018-12-06 07:10 | 0.82874 | 182.4205
22.6111 | 2018-12-06 07:20 | 0.68349 | 177.82
22.6181 | 2018-12-06 07:30 | 0.73493 | 182.8858
22.625 | 2018-12-06 07:40 | 0.80011 | 180.931
22.6319 | 2018-12-06 07:50 | 0.77666 | 182.3614
22.6389 | 2018-12-06 08:00 | 0.81201 | 180.2117
22.6458 | 2018-12-06 08:10 | 0.81201 | 180.2117
22.6528 | 2018-12-06 08:20 | 0.69189 | 182.8996
22.6597 | 2018-12-06 08:30 | 0.65501 | 179.6501
22.6667 | 2018-12-06 08:40 | 0.60701 | 179.6224
22.6736 | 2018-12-06 08:50 | 0.55661 | 177.3226
22.6806 | 2018-12-06 09:00 | 0.56626 | 181.7204
22.6875 | 2018-12-06 09:10 | 0.56626 | 181.7204
22.6944 | 2018-12-06 09:20 | 0.46878 | 176.6981
22.7014 | 2018-12-06 09:30 | 0.30624 | 177.7543
22.7083 | 2018-12-06 09:40 | 0.4137 | 183.3258
22.7153 | 2018-12-06 09:50 | 0.24507 | 178.5971
22.7222 | 2018-12-06 10:00 | 0.19719 | 165.6114
22.7292 | 2018-12-06 10:10 | 0.19719 | 165.6114
22.7361 | 2018-12-06 10:20 | 0.070937 | 49.5739
22.7431 | 2018-12-06 10:30 | 0.15778 | 30.4656
22.75 | 2018-12-06 10:40 | 0.33465 | 29.936
22.7569 | 2018-12-06 10:50 | 0.41411 | 20.054
22.7639 | 2018-12-06 11:00 | 0.55899 | 16.8465
22.7708 | 2018-12-06 11:10 | 0.55899 | 16.8465
22.7778 | 2018-12-06 11:20 | 0.57137 | 5.2217
22.7847 | 2018-12-06 11:30 | 0.61702 | 8.0119
22.7917 | 2018-12-06 11:40 | 0.76644 | 1.944
22.7986 | 2018-12-06 11:50 | 0.86435 | 6.3768
22.8056 | 2018-12-06 12:00 | 0.74793 | 7.22
22.8125 | 2018-12-06 12:10 | 0.74793 | 7.22
22.8194 | 2018-12-06 12:20 | 0.80125 | 1.4303
22.8264 | 2018-12-06 12:30 | 0.83379 | 10.4339
22.8333 | 2018-12-06 12:40 | 0.74177 | 9.3099
22.8403 | 2018-12-06 12:50 | 0.98993 | 2.4896
22.8472 | 2018-12-06 13:00 | 0.9664 | 8.8093
22.8542 | 2018-12-06 13:10 | 0.9664 | 8.8093
22.8611 | 2018-12-06 13:20 | 0.91159 | 9.5347
22.8681 | 2018-12-06 13:30 | 0.72392 | 5.1514
22.875 | 2018-12-06 13:40 | 0.88092 | 5.4064
22.8819 | 2018-12-06 13:50 | 0.78725 | 1.4557
22.8889 | 2018-12-06 14:00 | 0.84144 | 4.3621
22.8958 | 2018-12-06 14:10 | 0.84144 | 4.3621
22.9028 | 2018-12-06 14:20 | 0.71762 | 10.7619
22.9097 | 2018-12-06 14:30 | 0.72477 | 6.5759
22.9167 | 2018-12-06 14:40 | 0.62203 | 0.55268
22.9236 | 2018-12-06 14:50 | 0.61087 | 7.2414
22.9306 | 2018-12-06 15:00 | 0.53668 | 2.8837
22.9375 | 2018-12-06 15:10 | 0.53668 | 2.8837
22.9444 | 2018-12-06 15:20 | 0.42694 | 6.7255
22.9514 | 2018-12-06 15:30 | 0.53416 | 354.8444
22.9583 | 2018-12-06 15:40 | 0.40717 | 5.9206
22.9653 | 2018-12-06 15:50 | 0.37496 | 13.888
22.9722 | 2018-12-06 16:00 | 0.37326 | 353.6937
22.9792 | 2018-12-06 16:10 | 0.37326 | 353.6937
22.9861 | 2018-12-06 16:20 | 0.24353 | 13.2944
22.9931 | 2018-12-06 16:30 | 0.12233 | 355.7809
23 | 2018-12-06 16:40 | 0.060828 | 260.5377
23.0069 | 2018-12-06 16:50 | 0.042485 | 243.435
23.0139 | 2018-12-06 17:00 | 0.13014 | 206.9588
23.0208 | 2018-12-06 17:10 | 0.13014 | 206.9588
23.0278 | 2018-12-06 17:20 | 0.34531 | 184.9841
23.0347 | 2018-12-06 17:30 | 0.38305 | 189.3148
23.0417 | 2018-12-06 17:40 | 0.45437 | 192.8434
23.0486 | 2018-12-06 17:50 | 0.50854 | 191.6856
23.0556 | 2018-12-06 18:00 | 0.61066 | 184.226
23.0625 | 2018-12-06 18:10 | 0.61066 | 184.226
23.0694 | 2018-12-06 18:20 | 0.55107 | 189.1888
23.0764 | 2018-12-06 18:30 | 0.67476 | 182.7182
23.0833 | 2018-12-06 18:40 | 0.74908 | 180.8414
23.0903 | 2018-12-06 18:50 | 0.78859 | 186.1877
23.0972 | 2018-12-06 19:00 | 0.725 | 179.921
23.1042 | 2018-12-06 19:10 | 0.725 | 179.921
23.1111 | 2018-12-06 19:20 | 0.72211 | 183.1754
23.1181 | 2018-12-06 19:30 | 0.77391 | 184.9665
23.125 | 2018-12-06 19:40 | 0.78709 | 180.8736
23.1319 | 2018-12-06 19:50 | 0.71155 | 183.7873
23.1389 | 2018-12-06 20:00 | 0.72633 | 178.2643
23.1458 | 2018-12-06 20:10 | 0.72633 | 178.2643
23.1528 | 2018-12-06 20:20 | 0.77774 | 183.8337
23.1597 | 2018-12-06 20:30 | 0.82603 | 180.4855
23.1667 | 2018-12-06 20:40 | 0.71169 | 183.948
23.1736 | 2018-12-06 20:50 | 0.63642 | 182.0711
23.1806 | 2018-12-06 21:00 | 0.56 | 179.7954
23.1875 | 2018-12-06 21:10 | 0.56 | 179.7954
23.1944 | 2018-12-06 21:20 | 0.57135 | 182.006
23.2014 | 2018-12-06 21:30 | 0.50502 | 180.5673
23.2083 | 2018-12-06 21:40 | 0.45205 | 185.4584
23.2153 | 2018-12-06 21:50 | 0.45 | 180
23.2222 | 2018-12-06 22:00 | 0.29125 | 177.6386
23.2292 | 2018-12-06 22:10 | 0.29125 | 177.6386
23.2361 | 2018-12-06 22:20 | 0.20432 | 162.6292
23.2431 | 2018-12-06 22:30 | 0.11513 | 162.8241
23.25 | 2018-12-06 22:40 | 0.032249 | 330.2551
23.2569 | 2018-12-06 22:50 | 0.15086 | 38.5412
23.2639 | 2018-12-06 23:00 | 0.278 | 23.9834
23.2708 | 2018-12-06 23:10 | 0.278 | 23.9834
23.2778 | 2018-12-06 23:20 | 0.4703 | 14.6568
23.2847 | 2018-12-06 23:30 | 0.465 | 8.4089
23.2917 | 2018-12-06 23:40 | 0.45888 | 25.8391
23.2986 | 2018-12-06 23:50 | 0.5071 | 6.3402
23.3056 | 2018-12-07 | 0.60253 | 9.6499
23.3125 | 2018-12-07 00:10 | 0.60253 | 9.6499
23.3194 | 2018-12-07 00:20 | 0.69807 | 6.9112
23.3264 | 2018-12-07 00:30 | 0.70844 | 8.8507
23.3333 | 2018-12-07 00:40 | 0.87019 | 11.7361
23.3403 | 2018-12-07 00:50 | 0.79388 | 9.4979
23.3472 | 2018-12-07 01:00 | 0.80179 | 9.8383
23.3542 | 2018-12-07 01:10 | 0.80179 | 9.8383
23.3611 | 2018-12-07 01:20 | 0.7672 | 5.235
23.3681 | 2018-12-07 01:30 | 0.82812 | 0.96868
23.375 | 2018-12-07 01:40 | 0.69156 | 7.8958
23.3819 | 2018-12-07 01:50 | 0.81592 | 3.9355
23.3889 | 2018-12-07 02:00 | 0.82427 | 1.4599
23.3958 | 2018-12-07 02:10 | 0.82427 | 1.4599
23.4028 | 2018-12-07 02:20 | 0.76023 | 6.723
23.4097 | 2018-12-07 02:30 | 0.74308 | 9.4496
23.4167 | 2018-12-07 02:40 | 0.62566 | 7.7157
23.4236 | 2018-12-07 02:50 | 0.47077 | 6.2192
23.4306 | 2018-12-07 03:00 | 0.65324 | 8.5394
23.4375 | 2018-12-07 03:10 | 0.65324 | 8.5394
23.4444 | 2018-12-07 03:20 | 0.52977 | 8.4666
23.4514 | 2018-12-07 03:30 | 0.44472 | 9.9707
23.4583 | 2018-12-07 03:40 | 0.4031 | 1.2793
23.4653 | 2018-12-07 03:50 | 0.32422 | 2.1211
23.4722 | 2018-12-07 04:00 | 0.25691 | 11.2225
23.4792 | 2018-12-07 04:10 | 0.25691 | 11.2225
23.4861 | 2018-12-07 04:20 | 0.25886 | 6.8779
23.4931 | 2018-12-07 04:30 | 0.18304 | 358.7478
23.5 | 2018-12-07 04:40 | 0.11249 | 316.8011
23.5069 | 2018-12-07 04:50 | 0.087818 | 329.9314
23.5139 | 2018-12-07 05:00 | 0.14436 | 227.2457
23.5208 | 2018-12-07 05:10 | 0.14436 | 227.2457
23.5278 | 2018-12-07 05:20 | 0.34072 | 200.0837
23.5347 | 2018-12-07 05:30 | 0.39688 | 192.8107
23.5417 | 2018-12-07 05:40 | 0.4066 | 196.4293
23.5486 | 2018-12-07 05:50 | 0.4361 | 193.5264
23.5556 | 2018-12-07 06:00 | 0.50522 | 194.5589
23.5625 | 2018-12-07 06:10 | 0.50522 | 194.5589
23.5694 | 2018-12-07 06:20 | 0.61949 | 190.0401
23.5764 | 2018-12-07 06:30 | 0.50673 | 188.6258
23.5833 | 2018-12-07 06:40 | 0.61391 | 187.9585
23.5903 | 2018-12-07 06:50 | 0.51563 | 185.788
23.5972 | 2018-12-07 07:00 | 0.68411 | 181.0051
23.6042 | 2018-12-07 07:10 | 0.68411 | 181.0051
23.6111 | 2018-12-07 07:20 | 0.78602 | 179.6355
23.6181 | 2018-12-07 07:30 | 0.64119 | 184.7414
23.625 | 2018-12-07 07:40 | 0.75634 | 185.3865
23.6319 | 2018-12-07 07:50 | 0.80568 | 182.3475
23.6389 | 2018-12-07 08:00 | 0.66795 | 184.379
23.6458 | 2018-12-07 08:10 | 0.66795 | 184.379
23.6528 | 2018-12-07 08:20 | 0.65713 | 178.8664
23.6597 | 2018-12-07 08:30 | 0.70725 | 183.4045
23.6667 | 2018-12-07 08:40 | 0.62516 | 181.2832
23.6736 | 2018-12-07 08:50 | 0.55039 | 186.3632
23.6806 | 2018-12-07 09:00 | 0.60001 | 180.382
23.6875 | 2018-12-07 09:10 | 0.60001 | 180.382
23.6944 | 2018-12-07 09:20 | 0.50701 | 183.6186
23.7014 | 2018-12-07 09:30 | 0.506 | 180
23.7083 | 2018-12-07 09:40 | 0.42612 | 178.6553
23.7153 | 2018-12-07 09:50 | 0.30508 | 178.6852
23.7222 | 2018-12-07 10:00 | 0.40287 | 173.1572
23.7292 | 2018-12-07 10:10 | 0.40287 | 173.1572
23.7361 | 2018-12-07 10:20 | 0.16574 | 167.8087
23.7431 | 2018-12-07 10:30 | 0.14677 | 151.5142
23.75 | 2018-12-07 10:40 | 0.056462 | 67.0679
23.7569 | 2018-12-07 10:50 | 0.14183 | 58.5513
23.7639 | 2018-12-07 11:00 | 0.23865 | 29.3577
23.7708 | 2018-12-07 11:10 | 0.23865 | 29.3577
23.7778 | 2018-12-07 11:20 | 0.4085 | 23.3643
23.7847 | 2018-12-07 11:30 | 0.49601 | 15.9137
23.7917 | 2018-12-07 11:40 | 0.58718 | 5.963
23.7986 | 2018-12-07 11:50 | 0.47838 | 2.2762
23.8056 | 2018-12-07 12:00 | 0.57689 | 3.1798
23.8125 | 2018-12-07 12:10 | 0.57689 | 3.1798
23.8194 | 2018-12-07 12:20 | 0.83257 | 7.7311
23.8264 | 2018-12-07 12:30 | 0.85054 | 7.6347
23.8333 | 2018-12-07 12:40 | 0.8392 | 8.0142
23.8403 | 2018-12-07 12:50 | 0.82251 | 11.146
23.8472 | 2018-12-07 13:00 | 0.88101 | 5.4712
23.8542 | 2018-12-07 13:10 | 0.88101 | 5.4712
23.8611 | 2018-12-07 13:20 | 0.74971 | 10.1408
23.8681 | 2018-12-07 13:30 | 0.85498 | 7.3245
23.875 | 2018-12-07 13:40 | 0.86363 | 2.1898
23.8819 | 2018-12-07 13:50 | 0.83667 | 10.7459
23.8889 | 2018-12-07 14:00 | 0.86525 | 1.3907
23.8958 | 2018-12-07 14:10 | 0.86525 | 1.3907
23.9028 | 2018-12-07 14:20 | 0.92504 | 8.0162
23.9097 | 2018-12-07 14:30 | 0.86006 | 7.3481
23.9167 | 2018-12-07 14:40 | 0.60416 | 1.3278
23.9236 | 2018-12-07 14:50 | 0.70725 | 3.4045
23.9306 | 2018-12-07 15:00 | 0.7301 | 9.5397
23.9375 | 2018-12-07 15:10 | 0.7301 | 9.5397
23.9444 | 2018-12-07 15:20 | 0.55906 | 0.81992
23.9514 | 2018-12-07 15:30 | 0.72823 | 4.4892
23.9583 | 2018-12-07 15:40 | 0.66202 | 0.43274
23.9653 | 2018-12-07 15:50 | 0.49068 | 348.5985
23.9722 | 2018-12-07 16:00 | 0.48108 | 358.9281
23.9792 | 2018-12-07 16:10 | 0.48108 | 358.9281
23.9861 | 2018-12-07 16:20 | 0.39736 | 2.452
23.9931 | 2018-12-07 16:30 | 0.24622 | 7.7023
24 | 2018-12-07 16:40 | 0.2075 | 348.0403
24.0069 | 2018-12-07 16:50 | 0.25707 | 358.6626
24.0139 | 2018-12-07 17:00 | 0.17511 | 346.1225
24.0208 | 2018-12-07 17:10 | 0.17511 | 346.1225
24.0278 | 2018-12-07 17:20 | 0.097745 | 311.6822
24.0347 | 2018-12-07 17:30 | 0.15532 | 220.5613
24.0417 | 2018-12-07 17:40 | 0.2444 | 216.6824
24.0486 | 2018-12-07 17:50 | 0.35805 | 215.9097
24.0556 | 2018-12-07 18:00 | 0.42521 | 191.9442
24.0625 | 2018-12-07 18:10 | 0.42521 | 191.9442
24.0694 | 2018-12-07 18:20 | 0.43108 | 202.9368
24.0764 | 2018-12-07 18:30 | 0.49834 | 191.6933
24.0833 | 2018-12-07 18:40 | 0.5643 | 190.4138
24.0903 | 2018-12-07 18:50 | 0.58052 | 190.9228
24.0972 | 2018-12-07 19:00 | 0.6126 | 182.5261
24.1042 | 2018-12-07 19:10 | 0.6126 | 182.5261
24.1111 | 2018-12-07 19:20 | 0.70251 | 183.7544
24.1181 | 2018-12-07 19:30 | 0.67699 | 191.2435
24.125 | 2018-12-07 19:40 | 0.73593 | 185.9275
24.1319 | 2018-12-07 19:50 | 0.71612 | 183.202
24.1389 | 2018-12-07 20:00 | 0.71948 | 193.0125
24.1458 | 2018-12-07 20:10 | 0.71948 | 193.0125
24.1528 | 2018-12-07 20:20 | 0.68633 | 186.4416
24.1597 | 2018-12-07 20:30 | 0.67972 | 185.9958
24.1667 | 2018-12-07 20:40 | 0.70216 | 184.4926
24.1736 | 2018-12-07 20:50 | 0.65968 | 182.6065
24.1806 | 2018-12-07 21:00 | 0.66952 | 184.9697
24.1875 | 2018-12-07 21:10 | 0.66952 | 184.9697
24.1944 | 2018-12-07 21:20 | 0.62826 | 178.3582
24.2014 | 2018-12-07 21:30 | 0.68453 | 192.2292
24.2083 | 2018-12-07 21:40 | 0.5216 | 177.2528
24.2153 | 2018-12-07 21:50 | 0.4827 | 186.0649
24.2222 | 2018-12-07 22:00 | 0.43904 | 180.783
24.2292 | 2018-12-07 22:10 | 0.43904 | 180.783
24.2361 | 2018-12-07 22:20 | 0.34929 | 193.2405
24.2431 | 2018-12-07 22:30 | 0.30654 | 190.9067
24.25 | 2018-12-07 22:40 | 0.26347 | 172.1467
24.2569 | 2018-12-07 22:50 | 0.19144 | 176.1063
24.2639 | 2018-12-07 23:00 | 0.10279 | 162.4465
24.2708 | 2018-12-07 23:10 | 0.10279 | 162.4465
24.2778 | 2018-12-07 23:20 | 0.15275 | 39.4214
24.2847 | 2018-12-07 23:30 | 0.22309 | 23.2323
24.2917 | 2018-12-07 23:40 | 0.341 | 0
24.2986 | 2018-12-07 23:50 | 0.42571 | 6.474
24.3056 | 2018-12-08 | 0.47123 | 4.1376
24.3125 | 2018-12-08 00:10 | 0.47123 | 4.1376
24.3194 | 2018-12-08 00:20 | 0.54406 | 3.5829
24.3264 | 2018-12-08 00:30 | 0.72985 | 10.3399
24.3333 | 2018-12-08 00:40 | 0.82919 | 10.9847
24.3403 | 2018-12-08 00:50 | 0.75603 | 5.9217
24.3472 | 2018-12-08 01:00 | 0.74038 | 7.5282
24.3542 | 2018-12-08 01:10 | 0.74038 | 7.5282
24.3611 | 2018-12-08 01:20 | 0.89629 | 6.792
24.3681 | 2018-12-08 01:30 | 0.90849 | 9.8874
24.375 | 2018-12-08 01:40 | 0.82844 | 9.9399
24.3819 | 2018-12-08 01:50 | 0.77273 | 8.1091
24.3889 | 2018-12-08 02:00 | 0.8801 | 2.8657
24.3958 | 2018-12-08 02:10 | 0.8801 | 2.8657
24.4028 | 2018-12-08 02:20 | 0.88865 | 2.1927
24.4097 | 2018-12-08 02:30 | 0.89605 | 8.1482
24.4167 | 2018-12-08 02:40 | 0.66958 | 10.6722
24.4236 | 2018-12-08 02:50 | 0.87627 | 4.1229
24.4306 | 2018-12-08 03:00 | 0.68707 | 8.7905
24.4375 | 2018-12-08 03:10 | 0.68707 | 8.7905
24.4444 | 2018-12-08 03:20 | 0.7571 | 0.90818
24.4514 | 2018-12-08 03:30 | 0.66221 | 4.6774
24.4583 | 2018-12-08 03:40 | 0.69712 | 10.246
24.4653 | 2018-12-08 03:50 | 0.60725 | 356.3177
24.4722 | 2018-12-08 04:00 | 0.54134 | 6.3636
24.4792 | 2018-12-08 04:10 | 0.54134 | 6.3636
24.4861 | 2018-12-08 04:20 | 0.42557 | 357.0367
24.4931 | 2018-12-08 04:30 | 0.41024 | 358.0443
24.5 | 2018-12-08 04:40 | 0.35075 | 5.7268
24.5069 | 2018-12-08 04:50 | 0.32646 | 7.0379
24.5139 | 2018-12-08 05:00 | 0.24167 | 355.7286
24.5208 | 2018-12-08 05:10 | 0.24167 | 355.7286
24.5278 | 2018-12-08 05:20 | 0.19176 | 343.6442
24.5347 | 2018-12-08 05:30 | 0.11819 | 302.2109
24.5417 | 2018-12-08 05:40 | 0.051884 | 242.4472
24.5486 | 2018-12-08 05:50 | 0.19948 | 230.0841
24.5556 | 2018-12-08 06:00 | 0.23618 | 207.7585
24.5625 | 2018-12-08 06:10 | 0.23618 | 207.7585
24.5694 | 2018-12-08 06:20 | 0.41982 | 196.7515
24.5764 | 2018-12-08 06:30 | 0.38601 | 196.5571
24.5833 | 2018-12-08 06:40 | 0.432 | 196.1276
24.5903 | 2018-12-08 06:50 | 0.47959 | 196.848
24.5972 | 2018-12-08 07:00 | 0.56913 | 191.3494
24.6042 | 2018-12-08 07:10 | 0.56913 | 191.3494
24.6111 | 2018-12-08 07:20 | 0.64602 | 187.8291
24.6181 | 2018-12-08 07:30 | 0.75753 | 185.53
24.625 | 2018-12-08 07:40 | 0.63439 | 183.7961
24.6319 | 2018-12-08 07:50 | 0.73635 | 189.1425
24.6389 | 2018-12-08 08:00 | 0.78881 | 189.928
24.6458 | 2018-12-08 08:10 | 0.78881 | 189.928
24.6528 | 2018-12-08 08:20 | 0.68014 | 181.1795
24.6597 | 2018-12-08 08:30 | 0.72083 | 187.894
24.6667 | 2018-12-08 08:40 | 0.70495 | 189.1416
24.6736 | 2018-12-08 08:50 | 0.71655 | 187.1349
24.6806 | 2018-12-08 09:00 | 0.76253 | 186.2489
24.6875 | 2018-12-08 09:10 | 0.76253 | 186.2489
24.6944 | 2018-12-08 09:20 | 0.72473 | 183.9561
24.7014 | 2018-12-08 09:30 | 0.61281 | 184.3987
24.7083 | 2018-12-08 09:40 | 0.73056 | 185.656
24.7153 | 2018-12-08 09:50 | 0.6521 | 187.8443
24.7222 | 2018-12-08 10:00 | 0.49951 | 187.7083
24.7292 | 2018-12-08 10:10 | 0.49951 | 187.7083
24.7361 | 2018-12-08 10:20 | 0.44342 | 193.0334
24.7431 | 2018-12-08 10:30 | 0.41714 | 191.3369
24.75 | 2018-12-08 10:40 | 0.33859 | 183.3863
24.7569 | 2018-12-08 10:50 | 0.2255 | 197.5511
24.7639 | 2018-12-08 11:00 | 0.16468 | 185.2259
24.7708 | 2018-12-08 11:10 | 0.16468 | 185.2259
24.7778 | 2018-12-08 11:20 | 0.11744 | 285.8114
24.7847 | 2018-12-08 11:30 | 0.01077 | 201.8014
24.7917 | 2018-12-08 11:40 | 0.13314 | 357.417
24.7986 | 2018-12-08 11:50 | 0.27097 | 8.4889
24.8056 | 2018-12-08 12:00 | 0.27509 | 1.4581
24.8125 | 2018-12-08 12:10 | 0.27509 | 1.4581
24.8194 | 2018-12-08 12:20 | 0.47227 | 358.0585
24.8264 | 2018-12-08 12:30 | 0.46799 | 7.4895
24.8333 | 2018-12-08 12:40 | 0.55455 | 8.8169
24.8403 | 2018-12-08 12:50 | 0.75525 | 9.4498
24.8472 | 2018-12-08 13:00 | 0.73078 | 4.0018
24.8542 | 2018-12-08 13:10 | 0.73078 | 4.0018
24.8611 | 2018-12-08 13:20 | 0.76555 | 2.171
24.8681 | 2018-12-08 13:30 | 0.78653 | 2.113
24.875 | 2018-12-08 13:40 | 0.72076 | 5.0145
24.8819 | 2018-12-08 13:50 | 0.77862 | 9.9099
24.8889 | 2018-12-08 14:00 | 0.74806 | 7.296
24.8958 | 2018-12-08 14:10 | 0.74806 | 7.296
24.9028 | 2018-12-08 14:20 | 0.83747 | 9.0687
24.9097 | 2018-12-08 14:30 | 0.94417 | 10.6197
24.9167 | 2018-12-08 14:40 | 0.80347 | 8.8058
24.9236 | 2018-12-08 14:50 | 0.8574 | 3.2762
24.9306 | 2018-12-08 15:00 | 0.85651 | 10.5621
24.9375 | 2018-12-08 15:10 | 0.85651 | 10.5621
24.9444 | 2018-12-08 15:20 | 0.77104 | 4.165
24.9514 | 2018-12-08 15:30 | 0.643 | 359.8218
24.9583 | 2018-12-08 15:40 | 0.55001 | 4.9021
24.9653 | 2018-12-08 15:50 | 0.68857 | 5.8348
24.9722 | 2018-12-08 16:00 | 0.581 | 5.8283
24.9792 | 2018-12-08 16:10 | 0.581 | 5.8283
24.9861 | 2018-12-08 16:20 | 0.61689 | 10.2716
24.9931 | 2018-12-08 16:30 | 0.57345 | 10.9572
25 | 2018-12-08 16:40 | 0.45287 | 3.5448
25.0069 | 2018-12-08 16:50 | 0.4837 | 6.0524
25.0139 | 2018-12-08 17:00 | 0.32576 | 10.7925
25.0208 | 2018-12-08 17:10 | 0.32576 | 10.7925
25.0278 | 2018-12-08 17:20 | 0.24798 | 354.9102
25.0347 | 2018-12-08 17:30 | 0.2286 | 6.783
25.0417 | 2018-12-08 17:40 | 0.12322 | 346.866
25.0486 | 2018-12-08 17:50 | 0.10439 | 265.054
25.0556 | 2018-12-08 18:00 | 0.17259 | 226.4086
25.0625 | 2018-12-08 18:10 | 0.17259 | 226.4086
25.0694 | 2018-12-08 18:20 | 0.38006 | 193.8534
25.0764 | 2018-12-08 18:30 | 0.4264 | 201.0279
25.0833 | 2018-12-08 18:40 | 0.44467 | 197.5385
25.0903 | 2018-12-08 18:50 | 0.4967 | 195.7711
25.0972 | 2018-12-08 19:00 | 0.511 | 180.2242
25.1042 | 2018-12-08 19:10 | 0.511 | 180.2242
25.1111 | 2018-12-08 19:20 | 0.54983 | 193.7835
25.1181 | 2018-12-08 19:30 | 0.72716 | 184.4168
25.125 | 2018-12-08 19:40 | 0.71134 | 187.0251
25.1319 | 2018-12-08 19:50 | 0.62126 | 184.8938
25.1389 | 2018-12-08 20:00 | 0.754 | 179.924
25.1458 | 2018-12-08 20:10 | 0.754 | 179.924
25.1528 | 2018-12-08 20:20 | 0.77581 | 184.8802
25.1597 | 2018-12-08 20:30 | 0.80105 | 190.356
25.1667 | 2018-12-08 20:40 | 0.70439 | 184.7231
25.1736 | 2018-12-08 20:50 | 0.76021 | 187.3307
25.1806 | 2018-12-08 21:00 | 0.78354 | 182.1211
25.1875 | 2018-12-08 21:10 | 0.78354 | 182.1211
25.1944 | 2018-12-08 21:20 | 0.66303 | 186.3211
25.2014 | 2018-12-08 21:30 | 0.6606 | 183.9929
25.2083 | 2018-12-08 21:40 | 0.63528 | 181.7139
25.2153 | 2018-12-08 21:50 | 0.63623 | 185.7733
25.2222 | 2018-12-08 22:00 | 0.62398 | 183.2155
25.2292 | 2018-12-08 22:10 | 0.62398 | 183.2155
25.2361 | 2018-12-08 22:20 | 0.47369 | 187.155
25.2431 | 2018-12-08 22:30 | 0.50448 | 182.4994
25.25 | 2018-12-08 22:40 | 0.43297 | 183.8405
25.2569 | 2018-12-08 22:50 | 0.39579 | 176.3785
25.2639 | 2018-12-08 23:00 | 0.31951 | 176.7704
25.2708 | 2018-12-08 23:10 | 0.31951 | 176.7704
25.2778 | 2018-12-08 23:20 | 0.18302 | 179.0608
25.2847 | 2018-12-08 23:30 | 0.097324 | 170.5377
25.2917 | 2018-12-08 23:40 | 0.02687 | 315
25.2986 | 2018-12-08 23:50 | 0.050448 | 13.7608
25.3056 | 2018-12-09 | 0.24463 | 9.8859
25.3125 | 2018-12-09 00:10 | 0.24463 | 9.8859
25.3194 | 2018-12-09 00:20 | 0.44881 | 9.2315
25.3264 | 2018-12-09 00:30 | 0.45796 | 6.5198
25.3333 | 2018-12-09 00:40 | 0.47202 | 0.48555
25.3403 | 2018-12-09 00:50 | 0.53286 | 6.8983
25.3472 | 2018-12-09 01:00 | 0.6463 | 8.0047
25.3542 | 2018-12-09 01:10 | 0.6463 | 8.0047
25.3611 | 2018-12-09 01:20 | 0.82235 | 7.125
25.3681 | 2018-12-09 01:30 | 0.78965 | 2.3225
25.375 | 2018-12-09 01:40 | 0.80866 | 10.5457
25.3819 | 2018-12-09 01:50 | 0.79018 | 14.2121
25.3889 | 2018-12-09 02:00 | 0.80256 | 4.5739
25.3958 | 2018-12-09 02:10 | 0.80256 | 4.5739
25.4028 | 2018-12-09 02:20 | 0.76829 | 6.7273
25.4097 | 2018-12-09 02:30 | 0.93315 | 6.5843
25.4167 | 2018-12-09 02:40 | 0.78565 | 7.4597
25.4236 | 2018-12-09 02:50 | 0.64622 | 1.5074
25.4306 | 2018-12-09 03:00 | 0.84 | 3.9593
25.4375 | 2018-12-09 03:10 | 0.84 | 3.9593
25.4444 | 2018-12-09 03:20 | 0.78958 | 3.6307
25.4514 | 2018-12-09 03:30 | 0.65913 | 358.8699
25.4583 | 2018-12-09 03:40 | 0.7119 | 4.1888
25.4653 | 2018-12-09 03:50 | 0.6718 | 10.2896
25.4722 | 2018-12-09 04:00 | 0.63742 | 8.753
25.4792 | 2018-12-09 04:10 | 0.63742 | 8.753
25.4861 | 2018-12-09 04:20 | 0.58496 | 7.4652
25.4931 | 2018-12-09 04:30 | 0.57738 | 2.0844
25.5 | 2018-12-09 04:40 | 0.52019 | 1.5422
25.5069 | 2018-12-09 04:50 | 0.483 | 359.7628
25.5139 | 2018-12-09 05:00 | 0.37675 | 10.8626
25.5208 | 2018-12-09 05:10 | 0.37675 | 10.8626
25.5278 | 2018-12-09 05:20 | 0.43312 | 1.323
25.5347 | 2018-12-09 05:30 | 0.26967 | 355.9598
25.5417 | 2018-12-09 05:40 | 0.29095 | 342.1878
25.5486 | 2018-12-09 05:50 | 0.23527 | 341.411
25.5556 | 2018-12-09 06:00 | 0.18919 | 345.3027
25.5625 | 2018-12-09 06:10 | 0.18919 | 345.3027
25.5694 | 2018-12-09 06:20 | 0.10683 | 234.5247
25.5764 | 2018-12-09 06:30 | 0.13288 | 208.3008
25.5833 | 2018-12-09 06:40 | 0.27182 | 212.9885
25.5903 | 2018-12-09 06:50 | 0.32668 | 197.8249
25.5972 | 2018-12-09 07:00 | 0.41367 | 187.6404
25.6042 | 2018-12-09 07:10 | 0.41367 | 187.6404
25.6111 | 2018-12-09 07:20 | 0.5112 | 192.541
25.6181 | 2018-12-09 07:30 | 0.54168 | 186.6789
25.625 | 2018-12-09 07:40 | 0.46431 | 188.6711
25.6319 | 2018-12-09 07:50 | 0.63584 | 185.4147
25.6389 | 2018-12-09 08:00 | 0.65583 | 190.8987
25.6458 | 2018-12-09 08:10 | 0.65583 | 190.8987
25.6528 | 2018-12-09 08:20 | 0.77939 | 184.4889
25.6597 | 2018-12-09 08:30 | 0.72328 | 181.5845
25.6667 | 2018-12-09 08:40 | 0.79327 | 185.2075
25.6736 | 2018-12-09 08:50 | 0.82166 | 184.6073
25.6806 | 2018-12-09 09:00 | 0.77708 | 187.1707
25.6875 | 2018-12-09 09:10 | 0.77708 | 187.1707
25.6944 | 2018-12-09 09:20 | 0.68502 | 180.4182
25.7014 | 2018-12-09 09:30 | 0.73776 | 187.1635
25.7083 | 2018-12-09 09:40 | 0.87801 | 182.7418
25.7153 | 2018-12-09 09:50 | 0.77611 | 180.9598
25.7222 | 2018-12-09 10:00 | 0.68201 | 180.336
25.7292 | 2018-12-09 10:10 | 0.68201 | 180.336
25.7361 | 2018-12-09 10:20 | 0.58893 | 183.2122
25.7431 | 2018-12-09 10:30 | 0.59171 | 182.8092
25.75 | 2018-12-09 10:40 | 0.52757 | 185.6566
25.7569 | 2018-12-09 10:50 | 0.59386 | 184.5393
25.7639 | 2018-12-09 11:00 | 0.4568 | 183.3885
25.7708 | 2018-12-09 11:10 | 0.4568 | 183.3885
25.7778 | 2018-12-09 11:20 | 0.46379 | 183.3374
25.7847 | 2018-12-09 11:30 | 0.38887 | 183.8337
25.7917 | 2018-12-09 11:40 | 0.2424 | 188.0632
25.7986 | 2018-12-09 11:50 | 0.2072 | 177.5105
25.8056 | 2018-12-09 12:00 | 0.1042 | 153.189
25.8125 | 2018-12-09 12:10 | 0.1042 | 153.189
25.8194 | 2018-12-09 12:20 | 0.16289 | 38.7697
25.8264 | 2018-12-09 12:30 | 0.2417 | 8.5659
25.8333 | 2018-12-09 12:40 | 0.37953 | 19.3898
25.8403 | 2018-12-09 12:50 | 0.3953 | 7.4127
25.8472 | 2018-12-09 13:00 | 0.42426 | 8.1301
25.8542 | 2018-12-09 13:10 | 0.42426 | 8.1301
25.8611 | 2018-12-09 13:20 | 0.50537 | 9.7978
25.8681 | 2018-12-09 13:30 | 0.53729 | 10.0759
25.875 | 2018-12-09 13:40 | 0.72408 | 8.0182
25.8819 | 2018-12-09 13:50 | 0.68719 | 7.6938
25.8889 | 2018-12-09 14:00 | 0.621 | 0
25.8958 | 2018-12-09 14:10 | 0.621 | 0
25.9028 | 2018-12-09 14:20 | 0.77 | 0.07441
25.9097 | 2018-12-09 14:30 | 0.66843 | 4.8918
25.9167 | 2018-12-09 14:40 | 0.77231 | 11.048
25.9236 | 2018-12-09 14:50 | 0.77019 | 4.3188
25.9306 | 2018-12-09 15:00 | 0.67501 | 3.1422
25.9375 | 2018-12-09 15:10 | 0.67501 | 3.1422
25.9444 | 2018-12-09 15:20 | 0.77169 | 9.5478
25.9514 | 2018-12-09 15:30 | 0.75447 | 3.5716
25.9583 | 2018-12-09 15:40 | 0.6777 | 4.0615
25.9653 | 2018-12-09 15:50 | 0.62107 | 6.5643
25.9722 | 2018-12-09 16:00 | 0.66492 | 3.0173
25.9792 | 2018-12-09 16:10 | 0.66492 | 3.0173
25.9861 | 2018-12-09 16:20 | 0.5631 | 6.0143
25.9931 | 2018-12-09 16:30 | 0.60307 | 7.4314
26 | 2018-12-09 16:40 | 0.47147 | 2.5529
26.0069 | 2018-12-09 16:50 | 0.44807 | 1.023
26.0139 | 2018-12-09 17:00 | 0.39329 | 2.1858
26.0208 | 2018-12-09 17:10 | 0.39329 | 2.1858
26.0278 | 2018-12-09 17:20 | 0.40377 | 9.6956
26.0347 | 2018-12-09 17:30 | 0.31431 | 353.0559
26.0417 | 2018-12-09 17:40 | 0.25019 | 352.4205
26.0486 | 2018-12-09 17:50 | 0.16623 | 336.9825
26.0556 | 2018-12-09 18:00 | 0.090796 | 352.4054
26.0625 | 2018-12-09 18:10 | 0.090796 | 352.4054
26.0694 | 2018-12-09 18:20 | 0.07506 | 267.7094
26.0764 | 2018-12-09 18:30 | 0.18602 | 232.2061
26.0833 | 2018-12-09 18:40 | 0.21618 | 221.0613
26.0903 | 2018-12-09 18:50 | 0.28853 | 207.8973
26.0972 | 2018-12-09 19:00 | 0.382 | 194.4
26.1042 | 2018-12-09 19:10 | 0.382 | 194.4
26.1111 | 2018-12-09 19:20 | 0.4624 | 199.4538
26.1181 | 2018-12-09 19:30 | 0.53831 | 187.257
26.125 | 2018-12-09 19:40 | 0.47533 | 187.738
26.1319 | 2018-12-09 19:50 | 0.59948 | 182.2944
26.1389 | 2018-12-09 20:00 | 0.59863 | 185.3677
26.1458 | 2018-12-09 20:10 | 0.59863 | 185.3677
26.1528 | 2018-12-09 20:20 | 0.57075 | 174.3693
26.1597 | 2018-12-09 20:30 | 0.69865 | 183.9395
26.1667 | 2018-12-09 20:40 | 0.78353 | 183.5855
26.1736 | 2018-12-09 20:50 | 0.67357 | 183.9159
26.1806 | 2018-12-09 21:00 | 0.62684 | 184.3917
26.1875 | 2018-12-09 21:10 | 0.62684 | 184.3917
26.1944 | 2018-12-09 21:20 | 0.76778 | 188.1618
26.2014 | 2018-12-09 21:30 | 0.72003 | 187.4211
26.2083 | 2018-12-09 21:40 | 0.75129 | 186.8034
26.2153 | 2018-12-09 21:50 | 0.71831 | 181.6753
26.2222 | 2018-12-09 22:00 | 0.72366 | 177.5448
26.2292 | 2018-12-09 22:10 | 0.72366 | 177.5448
26.2361 | 2018-12-09 22:20 | 0.61166 | 174.6529
26.2431 | 2018-12-09 22:30 | 0.66446 | 187.3496
26.25 | 2018-12-09 22:40 | 0.59311 | 184.8358
26.2569 | 2018-12-09 22:50 | 0.47808 | 178.9213
26.2639 | 2018-12-09 23:00 | 0.52811 | 178.8065
26.2708 | 2018-12-09 23:10 | 0.52811 | 178.8065
26.2778 | 2018-12-09 23:20 | 0.49271 | 187.9328
26.2847 | 2018-12-09 23:30 | 0.34709 | 178.6793
26.2917 | 2018-12-09 23:40 | 0.49059 | 177.1959
26.2986 | 2018-12-09 23:50 | 0.31027 | 174.8223
26.3056 | 2018-12-10 | 0.23515 | 169.2157
26.3125 | 2018-12-10 00:10 | 0.23515 | 169.2157
26.3194 | 2018-12-10 00:20 | 0.13473 | 174.0355
26.3264 | 2018-12-10 00:30 | 0.064846 | 153.435
26.3333 | 2018-12-10 00:40 | 0.022361 | 26.565
26.3403 | 2018-12-10 00:50 | 0.2117 | 24.2648
26.3472 | 2018-12-10 01:00 | 0.33344 | 24.2591
26.3542 | 2018-12-10 01:10 | 0.33344 | 24.2591
26.3611 | 2018-12-10 01:20 | 0.43516 | 7.9253
26.3681 | 2018-12-10 01:30 | 0.56962 | 19.4847
26.375 | 2018-12-10 01:40 | 0.5063 | 18.9002
26.3819 | 2018-12-10 01:50 | 0.59689 | 13.6637
26.3889 | 2018-12-10 02:00 | 0.61718 | 1.3927
26.3958 | 2018-12-10 02:10 | 0.61718 | 1.3927
26.4028 | 2018-12-10 02:20 | 0.7463 | 1.6125
26.4097 | 2018-12-10 02:30 | 0.65043 | 10.2733
26.4167 | 2018-12-10 02:40 | 0.91062 | 8.3348
26.4236 | 2018-12-10 02:50 | 0.73514 | 4.3688
26.4306 | 2018-12-10 03:00 | 0.85173 | 11.3759
26.4375 | 2018-12-10 03:10 | 0.85173 | 11.3759
26.4444 | 2018-12-10 03:20 | 0.74722 | 9.0085
26.4514 | 2018-12-10 03:30 | 0.84821 | 11.5616
26.4583 | 2018-12-10 03:40 | 0.79101 | 0.28974
26.4653 | 2018-12-10 03:50 | 0.79119 | 5.1485
26.4722 | 2018-12-10 04:00 | 0.87125 | 5.6648
26.4792 | 2018-12-10 04:10 | 0.87125 | 5.6648
26.4861 | 2018-12-10 04:20 | 0.65441 | 3.7675
26.4931 | 2018-12-10 04:30 | 0.63866 | 4.1304
26.5 | 2018-12-10 04:40 | 0.6278 | 6.31
26.5069 | 2018-12-10 04:50 | 0.75604 | 0.60628
26.5139 | 2018-12-10 05:00 | 0.56079 | 8.9248
26.5208 | 2018-12-10 05:10 | 0.56079 | 8.9248
26.5278 | 2018-12-10 05:20 | 0.4228 | 356.4744
26.5347 | 2018-12-10 05:30 | 0.545 | 0
26.5417 | 2018-12-10 05:40 | 0.35112 | 358.5312
26.5486 | 2018-12-10 05:50 | 0.33518 | 1.8807
26.5556 | 2018-12-10 06:00 | 0.32835 | 342.9999
26.5625 | 2018-12-10 06:10 | 0.32835 | 342.9999
26.5694 | 2018-12-10 06:20 | 0.23345 | 353.6056
26.5764 | 2018-12-10 06:30 | 0.14277 | 348.6901
26.5833 | 2018-12-10 06:40 | 0.077621 | 284.9314
26.5903 | 2018-12-10 06:50 | 0.11116 | 273.0941
26.5972 | 2018-12-10 07:00 | 0.15086 | 255.4111
26.6042 | 2018-12-10 07:10 | 0.15086 | 255.4111
26.6111 | 2018-12-10 07:20 | 0.27896 | 209.4137
26.6181 | 2018-12-10 07:30 | 0.3338 | 196.5348
26.625 | 2018-12-10 07:40 | 0.45541 | 197.6392
26.6319 | 2018-12-10 07:50 | 0.47386 | 186.3001
26.6389 | 2018-12-10 08:00 | 0.52275 | 183.0704
26.6458 | 2018-12-10 08:10 | 0.52275 | 183.0704
26.6528 | 2018-12-10 08:20 | 0.583 | 192.5821
26.6597 | 2018-12-10 08:30 | 0.63145 | 188.1943
26.6667 | 2018-12-10 08:40 | 0.62676 | 184.3006
26.6736 | 2018-12-10 08:50 | 0.7031 | 179.0221
26.6806 | 2018-12-10 09:00 | 0.66852 | 183.8597
26.6875 | 2018-12-10 09:10 | 0.66852 | 183.8597
26.6944 | 2018-12-10 09:20 | 0.82203 | 179.5121
26.7014 | 2018-12-10 09:30 | 0.76016 | 183.1673
26.7083 | 2018-12-10 09:40 | 0.76944 | 181.9364
26.7153 | 2018-12-10 09:50 | 0.73825 | 183.3391
26.7222 | 2018-12-10 10:00 | 0.79273 | 182.4582
26.7292 | 2018-12-10 10:10 | 0.79273 | 182.4582
26.7361 | 2018-12-10 10:20 | 0.70048 | 177.8728
26.7431 | 2018-12-10 10:30 | 0.82516 | 181.1111
26.75 | 2018-12-10 10:40 | 0.63928 | 187.3696
26.7569 | 2018-12-10 10:50 | 0.80176 | 182.502
26.7639 | 2018-12-10 11:00 | 0.63697 | 186.3998
26.7708 | 2018-12-10 11:10 | 0.63697 | 186.3998
26.7778 | 2018-12-10 11:20 | 0.50058 | 182.7481
26.7847 | 2018-12-10 11:30 | 0.60801 | 183.3001
26.7917 | 2018-12-10 11:40 | 0.54121 | 181.5882
26.7986 | 2018-12-10 11:50 | 0.52688 | 185.9919
26.8056 | 2018-12-10 12:00 | 0.42692 | 183.7605
26.8125 | 2018-12-10 12:10 | 0.42692 | 183.7605
26.8194 | 2018-12-10 12:20 | 0.36251 | 170.9534
26.8264 | 2018-12-10 12:30 | 0.364 | 180.1574
26.8333 | 2018-12-10 12:40 | 0.13697 | 163.0203
26.8403 | 2018-12-10 12:50 | 0.11861 | 185.8067
26.8472 | 2018-12-10 13:00 | 0.070214 | 72.5973
26.8542 | 2018-12-10 13:10 | 0.070214 | 72.5973
26.8611 | 2018-12-10 13:20 | 0.24649 | 20.42
26.8681 | 2018-12-10 13:30 | 0.40148 | 22.0929
26.875 | 2018-12-10 13:40 | 0.39687 | 18.6632
26.8819 | 2018-12-10 13:50 | 0.47369 | 7.155
26.8889 | 2018-12-10 14:00 | 0.50399 | 14.0087
26.8958 | 2018-12-10 14:10 | 0.50399 | 14.0087
26.9028 | 2018-12-10 14:20 | 0.51569 | 16.678
26.9097 | 2018-12-10 14:30 | 0.51275 | 14.6867
26.9167 | 2018-12-10 14:40 | 0.55616 | 5.0545
26.9236 | 2018-12-10 14:50 | 0.60649 | 6.1524
26.9306 | 2018-12-10 15:00 | 0.77037 | 1.7853
26.9375 | 2018-12-10 15:10 | 0.77037 | 1.7853
26.9444 | 2018-12-10 15:20 | 0.8569 | 3.8141
26.9514 | 2018-12-10 15:30 | 0.7581 | 7.275
26.9583 | 2018-12-10 15:40 | 0.87277 | 5.3252
26.9653 | 2018-12-10 15:50 | 0.76215 | 9.3635
26.9722 | 2018-12-10 16:00 | 0.66915 | 1.1988
26.9792 | 2018-12-10 16:10 | 0.66915 | 1.1988
26.9861 | 2018-12-10 16:20 | 0.63912 | 355.3331
26.9931 | 2018-12-10 16:30 | 0.63665 | 5.227
27 | 2018-12-10 16:40 | 0.66503 | 0.51694
27.0069 | 2018-12-10 16:50 | 0.66117 | 1.3
27.0139 | 2018-12-10 17:00 | 0.53138 | 357.843
27.0208 | 2018-12-10 17:10 | 0.53138 | 357.843
27.0278 | 2018-12-10 17:20 | 0.45009 | 358.8542
27.0347 | 2018-12-10 17:30 | 0.47309 | 1.0901
27.0417 | 2018-12-10 17:40 | 0.34471 | 12.9074
27.0486 | 2018-12-10 17:50 | 0.41019 | 9.9675
27.0556 | 2018-12-10 18:00 | 0.32601 | 345.0686
27.0625 | 2018-12-10 18:10 | 0.32601 | 345.0686
27.0694 | 2018-12-10 18:20 | 0.26468 | 9.5691
27.0764 | 2018-12-10 18:30 | 0.16362 | 337.3532
27.0833 | 2018-12-10 18:40 | 0.14384 | 308.2243
27.0903 | 2018-12-10 18:50 | 0.078791 | 293.9625
27.0972 | 2018-12-10 19:00 | 0.106 | 270
27.1042 | 2018-12-10 19:10 | 0.106 | 270
27.1111 | 2018-12-10 19:20 | 0.15981 | 217.3719
27.1181 | 2018-12-10 19:30 | 0.34937 | 200.6136
27.125 | 2018-12-10 19:40 | 0.34447 | 205.0772
27.1319 | 2018-12-10 19:50 | 0.42032 | 196.0203
27.1389 | 2018-12-10 20:00 | 0.43376 | 192.7867
27.1458 | 2018-12-10 20:10 | 0.43376 | 192.7867
27.1528 | 2018-12-10 20:20 | 0.51598 | 192.8781
27.1597 | 2018-12-10 20:30 | 0.59673 | 185.4813
27.1667 | 2018-12-10 20:40 | 0.50512 | 181.2478
27.1736 | 2018-12-10 20:50 | 0.60222 | 190.041
27.1806 | 2018-12-10 21:00 | 0.59609 | 183.4624
27.1875 | 2018-12-10 21:10 | 0.59609 | 183.4624
27.1944 | 2018-12-10 21:20 | 0.70371 | 176.0072
27.2014 | 2018-12-10 21:30 | 0.69318 | 190.3048
27.2083 | 2018-12-10 21:40 | 0.69395 | 184.2974
27.2153 | 2018-12-10 21:50 | 0.6613 | 178.2669
27.2222 | 2018-12-10 22:00 | 0.79821 | 183.1599
27.2292 | 2018-12-10 22:10 | 0.79821 | 183.1599
27.2361 | 2018-12-10 22:20 | 0.80604 | 179.4313
27.2431 | 2018-12-10 22:30 | 0.778 | 180.0736
27.25 | 2018-12-10 22:40 | 0.76675 | 177.4585
27.2569 | 2018-12-10 22:50 | 0.65533 | 185.7802
27.2639 | 2018-12-10 23:00 | 0.65541 | 183.7617
27.2708 | 2018-12-10 23:10 | 0.65541 | 183.7617
27.2778 | 2018-12-10 23:20 | 0.61555 | 177.5792
27.2847 | 2018-12-10 23:30 | 0.59912 | 178.8523
27.2917 | 2018-12-10 23:40 | 0.52774 | 183.0413
27.2986 | 2018-12-10 23:50 | 0.48907 | 180.9373
27.3056 | 2018-12-11 | 0.41133 | 175.3983
27.3125 | 2018-12-11 00:10 | 0.41133 | 175.3983
27.3194 | 2018-12-11 00:20 | 0.31495 | 173.6196
27.3264 | 2018-12-11 00:30 | 0.33049 | 183.1221
27.3333 | 2018-12-11 00:40 | 0.17439 | 159.1748
27.3403 | 2018-12-11 00:50 | 0.15876 | 160.8803
27.3472 | 2018-12-11 01:00 | 0.072062 | 92.3859
27.3542 | 2018-12-11 01:10 | 0.072062 | 92.3859
27.3611 | 2018-12-11 01:20 | 0.19535 | 47.4896
27.3681 | 2018-12-11 01:30 | 0.3137 | 18.7815
27.375 | 2018-12-11 01:40 | 0.33317 | 26.565
27.3819 | 2018-12-11 01:50 | 0.44507 | 25.4135
27.3889 | 2018-12-11 02:00 | 0.52938 | 18.8457
27.3958 | 2018-12-11 02:10 | 0.52938 | 18.8457
27.4028 | 2018-12-11 02:20 | 0.64257 | 15.8964
27.4097 | 2018-12-11 02:30 | 0.45732 | 5.7729
27.4167 | 2018-12-11 02:40 | 0.5374 | 8.1301
27.4236 | 2018-12-11 02:50 | 0.60534 | 8.9333
27.4306 | 2018-12-11 03:00 | 0.73139 | 3.5275
27.4375 | 2018-12-11 03:10 | 0.73139 | 3.5275
27.4444 | 2018-12-11 03:20 | 0.77218 | 4.3077
27.4514 | 2018-12-11 03:30 | 0.74685 | 6.535
27.4583 | 2018-12-11 03:40 | 0.78928 | 3.2684
27.4653 | 2018-12-11 03:50 | 0.90982 | 7.5156
27.4722 | 2018-12-11 04:00 | 0.84613 | 10.4865
27.4792 | 2018-12-11 04:10 | 0.84613 | 10.4865
27.4861 | 2018-12-11 04:20 | 0.72008 | 359.1247
27.4931 | 2018-12-11 04:30 | 0.81031 | 3.2544
27.5 | 2018-12-11 04:40 | 0.76389 | 5.7852
27.5069 | 2018-12-11 04:50 | 0.728 | 0
27.5139 | 2018-12-11 05:00 | 0.72128 | 1.5889
27.5208 | 2018-12-11 05:10 | 0.72128 | 1.5889
27.5278 | 2018-12-11 05:20 | 0.54258 | 2.6409
27.5347 | 2018-12-11 05:30 | 0.49403 | 0.5799
27.5417 | 2018-12-11 05:40 | 0.51198 | 8.7632
27.5486 | 2018-12-11 05:50 | 0.39501 | 0.2901
27.5556 | 2018-12-11 06:00 | 0.34071 | 356.2978
27.5625 | 2018-12-11 06:10 | 0.34071 | 356.2978
27.5694 | 2018-12-11 06:20 | 0.33925 | 357.8039
27.5764 | 2018-12-11 06:30 | 0.30472 | 3.9517
27.5833 | 2018-12-11 06:40 | 0.30859 | 356.47
27.5903 | 2018-12-11 06:50 | 0.20006 | 324.5622
27.5972 | 2018-12-11 07:00 | 0.21974 | 327.8288
27.6042 | 2018-12-11 07:10 | 0.21974 | 327.8288
27.6111 | 2018-12-11 07:20 | 0.16038 | 299.9221
27.6181 | 2018-12-11 07:30 | 0.10868 | 282.7575
27.625 | 2018-12-11 07:40 | 0.092455 | 231.1466
27.6319 | 2018-12-11 07:50 | 0.15526 | 204.7494
27.6389 | 2018-12-11 08:00 | 0.2404 | 195.1924
27.6458 | 2018-12-11 08:10 | 0.2404 | 195.1924
27.6528 | 2018-12-11 08:20 | 0.45507 | 197.9173
27.6597 | 2018-12-11 08:30 | 0.45503 | 180.6296
27.6667 | 2018-12-11 08:40 | 0.50676 | 191.2656
27.6736 | 2018-12-11 08:50 | 0.5092 | 186.4272
27.6806 | 2018-12-11 09:00 | 0.49147 | 191.2642
27.6875 | 2018-12-11 09:10 | 0.49147 | 191.2642
27.6944 | 2018-12-11 09:20 | 0.607 | 180.1888
27.7014 | 2018-12-11 09:30 | 0.68905 | 183.1614
27.7083 | 2018-12-11 09:40 | 0.68642 | 182.0037
27.7153 | 2018-12-11 09:50 | 0.74148 | 186.9717
27.7222 | 2018-12-11 10:00 | 0.65933 | 181.8252
27.7292 | 2018-12-11 10:10 | 0.65933 | 181.8252
27.7361 | 2018-12-11 10:20 | 0.69502 | 180.4122
27.7431 | 2018-12-11 10:30 | 0.70831 | 181.699
27.75 | 2018-12-11 10:40 | 0.76335 | 178.2734
27.7569 | 2018-12-11 10:50 | 0.7006 | 177.6277
27.7639 | 2018-12-11 11:00 | 0.79742 | 187.2765
27.7708 | 2018-12-11 11:10 | 0.79742 | 187.2765
27.7778 | 2018-12-11 11:20 | 0.71943 | 181.9914
27.7847 | 2018-12-11 11:30 | 0.68504 | 180.5855
27.7917 | 2018-12-11 11:40 | 0.59965 | 182.6763
27.7986 | 2018-12-11 11:50 | 0.61336 | 181.9621
27.8056 | 2018-12-11 12:00 | 0.48437 | 182.2481
27.8125 | 2018-12-11 12:10 | 0.48437 | 182.2481
27.8194 | 2018-12-11 12:20 | 0.49312 | 178.7218
27.8264 | 2018-12-11 12:30 | 0.43533 | 177.762
27.8333 | 2018-12-11 12:40 | 0.38829 | 182.2139
27.8403 | 2018-12-11 12:50 | 0.27638 | 169.7879
27.8472 | 2018-12-11 13:00 | 0.26521 | 152.8552
27.8542 | 2018-12-11 13:10 | 0.26521 | 152.8552
27.8611 | 2018-12-11 13:20 | 0.1786 | 126.8057
27.8681 | 2018-12-11 13:30 | 0.14318 | 102.0948
27.875 | 2018-12-11 13:40 | 0.173 | 49.2191
27.8819 | 2018-12-11 13:50 | 0.16607 | 40.1148
27.8889 | 2018-12-11 14:00 | 0.30208 | 40.7042
27.8958 | 2018-12-11 14:10 | 0.30208 | 40.7042
27.9028 | 2018-12-11 14:20 | 0.41801 | 22.2087
27.9097 | 2018-12-11 14:30 | 0.48987 | 19.0637
27.9167 | 2018-12-11 14:40 | 0.56782 | 12.2005
27.9236 | 2018-12-11 14:50 | 0.69438 | 13.9162
27.9306 | 2018-12-11 15:00 | 0.6743 | 6.4716
27.9375 | 2018-12-11 15:10 | 0.6743 | 6.4716
27.9444 | 2018-12-11 15:20 | 0.68466 | 2.5114
27.9514 | 2018-12-11 15:30 | 0.72504 | 359.3678
27.9583 | 2018-12-11 15:40 | 0.78429 | 3.2892
27.9653 | 2018-12-11 15:50 | 0.74483 | 13.9056
27.9722 | 2018-12-11 16:00 | 0.76958 | 4.6956
27.9792 | 2018-12-11 16:10 | 0.76958 | 4.6956
27.9861 | 2018-12-11 16:20 | 0.85544 | 13.7276
27.9931 | 2018-12-11 16:30 | 0.73227 | 6.1933
28 | 2018-12-11 16:40 | 0.90581 | 5.2574
28.0069 | 2018-12-11 16:50 | 0.68966 | 6.6613
28.0139 | 2018-12-11 17:00 | 0.8046 | 2.2081
28.0208 | 2018-12-11 17:10 | 0.8046 | 2.2081
28.0278 | 2018-12-11 17:20 | 0.62663 | 2.561
28.0347 | 2018-12-11 17:30 | 0.63039 | 10.4187
28.0417 | 2018-12-11 17:40 | 0.45181 | 3.426
28.0486 | 2018-12-11 17:50 | 0.53958 | 8.9561
28.0556 | 2018-12-11 18:00 | 0.506 | 5.1022
28.0625 | 2018-12-11 18:10 | 0.506 | 5.1022
28.0694 | 2018-12-11 18:20 | 0.34632 | 6.6325
28.0764 | 2018-12-11 18:30 | 0.331 | 0.1731
28.0833 | 2018-12-11 18:40 | 0.36685 | 351.6932
28.0903 | 2018-12-11 18:50 | 0.24956 | 350.3112
28.0972 | 2018-12-11 19:00 | 0.205 | 359.7205
28.1042 | 2018-12-11 19:10 | 0.205 | 359.7205
28.1111 | 2018-12-11 19:20 | 0.049041 | 267.6627
28.1181 | 2018-12-11 19:30 | 0.15451 | 291.2505
28.125 | 2018-12-11 19:40 | 0.11456 | 225.7073
28.1319 | 2018-12-11 19:50 | 0.16403 | 215.8219
28.1389 | 2018-12-11 20:00 | 0.30455 | 202.1857
28.1458 | 2018-12-11 20:10 | 0.30455 | 202.1857
28.1528 | 2018-12-11 20:20 | 0.38502 | 189.2666
28.1597 | 2018-12-11 20:30 | 0.52161 | 192.6241
28.1667 | 2018-12-11 20:40 | 0.47994 | 186.3402
28.1736 | 2018-12-11 20:50 | 0.458 | 179.7498
28.1806 | 2018-12-11 21:00 | 0.59586 | 184.5241
28.1875 | 2018-12-11 21:10 | 0.59586 | 184.5241
28.1944 | 2018-12-11 21:20 | 0.507 | 180.226
28.2014 | 2018-12-11 21:30 | 0.59112 | 181.1632
28.2083 | 2018-12-11 21:40 | 0.70244 | 188.3493
28.2153 | 2018-12-11 21:50 | 0.71112 | 181.0475
28.2222 | 2018-12-11 22:00 | 0.69501 | 179.6702
28.2292 | 2018-12-11 22:10 | 0.69501 | 179.6702
28.2361 | 2018-12-11 22:20 | 0.66892 | 177.0007
28.2431 | 2018-12-11 22:30 | 0.69232 | 178.2618
28.25 | 2018-12-11 22:40 | 0.78687 | 182.6951
28.2569 | 2018-12-11 22:50 | 0.73704 | 179.3781
28.2639 | 2018-12-11 23:00 | 0.7342 | 178.6732
28.2708 | 2018-12-11 23:10 | 0.7342 | 178.6732
28.2778 | 2018-12-11 23:20 | 0.6586 | 182.4366
28.2847 | 2018-12-11 23:30 | 0.69462 | 186.6135
28.2917 | 2018-12-11 23:40 | 0.5403 | 187.2302
28.2986 | 2018-12-11 23:50 | 0.59201 | 179.7097
28.3056 | 2018-12-12 | 0.41316 | 175.697
28.3125 | 2018-12-12 00:10 | 0.41316 | 175.697
28.3194 | 2018-12-12 00:20 | 0.4783 | 172.3104
28.3264 | 2018-12-12 00:30 | 0.41881 | 176.4407
28.3333 | 2018-12-12 00:40 | 0.35221 | 166.8713
28.3403 | 2018-12-12 00:50 | 0.34808 | 173.7325
28.3472 | 2018-12-12 01:00 | 0.33333 | 160.9128
28.3542 | 2018-12-12 01:10 | 0.33333 | 160.9128
28.3611 | 2018-12-12 01:20 | 0.15535 | 156.075
28.3681 | 2018-12-12 01:30 | 0.12163 | 134.3338
28.375 | 2018-12-12 01:40 | 0.11035 | 75.8378
28.3819 | 2018-12-12 01:50 | 0.051478 | 60.9454
28.3889 | 2018-12-12 02:00 | 0.16477 | 44.2623
28.3958 | 2018-12-12 02:10 | 0.16477 | 44.2623
28.4028 | 2018-12-12 02:20 | 0.34545 | 31.9878
28.4097 | 2018-12-12 02:30 | 0.39899 | 20.388
28.4167 | 2018-12-12 02:40 | 0.49156 | 12.4529
28.4236 | 2018-12-12 02:50 | 0.58791 | 17.7261
28.4306 | 2018-12-12 03:00 | 0.61951 | 18.9321
28.4375 | 2018-12-12 03:10 | 0.61951 | 18.9321
28.4444 | 2018-12-12 03:20 | 0.58248 | 10.8855
28.4514 | 2018-12-12 03:30 | 0.57248 | 7.9319
28.4583 | 2018-12-12 03:40 | 0.68557 | 357.6593
28.4653 | 2018-12-12 03:50 | 0.71347 | 8.3005
28.4722 | 2018-12-12 04:00 | 0.83171 | 7.8086
28.4792 | 2018-12-12 04:10 | 0.83171 | 7.8086
28.4861 | 2018-12-12 04:20 | 0.66033 | 11.5312
28.4931 | 2018-12-12 04:30 | 0.85307 | 9.2415
28.5 | 2018-12-12 04:40 | 0.8056 | 2.2053
28.5069 | 2018-12-12 04:50 | 0.81476 | 4.7169
28.5139 | 2018-12-12 05:00 | 0.6224 | 5.9946
28.5208 | 2018-12-12 05:10 | 0.6224 | 5.9946
28.5278 | 2018-12-12 05:20 | 0.73828 | 4.5058
28.5347 | 2018-12-12 05:30 | 0.63333 | 3.7118
28.5417 | 2018-12-12 05:40 | 0.67386 | 6.1336
28.5486 | 2018-12-12 05:50 | 0.66289 | 10.8692
28.5556 | 2018-12-12 06:00 | 0.60205 | 9.9473
28.5625 | 2018-12-12 06:10 | 0.60205 | 9.9473
28.5694 | 2018-12-12 06:20 | 0.50014 | 1.3748
28.5764 | 2018-12-12 06:30 | 0.41204 | 359.1656
28.5833 | 2018-12-12 06:40 | 0.41922 | 4.3777
28.5903 | 2018-12-12 06:50 | 0.41701 | 6.8864
28.5972 | 2018-12-12 07:00 | 0.35952 | 5.2666
28.6042 | 2018-12-12 07:10 | 0.35952 | 5.2666
28.6111 | 2018-12-12 07:20 | 0.35152 | 6.8622
28.6181 | 2018-12-12 07:30 | 0.26403 | 359.132
28.625 | 2018-12-12 07:40 | 0.22918 | 357.7494
28.6319 | 2018-12-12 07:50 | 0.10771 | 12.875
28.6389 | 2018-12-12 08:00 | 0.12008 | 347.0054
28.6458 | 2018-12-12 08:10 | 0.12008 | 347.0054
28.6528 | 2018-12-12 08:20 | 0.088091 | 230.5275
28.6597 | 2018-12-12 08:30 | 0.12806 | 231.3402
28.6667 | 2018-12-12 08:40 | 0.16564 | 201.6087
28.6736 | 2018-12-12 08:50 | 0.27196 | 198.435
28.6806 | 2018-12-12 09:00 | 0.34091 | 192.3647
28.6875 | 2018-12-12 09:10 | 0.34091 | 192.3647
28.6944 | 2018-12-12 09:20 | 0.38835 | 199.0881
28.7014 | 2018-12-12 09:30 | 0.41057 | 187.5578
28.7083 | 2018-12-12 09:40 | 0.47586 | 174.9364
28.7153 | 2018-12-12 09:50 | 0.42517 | 178.3827
28.7222 | 2018-12-12 10:00 | 0.47383 | 183.3878
28.7292 | 2018-12-12 10:10 | 0.47383 | 183.3878
28.7361 | 2018-12-12 10:20 | 0.5707 | 175.5782
28.7431 | 2018-12-12 10:30 | 0.60805 | 179.2462
28.75 | 2018-12-12 10:40 | 0.55926 | 178.2581
28.7569 | 2018-12-12 10:50 | 0.5704 | 184.0212
28.7639 | 2018-12-12 11:00 | 0.63146 | 182.1782
28.7708 | 2018-12-12 11:10 | 0.63146 | 182.1782
28.7778 | 2018-12-12 11:20 | 0.59686 | 183.0733
28.7847 | 2018-12-12 11:30 | 0.58712 | 181.1711
28.7917 | 2018-12-12 11:40 | 0.58841 | 177.8573
28.7986 | 2018-12-12 11:50 | 0.6321 | 179.0029
28.8056 | 2018-12-12 12:00 | 0.60302 | 179.5249
28.8125 | 2018-12-12 12:10 | 0.60302 | 179.5249
28.8194 | 2018-12-12 12:20 | 0.5775 | 177.6182
28.8264 | 2018-12-12 12:30 | 0.48218 | 181.545
28.8333 | 2018-12-12 12:40 | 0.51531 | 182.0018
28.8403 | 2018-12-12 12:50 | 0.45463 | 183.026
28.8472 | 2018-12-12 13:00 | 0.39704 | 172.9108
28.8542 | 2018-12-12 13:10 | 0.39704 | 172.9108
28.8611 | 2018-12-12 13:20 | 0.28398 | 161.9479
28.8681 | 2018-12-12 13:30 | 0.2563 | 152.3352
28.875 | 2018-12-12 13:40 | 0.19366 | 170.489
28.8819 | 2018-12-12 13:50 | 0.15426 | 144.7646
28.8889 | 2018-12-12 14:00 | 0.13746 | 81.6341
28.8958 | 2018-12-12 14:10 | 0.13746 | 81.6341
28.9028 | 2018-12-12 14:20 | 0.18651 | 64.2593
28.9097 | 2018-12-12 14:30 | 0.2588 | 44.6869
28.9167 | 2018-12-12 14:40 | 0.38663 | 33.6079
28.9236 | 2018-12-12 14:50 | 0.39854 | 22.5756
28.9306 | 2018-12-12 15:00 | 0.46485 | 22.6483
28.9375 | 2018-12-12 15:10 | 0.46485 | 22.6483
28.9444 | 2018-12-12 15:20 | 0.48524 | 17.0159
28.9514 | 2018-12-12 15:30 | 0.54961 | 14.5419
28.9583 | 2018-12-12 15:40 | 0.63531 | 10.3371
28.9653 | 2018-12-12 15:50 | 0.53982 | 7.6648
28.9722 | 2018-12-12 16:00 | 0.62103 | 0.55357
28.9792 | 2018-12-12 16:10 | 0.62103 | 0.55357
28.9861 | 2018-12-12 16:20 | 0.74798 | 8.3793
28.9931 | 2018-12-12 16:30 | 0.80894 | 2.7634
29 | 2018-12-12 16:40 | 0.7227 | 9.3972
29.0069 | 2018-12-12 16:50 | 0.76114 | 7.8533
29.0139 | 2018-12-12 17:00 | 0.84403 | 6.2577
29.0208 | 2018-12-12 17:10 | 0.84403 | 6.2577
29.0278 | 2018-12-12 17:20 | 0.81004 | 2.9013
29.0347 | 2018-12-12 17:30 | 0.65504 | 0.6123
29.0417 | 2018-12-12 17:40 | 0.64154 | 5.0974
29.0486 | 2018-12-12 17:50 | 0.69659 | 3.8688
29.0556 | 2018-12-12 18:00 | 0.63084 | 14.0362
29.0625 | 2018-12-12 18:10 | 0.63084 | 14.0362
29.0694 | 2018-12-12 18:20 | 0.52138 | 2.1984
29.0764 | 2018-12-12 18:30 | 0.57717 | 4.9697
29.0833 | 2018-12-12 18:40 | 0.44152 | 8.2035
29.0903 | 2018-12-12 18:50 | 0.42217 | 358.3712
29.0972 | 2018-12-12 19:00 | 0.44026 | 358.0475
29.1042 | 2018-12-12 19:10 | 0.44026 | 358.0475
29.1111 | 2018-12-12 19:20 | 0.31501 | 0.36378
29.1181 | 2018-12-12 19:30 | 0.251 | 359.7717
29.125 | 2018-12-12 19:40 | 0.14454 | 10.7658
29.1319 | 2018-12-12 19:50 | 0.17641 | 32.9694
29.1389 | 2018-12-12 20:00 | 0.067476 | 320.4119
29.1458 | 2018-12-12 20:10 | 0.067476 | 320.4119
29.1528 | 2018-12-12 20:20 | 0.056719 | 189.1302
29.1597 | 2018-12-12 20:30 | 0.1843 | 170.9466
29.1667 | 2018-12-12 20:40 | 0.16337 | 214.2737
29.1736 | 2018-12-12 20:50 | 0.29095 | 197.8122
29.1806 | 2018-12-12 21:00 | 0.30237 | 188.5589
29.1875 | 2018-12-12 21:10 | 0.30237 | 188.5589
29.1944 | 2018-12-12 21:20 | 0.46318 | 181.6083
29.2014 | 2018-12-12 21:30 | 0.45319 | 181.6438
29.2083 | 2018-12-12 21:40 | 0.54483 | 189.082
29.2153 | 2018-12-12 21:50 | 0.53637 | 177.8631
29.2222 | 2018-12-12 22:00 | 0.40959 | 174.9576
29.2292 | 2018-12-12 22:10 | 0.40959 | 174.9576
29.2361 | 2018-12-12 22:20 | 0.57038 | 186.2404
29.2431 | 2018-12-12 22:30 | 0.66647 | 182.1497
29.25 | 2018-12-12 22:40 | 0.58829 | 183.8011
29.2569 | 2018-12-12 22:50 | 0.6604 | 178.0041
29.2639 | 2018-12-12 23:00 | 0.625 | 179.9083
29.2708 | 2018-12-12 23:10 | 0.625 | 179.9083
29.2778 | 2018-12-12 23:20 | 0.61394 | 183.1747
29.2847 | 2018-12-12 23:30 | 0.57055 | 177.4886
29.2917 | 2018-12-12 23:40 | 0.64585 | 172.974
29.2986 | 2018-12-12 23:50 | 0.59134 | 178.0618
29.3056 | 2018-12-13 | 0.55729 | 178.1491
29.3125 | 2018-12-13 00:10 | 0.55729 | 178.1491
29.3194 | 2018-12-13 00:20 | 0.47812 | 185.4006
29.3264 | 2018-12-13 00:30 | 0.5345 | 182.4663
29.3333 | 2018-12-13 00:40 | 0.37961 | 188.9412
29.3403 | 2018-12-13 00:50 | 0.43026 | 178.0021
29.3472 | 2018-12-13 01:00 | 0.41159 | 176.936
29.3542 | 2018-12-13 01:10 | 0.41159 | 176.936
29.3611 | 2018-12-13 01:20 | 0.34098 | 172.4165
29.3681 | 2018-12-13 01:30 | 0.35893 | 171.5087
29.375 | 2018-12-13 01:40 | 0.25479 | 175.4978
29.3819 | 2018-12-13 01:50 | 0.18495 | 168.1432
29.3889 | 2018-12-13 02:00 | 0.19186 | 153.7021
29.3958 | 2018-12-13 02:10 | 0.19186 | 153.7021
29.4028 | 2018-12-13 02:20 | 0.158 | 90.3626
29.4097 | 2018-12-13 02:30 | 0.14736 | 82.1998
29.4167 | 2018-12-13 02:40 | 0.18021 | 13.8049
29.4236 | 2018-12-13 02:50 | 0.1832 | 12.2913
29.4306 | 2018-12-13 03:00 | 0.37497 | 14.518
29.4375 | 2018-12-13 03:10 | 0.37497 | 14.518
29.4444 | 2018-12-13 03:20 | 0.48145 | 13.5744
29.4514 | 2018-12-13 03:30 | 0.44537 | 15.0972
29.4583 | 2018-12-13 03:40 | 0.57868 | 4.3607
29.4653 | 2018-12-13 03:50 | 0.53146 | 8.2216
29.4722 | 2018-12-13 04:00 | 0.56739 | 5.2584
29.4792 | 2018-12-13 04:10 | 0.56739 | 5.2584
29.4861 | 2018-12-13 04:20 | 0.68545 | 6.534
29.4931 | 2018-12-13 04:30 | 0.77138 | 15.0271
29.5 | 2018-12-13 04:40 | 0.77379 | 6.3811
29.5069 | 2018-12-13 04:50 | 0.89208 | 6.6948
29.5139 | 2018-12-13 05:00 | 0.78801 | 0.29084
29.5208 | 2018-12-13 05:10 | 0.78801 | 0.29084
29.5278 | 2018-12-13 05:20 | 0.86977 | 6.6021
29.5347 | 2018-12-13 05:30 | 0.78367 | 7.4787
29.5417 | 2018-12-13 05:40 | 0.7221 | 4.3683
29.5486 | 2018-12-13 05:50 | 0.77468 | 3.7747
29.5556 | 2018-12-13 06:00 | 0.66996 | 8.8437
29.5625 | 2018-12-13 06:10 | 0.66996 | 8.8437
29.5694 | 2018-12-13 06:20 | 0.73022 | 1.4125
29.5764 | 2018-12-13 06:30 | 0.59543 | 13.8962
29.5833 | 2018-12-13 06:40 | 0.69909 | 4.4301
29.5903 | 2018-12-13 06:50 | 0.53816 | 1.3842
29.5972 | 2018-12-13 07:00 | 0.63576 | 6.2307
29.6042 | 2018-12-13 07:10 | 0.63576 | 6.2307
29.6111 | 2018-12-13 07:20 | 0.51643 | 5.556
29.6181 | 2018-12-13 07:30 | 0.48421 | 11.1939
29.625 | 2018-12-13 07:40 | 0.39767 | 15.609
29.6319 | 2018-12-13 07:50 | 0.35336 | 2.5952
29.6389 | 2018-12-13 08:00 | 0.36309 | 358.7375
29.6458 | 2018-12-13 08:10 | 0.36309 | 358.7375
29.6528 | 2018-12-13 08:20 | 0.31317 | 4.946
29.6597 | 2018-12-13 08:30 | 0.11678 | 24.8094
29.6667 | 2018-12-13 08:40 | 0.15718 | 14.7436
29.6736 | 2018-12-13 08:50 | 0.14053 | 335.6235
29.6806 | 2018-12-13 09:00 | 0.017889 | 26.565
29.6875 | 2018-12-13 09:10 | 0.017889 | 26.565
29.6944 | 2018-12-13 09:20 | 0.055227 | 211.6755
29.7014 | 2018-12-13 09:30 | 0.12965 | 185.7546
29.7083 | 2018-12-13 09:40 | 0.23576 | 188.7831
29.7153 | 2018-12-13 09:50 | 0.17755 | 200.7827
29.7222 | 2018-12-13 10:00 | 0.28539 | 176.9872
29.7292 | 2018-12-13 10:10 | 0.28539 | 176.9872
29.7361 | 2018-12-13 10:20 | 0.33942 | 174.7597
29.7431 | 2018-12-13 10:30 | 0.41018 | 178.3235
29.75 | 2018-12-13 10:40 | 0.41 | 180.2795
29.7569 | 2018-12-13 10:50 | 0.428 | 180
29.7639 | 2018-12-13 11:00 | 0.38263 | 176.7039
29.7708 | 2018-12-13 11:10 | 0.38263 | 176.7039
29.7778 | 2018-12-13 11:20 | 0.46178 | 187.3405
29.7847 | 2018-12-13 11:30 | 0.57501 | 176.6101
29.7917 | 2018-12-13 11:40 | 0.59247 | 186.2014
29.7986 | 2018-12-13 11:50 | 0.60319 | 185.8996
29.8056 | 2018-12-13 12:00 | 0.60751 | 182.3585
29.8125 | 2018-12-13 12:10 | 0.60751 | 182.3585
29.8194 | 2018-12-13 12:20 | 0.59234 | 181.9349
29.8264 | 2018-12-13 12:30 | 0.59029 | 173.0917
29.8333 | 2018-12-13 12:40 | 0.6136 | 187.0208
29.8403 | 2018-12-13 12:50 | 0.53907 | 170.7124
29.8472 | 2018-12-13 13:00 | 0.47502 | 179.5175
29.8542 | 2018-12-13 13:10 | 0.47502 | 179.5175
29.8611 | 2018-12-13 13:20 | 0.4428 | 188.4412
29.8681 | 2018-12-13 13:30 | 0.42006 | 180.9548
29.875 | 2018-12-13 13:40 | 0.4302 | 178.2683
29.8819 | 2018-12-13 13:50 | 0.43342 | 175.3681
29.8889 | 2018-12-13 14:00 | 0.30008 | 190.561
29.8958 | 2018-12-13 14:10 | 0.30008 | 190.561
29.9028 | 2018-12-13 14:20 | 0.19765 | 184.6433
29.9097 | 2018-12-13 14:30 | 0.23602 | 158.1084
29.9167 | 2018-12-13 14:40 | 0.159 | 148.1092
29.9236 | 2018-12-13 14:50 | 0.098031 | 108.435
29.9306 | 2018-12-13 15:00 | 0.093215 | 80.7398
29.9375 | 2018-12-13 15:10 | 0.093215 | 80.7398
29.9444 | 2018-12-13 15:20 | 0.086608 | 36.076
29.9514 | 2018-12-13 15:30 | 0.17565 | 35.4998
29.9583 | 2018-12-13 15:40 | 0.30224 | 14.9558
29.9653 | 2018-12-13 15:50 | 0.35174 | 19.7743
29.9722 | 2018-12-13 16:00 | 0.41611 | 8.9869
29.9792 | 2018-12-13 16:10 | 0.41611 | 8.9869
29.9861 | 2018-12-13 16:20 | 0.41811 | 5.7651
29.9931 | 2018-12-13 16:30 | 0.50483 | 11.8887

## southern slk 0.1
SZC southern slk 0.1 |  |  | SZC intake alignment: |  |  | 8.5
Count of Direction at 2.09m above bed (deg) | Column Labels | [13 empty] | 284
Row Labels | 0-0.1 | 0.1-0.2 | 0.2-0.3 | 0.3-0.4 | 0.4-0.5 | 0.5-0.6 | 0.6-0.7 | 0.7-0.8 | 0.8-0.9 | 0.9-1 | 1-1.1 | Grand Total |  | mid bin | area m2
0-1 | 3 | 7 | 10 | 11 | 8 | 6 | 3 | 1 |  |  |  | 49 | 49 | 0.5 | 39.5252
1-2 |  | 3 | 11 | 5 | 12 | 9 | 4 |  | 1 |  |  | 45 | 45 | 1.5 | 34.6109
2-3 |  | 3 | 11 | 14 | 14 | 8 | 12 | 6 | 3 |  |  | 71 | 71 | 2.5 | 29.6861
3-4 |  | 1 | 5 | 8 | 10 | 14 | 7 | 9 | 3 | 1 |  | 58 | 58 | 3.5 | 24.7522
4-5 |  | 5 | 11 | 10 | 15 | 12 | 17 | 15 | 6 | 1 |  | 92 | 92 | 4.5 | 19.8108
5-6 | 5 |  | 3 | 10 | 14 | 22 | 22 | 16 | 7 | 2 |  | 101 | 101 | 5.5 | 14.8634
6-7 | 3 |  | 4 | 15 | 24 | 23 | 21 | 27 | 12 | 4 |  | 133 | 133 | 6.5 | 9.9115
7-8 |  | 4 | 9 | 20 | 17 | 28 | 26 | 12 | 14 | 5 |  | 135 | 135 | 7.5 | 4.9565
8-9 |  | 3 | 5 | 11 | 20 | 16 | 37 | 29 | 15 | 4 | 2 | 142 | 142 | 8.5 | 0
9-10 |  | 1 | 3 | 11 | 18 | 27 | 20 | 20 | 9 | 3 |  | 112 | 112 | 9.5 | 4.9565
10-11 | 1 | 3 | 5 | 9 | 23 | 20 | 32 | 30 | 21 | 5 | 2 | 151 | 151 | 10.5 | 9.9115
11-12 |  | 1 | 4 | 16 | 17 | 29 | 24 | 25 | 11 | 6 | 1 | 134 | 134 | 11.5 | 14.8634
12-13 | 3 | 3 | 9 | 5 | 17 | 18 | 19 | 21 | 19 | 5 |  | 119 | 119 | 12.5 | 19.8108
13-14 |  | 5 | 3 | 12 | 23 | 14 | 10 | 9 | 4 | 1 | 3 | 84 | 84 | 13.5 | 24.7522
14-15 | 1 | 2 | 7 | 6 | 5 | 14 | 10 | 13 | 9 | 2 |  | 69 | 69 | 14.5 | 29.6861
15-16 |  |  | 4 | 12 | 16 | 9 | 11 | 12 | 3 | 2 |  | 69 | 69 | 15.5 | 34.6109
16-17 |  |  | 2 | 13 | 5 | 10 | 5 | 7 | 4 |  |  | 46 | 46 | 16.5 | 39.5252
17-18 |  |  | 9 |  | 9 | 5 | 7 | 1 |  | 1 |  | 32 | 32 | 17.5 | 44.4274
18-19 | 1 | 2 | 2 | 8 | 7 | 7 | 4 | 1 | 1 |  |  | 33 | 33 | 18.5 | 49.3161
19-20 |  | 4 | 1 | 7 | 5 | 3 | 3 | 3 | 2 |  |  | 28 | 28 | 19.5 | 54.1898
20-21 |  | 2 | 1 | 6 | 3 | 4 | 1 |  |  |  |  | 17 | 17 | 20.5 | 59.0469
21-22 | 2 | 2 | 2 | 10 | 5 | 1 | [5 empty] | 22 | 22 | 21.5 | 63.8861
22-23 | 2 | 2 | 3 | 5 | 3 |  | 1 |  |  |  |  | 16 | 16 | 22.5 | 68.7058
23-24 |  | 2 | 1 |  | 3 | 2 | [5 empty] | 8 | 8 | 23.5 | 73.5046
24-25 | 1 | 4 | 6 | 1 | 2 | [6 empty] | 14 | 14 | 24.5 | 78.281
25-26 |  | 2 | 7 | 4 | 4 | [6 empty] | 17 | 17 | 25.5 | 83.0336
26-27 | 3 | 1 | 1 | 1 | [7 empty] | 6 | 6 | 26.5 | 87.7608
27-28 |  | 2 | 7 | 3 |  | 1 | [5 empty] | 13 | 13 | 27.5 | 92.4614
28-29 |  |  | 3 | 4 | [7 empty] | 7 | 7 | 28.5 | 97.1337
29-30 |  | 2 | 2 | [8 empty] | 4 | 4 | 29.5 | 101.7765
30-31 |  | 2 | 1 | 5 | 1 | [6 empty] | 9 | 9 | 30.5 | 106.3883
31-32 |  | 3 | 3 | [8 empty] | 6 | 6 | 31.5 | 110.9676
32-33 |  | 3 | 4 | 1 | [7 empty] | 8 | 8 | 32.5 | 115.5132
33-34 |  | 2 | 1 |  | 1 | [6 empty] | 4 | 4 | 33.5 | 120.0236
34-35 | 1 | 4 | 1 |  | 1 | [6 empty] | 7 | 7 | 34.5 | 124.4974
35-36 | 1 |  | 2 | [8 empty] | 3 | 3 | 35.5 | 128.9333
36-37 | 1 | 2 | [9 empty] | 3 | 3 | 36.5 | 133.3299
37-38 | 1 | 2 | 1 | [8 empty] | 4 | 4 | 37.5 | 137.6859
38-39 | 1 | 1 | 1 | [8 empty] | 3 | 3 | 38.5 | 142
39-40 |  | 2 | [9 empty] | 2 | 2 | 39.5 | 146.2708
40-41 |  | 1 | [9 empty] | 1 | 1 | 40.5 | 150.4971
41-42 |  | 1 | 1 | [8 empty] | 2 | 2 | 41.5 | 154.6775
42-43 |  | 2 | [9 empty] | 2 | 2 | 42.5 | 158.8108
43-44 | 3 | 3 | [9 empty] | 6 | 6 | 43.5 | 162.8957
44-45 |  | 2 | [9 empty] | 2 | 2 | 44.5 | 166.931
45-46 | 3 | 1 | 2 | [8 empty] | 6 | 6 | 45.5 | 170.9155
46-47 |  | 1 | [9 empty] | 1 | 1 | 46.5 | 174.8479
47-48 | 1 | [10 empty] | 1 | 1 | 47.5 | 178.727
48-49 |  | 1 | [9 empty] | 1 | 1 | 48.5 | 182.5517
49-50 | 2 | 3 | [9 empty] | 5 | 5 | 49.5 | 186.3208
51-52 |  | 3 | [9 empty] | 3 | 3 | 51.5 | 193.6875
52-53 |  | 2 | [9 empty] | 2 | 2 | 52.5 | 197.283
54-55 |  | 1 | [9 empty] | 1 | 1 | 54.5 | 204.2925
55-56 | 1 | [10 empty] | 1 | 1 | 55.5 | 207.7045
57-58 |  | 1 | [9 empty] | 1 | 1 | 57.5 | 214.3375
58-59 | 1 | [10 empty] | 1 | 1 | 58.5 | 217.5566
59-60 |  | 2 | [9 empty] | 2 | 2 | 59.5 | 220.7095
60-61 |  | 1 | [9 empty] | 1 | 1 | 60.5 | 223.7951
63-64 | 1 | [10 empty] | 1 | 1 | 63.5 | 232.6392
64-65 | 1 | [10 empty] | 1 | 1 | 64.5 | 235.4467
65-66 | 1 | [10 empty] | 1 | 1 | 65.5 | 238.1824
66-67 | 1 | 1 | [9 empty] | 2 | 2 | 66.5 | 240.8457
67-68 | 2 | [10 empty] | 2 | 2 | 67.5 | 243.4355
68-69 | 1 | 2 | [9 empty] | 3 | 3 | 68.5 | 245.9512
69-70 |  | 1 | [9 empty] | 1 | 1 | 69.5 | 248.392
71-72 | 1 | [10 empty] | 1 | 1 | 71.5 | 253.0459
72-73 |  | 1 | [9 empty] | 1 | 1 | 72.5 | 255.2575
76-77 | 5 | 1 | [9 empty] | 6 | 6 | 76.5 | 263.3202
77-78 | 1 | [10 empty] | 1 | 1 | 77.5 | 265.1368
78-79 |  | 1 | [9 empty] | 1 | 1 | 78.5 | 266.8727
81-82 |  | 1 | [9 empty] | 1 | 1 | 81.5 | 271.5906
84-85 | 1 | [10 empty] | 1 | 1 | 84.5 | 275.564
87-88 | 1 | [10 empty] | 1 | 1 | 87.5 | 278.7821
89-90 | 2 | [10 empty] | 2 | 2 | 89.5 | 280.5035
90-91 | 1 | [10 empty] | 1 | 1 | 90.5 | 281.2361
91-92 | 1 | [10 empty] | 1 | 1 | 91.5 | 281.8831
96-97 | 1 | [10 empty] | 1 | 1 | 96.5 | 283.827
101-102 | 1 | 5 | [9 empty] | 6 | 6 | 101.5 | 283.6108
102-103 | 1 | [10 empty] | 1 | 1 | 102.5 | 283.3082
104-105 | 1 | [10 empty] | 1 | 1 | 104.5 | 282.4442
109-110 | 2 | 1 | [9 empty] | 3 | 3 | 109.5 | 278.7821
111-112 | 1 | [10 empty] | 1 | 1 | 111.5 | 276.7211
112-113 | 2 | [10 empty] | 2 | 2 | 112.5 | 275.564
113-114 | 2 | [10 empty] | 2 | 2 | 113.5 | 274.3229
114-115 | 1 | 1 | [9 empty] | 2 | 2 | 114.5 | 272.9983
115-116 | 2 | [10 empty] | 2 | 2 | 115.5 | 271.5906
118-119 | 1 | [10 empty] | 1 | 1 | 118.5 | 266.8727
120-121 | 2 | 1 | [9 empty] | 3 | 3 | 120.5 | 263.3202
121-122 |  | 1 | [9 empty] | 1 | 1 | 121.5 | 261.4234
127-128 |  | 1 | [9 empty] | 1 | 1 | 127.5 | 248.392
129-130 | 1 | [10 empty] | 1 | 1 | 129.5 | 243.4355
131-132 |  | 1 | [9 empty] | 1 | 1 | 131.5 | 238.1824
132-133 | 1 | [10 empty] | 1 | 1 | 132.5 | 235.4467
133-134 |  |  | 1 | [8 empty] | 1 | 1 | 133.5 | 232.6392
136-137 | 2 | 1 | [9 empty] | 3 | 3 | 136.5 | 223.7951
138-139 |  | 2 | 1 | [8 empty] | 3 | 3 | 138.5 | 217.5566
139-140 |  | 2 | [9 empty] | 2 | 2 | 139.5 | 214.3375
140-141 | 3 | 2 | [9 empty] | 5 | 5 | 140.5 | 211.0531
141-142 | 3 | [10 empty] | 3 | 3 | 141.5 | 207.7045
142-143 |  | 3 | 2 | [8 empty] | 5 | 5 | 142.5 | 204.2925
144-145 | 1 | 1 | [9 empty] | 2 | 2 | 144.5 | 197.283
145-146 | 1 | 1 | [9 empty] | 2 | 2 | 145.5 | 193.6875
146-147 |  | 1 | [9 empty] | 1 | 1 | 146.5 | 190.0331
148-149 | 1 | 2 | 1 | [8 empty] | 4 | 4 | 148.5 | 182.5517
149-150 |  | 1 | [9 empty] | 1 | 1 | 149.5 | 178.727
150-151 |  | 2 | [9 empty] | 2 | 2 | 150.5 | 174.8479
151-152 | 5 | 1 | [9 empty] | 6 | 6 | 151.5 | 170.9155
152-153 | 3 | 4 | [9 empty] | 7 | 7 | 152.5 | 166.931
153-154 |  |  | 1 | [8 empty] | 1 | 1 | 153.5 | 162.8957
154-155 |  | 2 | 1 | [8 empty] | 3 | 3 | 154.5 | 158.8108
155-156 |  |  | 2 | [8 empty] | 2 | 2 | 155.5 | 154.6775
156-157 | 1 | 2 | [9 empty] | 3 | 3 | 156.5 | 150.4971
157-158 |  | 3 | [9 empty] | 3 | 3 | 157.5 | 146.2708
158-159 | 2 | 2 | [9 empty] | 4 | 4 | 158.5 | 142
159-160 |  | 5 | [9 empty] | 5 | 5 | 159.5 | 137.6859
160-161 | 1 | 4 | [9 empty] | 5 | 5 | 160.5 | 133.3299
161-162 | 3 |  | 1 | [8 empty] | 4 | 4 | 161.5 | 128.9333
162-163 |  | 2 | 2 | [8 empty] | 4 | 4 | 162.5 | 124.4974
163-164 |  |  | 1 | [8 empty] | 1 | 1 | 163.5 | 120.0236
164-165 |  | 1 | [9 empty] | 1 | 1 | 164.5 | 115.5132
165-166 |  |  | 1 | [8 empty] | 1 | 1 | 165.5 | 110.9676
166-167 |  |  |  | 1 | 2 | [6 empty] | 3 | 3 | 166.5 | 106.3883
167-168 | 1 | 1 | 2 | 3 | [7 empty] | 7 | 7 | 167.5 | 101.7765
168-169 |  |  | 2 | 3 | [7 empty] | 5 | 5 | 168.5 | 97.1337
169-170 | 1 | 3 | 1 | 2 | [7 empty] | 7 | 7 | 169.5 | 92.4614
170-171 |  | 3 | 1 | 2 | [7 empty] | 6 | 6 | 170.5 | 87.7608
171-172 |  | 3 | 5 | 8 | [7 empty] | 16 | 16 | 171.5 | 83.0336
172-173 | 2 | 4 | 1 | 2 | [7 empty] | 9 | 9 | 172.5 | 78.281
173-174 | 1 | 2 | 2 |  | 2 | 2 | [5 empty] | 9 | 9 | 173.5 | 73.5046
174-175 |  | 1 | 4 | 4 | 10 | 1 | 1 |  |  |  |  | 21 | 21 | 174.5 | 68.7058
175-176 |  | 4 | 4 | 2 | 6 | 2 | 1 | 3 |  |  |  | 22 | 22 | 175.5 | 63.8861
176-177 | 1 | 6 | 7 | 5 | 4 | 5 | [5 empty] | 28 | 28 | 176.5 | 59.0469
177-178 |  | 2 | 7 | 6 | 3 |  | 5 |  |  |  |  | 23 | 23 | 177.5 | 54.1898
178-179 | 1 | 2 | 8 | 2 | 6 | 4 | 2 | 1 |  |  |  | 26 | 26 | 178.5 | 49.3161
179-180 |  | 2 | 1 | 7 | 6 | 6 | 5 | 1 |  |  |  | 28 | 28 | 179.5 | 44.4274
180-181 | 3 | 1 | 5 | 5 | 21 | 12 | 8 | 2 | 2 |  |  | 59 | 59 | 180.5 | 39.5252
181-182 |  | 3 | 4 | 6 | 16 | 16 | 20 | 3 | 1 |  |  | 69 | 69 | 181.5 | 34.6109
182-183 |  | 2 | 4 | 4 | 20 | 11 | 12 | 5 | 1 |  |  | 59 | 59 | 182.5 | 29.6861
183-184 |  | 7 | 9 | 12 | 14 | 22 | 24 | 10 | 3 |  |  | 101 | 101 | 183.5 | 24.7522
184-185 |  | 4 | 6 | 15 | 18 | 21 | 15 | 2 | 3 |  |  | 84 | 84 | 184.5 | 19.8108
185-186 |  | 3 | 11 | 10 | 23 | 34 | 27 | 5 | 2 |  |  | 115 | 115 | 185.5 | 14.8634
186-187 |  | 4 | 3 | 15 | 23 | 29 | 35 | 5 |  |  |  | 114 | 114 | 186.5 | 9.9115
187-188 |  | 3 | 5 | 13 | 26 | 32 | 24 | 14 | 2 |  |  | 119 | 119 | 187.5 | 4.9565
188-189 | 1 | 2 | 6 | 19 | 13 | 29 | 34 | 21 | 4 |  |  | 129 | 129 | 188.5 | 3.4794e-14
189-190 |  |  | 5 | 4 | 18 | 35 | 19 | 14 | 3 |  |  | 98 | 98 | 189.5 | 4.9565
190-191 |  | 3 | 2 | 12 | 28 | 23 | 34 | 14 | 1 |  |  | 117 | 117 | 190.5 | 9.9115
191-192 | 2 | 2 | 5 | 11 | 19 | 15 | 29 | 6 |  |  |  | 89 | 89 | 191.5 | 14.8634
192-193 | 1 |  | 2 | 8 | 21 | 13 | 15 | 11 | 3 |  |  | 74 | 74 | 192.5 | 19.8108
193-194 |  | 2 | 2 | 15 | 15 | 16 | 12 | 8 | 1 |  |  | 71 | 71 | 193.5 | 24.7522
194-195 | 1 | 3 | 4 | 11 | 16 | 10 | 19 | 6 |  |  |  | 70 | 70 | 194.5 | 29.6861
195-196 |  | 3 | 2 | 14 | 11 | 8 | 8 | 2 |  |  |  | 48 | 48 | 195.5 | 34.6109
196-197 | 1 | 2 | 3 | 7 | 5 | 8 | 2 |  |  |  |  | 28 | 28 | 196.5 | 39.5252
197-198 |  | 3 | 5 | 10 | 8 | 8 | 2 | 2 |  |  |  | 38 | 38 | 197.5 | 44.4274
198-199 | 1 |  | 7 | 11 | 7 | 4 | 1 |  |  |  |  | 31 | 31 | 198.5 | 49.3161
199-200 | 1 | 1 | 4 | 5 | 9 | 3 | [5 empty] | 23 | 23 | 199.5 | 54.1898
200-201 | 1 | 3 | 3 | 8 | 8 | 4 | [5 empty] | 27 | 27 | 200.5 | 59.0469
201-202 | 2 | 5 | 1 | 6 | 5 | 2 | [5 empty] | 21 | 21 | 201.5 | 63.8861
202-203 | 3 | 2 | 2 | 3 | 9 | 1 | [5 empty] | 20 | 20 | 202.5 | 68.7058
203-204 | 2 | 6 | 1 | 7 | [7 empty] | 16 | 16 | 203.5 | 73.5046
204-205 |  | 2 | 1 | 5 | 5 | [6 empty] | 13 | 13 | 204.5 | 78.281
205-206 |  | 6 | 3 | 2 | 7 | 1 | [5 empty] | 19 | 19 | 205.5 | 83.0336
206-207 |  |  | 1 |  | 2 | [6 empty] | 3 | 3 | 206.5 | 87.7608
207-208 |  | 2 | 4 | 2 | 2 | [6 empty] | 10 | 10 | 207.5 | 92.4614
208-209 | 3 | 2 | 1 | 3 | 1 | [6 empty] | 10 | 10 | 208.5 | 97.1337
209-210 |  | 1 | 6 | 1 | [7 empty] | 8 | 8 | 209.5 | 101.7765
210-211 | 4 | 1 | 1 | [8 empty] | 6 | 6 | 210.5 | 106.3883
211-212 |  |  | 6 | [8 empty] | 6 | 6 | 211.5 | 110.9676
212-213 | 1 | 2 | 1 | [8 empty] | 4 | 4 | 212.5 | 115.5132
213-214 |  | 4 | 3 | 2 | [7 empty] | 9 | 9 | 213.5 | 120.0236
214-215 |  | 2 | 1 | 1 | [7 empty] | 4 | 4 | 214.5 | 124.4974
215-216 | 1 | 2 | [9 empty] | 3 | 3 | 215.5 | 128.9333
216-217 | 1 | 3 | [9 empty] | 4 | 4 | 216.5 | 133.3299
217-218 |  | 6 | 4 | [8 empty] | 10 | 10 | 217.5 | 137.6859
218-219 |  |  | 2 | [8 empty] | 2 | 2 | 218.5 | 142
219-220 | 1 | 1 | 3 | [8 empty] | 5 | 5 | 219.5 | 146.2708
221-222 |  | 1 | [9 empty] | 1 | 1 | 221.5 | 154.6775
222-223 |  |  |  | 1 | [7 empty] | 1 | 1 | 222.5 | 158.8108
223-224 |  | 2 | 1 | [8 empty] | 3 | 3 | 223.5 | 162.8957
224-225 |  | 2 | [9 empty] | 2 | 2 | 224.5 | 166.931
225-226 | 1 | 4 | [9 empty] | 5 | 5 | 225.5 | 170.9155
228-229 | 1 | 1 | [9 empty] | 2 | 2 | 228.5 | 182.5517
229-230 |  | 1 | [9 empty] | 1 | 1 | 229.5 | 186.3208
230-231 | 1 | 1 | 1 | [8 empty] | 3 | 3 | 230.5 | 190.0331
231-232 |  |  | 1 | [8 empty] | 1 | 1 | 231.5 | 193.6875
232-233 | 2 | [10 empty] | 2 | 2 | 232.5 | 197.283
233-234 | 2 | 1 | [9 empty] | 3 | 3 | 233.5 | 200.8183
234-235 | 1 | 1 | [9 empty] | 2 | 2 | 234.5 | 204.2925
235-236 | 2 | 1 | [9 empty] | 3 | 3 | 235.5 | 207.7045
236-237 |  | 3 | [9 empty] | 3 | 3 | 236.5 | 211.0531
237-238 | 1 | 1 | [9 empty] | 2 | 2 | 237.5 | 214.3375
238-239 | 1 | 1 | [9 empty] | 2 | 2 | 238.5 | 217.5566
240-241 |  | 2 | [9 empty] | 2 | 2 | 240.5 | 223.7951
241-242 | 2 |  | 2 | [8 empty] | 4 | 4 | 241.5 | 226.8125
242-243 | 1 | [10 empty] | 1 | 1 | 242.5 | 229.7608
243-244 | 2 | [10 empty] | 2 | 2 | 243.5 | 232.6392
245-246 | 1 | 2 | [9 empty] | 3 | 3 | 245.5 | 238.1824
248-249 |  | 1 | [9 empty] | 1 | 1 | 248.5 | 245.9512
249-250 | 1 | [10 empty] | 1 | 1 | 249.5 | 248.392
250-251 | 1 | 1 | [9 empty] | 2 | 2 | 250.5 | 250.7571
252-253 | 1 | [10 empty] | 1 | 1 | 252.5 | 255.2575
253-254 | 1 | [10 empty] | 1 | 1 | 253.5 | 257.3914
254-255 | 1 | [10 empty] | 1 | 1 | 254.5 | 259.4469
256-257 | 2 | [10 empty] | 2 | 2 | 256.5 | 263.3202
257-258 |  | 2 | [9 empty] | 2 | 2 | 257.5 | 265.1368
258-259 |  | 1 | [9 empty] | 1 | 1 | 258.5 | 266.8727
263-264 | 3 | 2 | [9 empty] | 5 | 5 | 263.5 | 274.3229
266-267 | 1 | [10 empty] | 1 | 1 | 266.5 | 277.7939
267-268 |  | 1 | [9 empty] | 1 | 1 | 267.5 | 278.7821
270-271 | 3 | [10 empty] | 3 | 3 | 270.5 | 281.2361
271-272 |  | 1 | [9 empty] | 1 | 1 | 271.5 | 281.8831
277-278 | 1 | [10 empty] | 1 | 1 | 277.5 | 283.9567
279-280 | 1 | [10 empty] | 1 | 1 | 279.5 | 283.9567
285-286 | 1 | [10 empty] | 1 | 1 | 285.5 | 281.8831
286-287 | 1 | 1 | [9 empty] | 2 | 2 | 286.5 | 281.2361
287-288 | 2 | 1 | [9 empty] | 3 | 3 | 287.5 | 280.5035
293-294 | 1 | 1 | [9 empty] | 2 | 2 | 293.5 | 274.3229
294-295 |  | 1 | [9 empty] | 1 | 1 | 294.5 | 272.9983
300-301 | 1 | 1 | [9 empty] | 2 | 2 | 300.5 | 263.3202
301-302 |  | 2 | [9 empty] | 2 | 2 | 301.5 | 261.4234
302-303 | 1 | [10 empty] | 1 | 1 | 302.5 | 259.4469
304-305 |  | 1 | [9 empty] | 1 | 1 | 304.5 | 255.2575
306-307 | 1 | [10 empty] | 1 | 1 | 306.5 | 250.7571
308-309 | 1 | 1 | [9 empty] | 2 | 2 | 308.5 | 245.9512
309-310 | 4 | 4 | [9 empty] | 8 | 8 | 309.5 | 243.4355
310-311 | 1 | [10 empty] | 1 | 1 | 310.5 | 240.8457
311-312 | 1 | 1 | [9 empty] | 2 | 2 | 311.5 | 238.1824
313-314 | 1 | [10 empty] | 1 | 1 | 313.5 | 232.6392
314-315 | 2 | [10 empty] | 2 | 2 | 314.5 | 229.7608
315-316 | 2 | [10 empty] | 2 | 2 | 315.5 | 226.8125
317-318 |  | 1 | [9 empty] | 1 | 1 | 317.5 | 220.7095
319-320 | 1 | 1 | [9 empty] | 2 | 2 | 319.5 | 214.3375
320-321 |  |  | 1 | [8 empty] | 1 | 1 | 320.5 | 211.0531
321-322 |  | 5 | [9 empty] | 5 | 5 | 321.5 | 207.7045
322-323 |  | 1 | [9 empty] | 1 | 1 | 322.5 | 204.2925
323-324 | 2 | [10 empty] | 2 | 2 | 323.5 | 200.8183
324-325 | 2 | [10 empty] | 2 | 2 | 324.5 | 197.283
325-326 | 1 | 2 | [9 empty] | 3 | 3 | 325.5 | 193.6875
329-330 | 2 | 2 | [9 empty] | 4 | 4 | 329.5 | 178.727
330-331 | 1 | 3 | [5 empty] | 2 |  |  |  | 6 | 6 | 330.5 | 174.8479
331-332 | 1 | 3 | [9 empty] | 4 | 4 | 331.5 | 170.9155
332-333 | 2 | 2 | [9 empty] | 4 | 4 | 332.5 | 166.931
333-334 | 2 | [10 empty] | 2 | 2 | 333.5 | 162.8957
334-335 |  | 3 | 1 | [8 empty] | 4 | 4 | 334.5 | 158.8108
335-336 | 2 | 1 | [9 empty] | 3 | 3 | 335.5 | 154.6775
336-337 | 1 | [10 empty] | 1 | 1 | 336.5 | 150.4971
337-338 | 2 | 3 | [9 empty] | 5 | 5 | 337.5 | 146.2708
338-339 |  | 2 | 1 | [8 empty] | 3 | 3 | 338.5 | 142
339-340 |  |  | 1 | [8 empty] | 1 | 1 | 339.5 | 137.6859
340-341 |  | 1 | [9 empty] | 1 | 1 | 340.5 | 133.3299
341-342 |  | 2 | 1 | [8 empty] | 3 | 3 | 341.5 | 128.9333
342-343 | 1 | [10 empty] | 1 | 1 | 342.5 | 124.4974
343-344 | 1 | 2 | 1 | [8 empty] | 4 | 4 | 343.5 | 120.0236
344-345 | 1 | 2 | 1 | [8 empty] | 4 | 4 | 344.5 | 115.5132
345-346 | 1 | 1 | [9 empty] | 2 | 2 | 345.5 | 110.9676
346-347 | 1 | 4 | 3 | 1 | [7 empty] | 9 | 9 | 346.5 | 106.3883
347-348 | 2 | 4 | 7 | [8 empty] | 13 | 13 | 347.5 | 101.7765
348-349 | 1 | 2 | 4 | 2 | [7 empty] | 9 | 9 | 348.5 | 97.1337
349-350 |  | 4 | 2 | 1 | [7 empty] | 7 | 7 | 349.5 | 92.4614
350-351 | 1 | 4 | 4 |  | 1 | [6 empty] | 10 | 10 | 350.5 | 87.7608
351-352 | 2 | 5 | 1 |  |  |  | 1 |  |  |  |  | 9 | 9 | 351.5 | 83.0336
352-353 |  | 3 | 2 |  | 1 | [6 empty] | 6 | 6 | 352.5 | 78.281
353-354 |  | 3 | 3 | 2 | 4 | [6 empty] | 12 | 12 | 353.5 | 73.5046
354-355 |  | 1 | 6 |  | 2 | [6 empty] | 9 | 9 | 354.5 | 68.7058
355-356 |  | 3 | 4 | 2 | 1 | 1 | [5 empty] | 11 | 11 | 355.5 | 63.8861
356-357 |  | 6 | 2 | 1 | 2 | [6 empty] | 11 | 11 | 356.5 | 59.0469
357-358 |  | 3 | 4 | 2 | 2 | 2 | 1 |  |  |  |  | 14 | 14 | 357.5 | 54.1898
358-359 |  | 1 | 3 | 4 | 4 | 2 | [5 empty] | 14 | 14 | 358.5 | 49.3161
359-360 |  | 2 | 6 | 5 | 4 |  |  | 2 |  |  |  | 19 | 19 | 359.5 | 44.4274
Grand Total | 227 | 435 | 428 | 558 | 732 | 684 | 652 | 396 | 170 | 42 | 8 | 4332
| 227 | 435 | 428 | 558 | 732 | 684 | 652 | 396 | 170 | 42 | 8 | 4332 | 722
"weight" speed | 0 | 0.15 | 0.25 | 0.35 | 0.45 | 0.55 | 0.65 | 0.75 | 0.85 | 0.95 | 1.05
slack weight | 0: 227; 0.35: slack area; 0.45: 228.65; 0.55: ratio; 0.65: 5.24%
|  |  |  | slack speed (intake velocity) | 0.3
Inflow = area * weight speed * count
Direction | 0-0.1 | 0.1-0.2 | 0.2-0.3 | 0.3-0.4 | 0.4-0.5 | 0.5-0.6 | 0.6-0.7 | 0.7-0.8 | 0.8-0.9 | 0.9-1 | 1-1.1 | direction total
0-1 | 0 | 41.5014 | 98.8129 | 152.1719 | 142.2906 | 130.433 | 77.0741 | 29.6439 | 0 | 0 | 0 | 671.9277
1-2 | 0 | 15.5749 | 95.18 | 60.5691 | 186.8988 | 171.3239 | 89.9883 | 0 | 29.4193 | 0 | 0 | 648.9543
2-3 | 0 | 13.3587 | 81.6367 | 145.4618 | 187.0223 | 130.6188 | 231.5515 | 133.5874 | 75.6995 | 0 | 0 | 998.9367
3-4 | 0 | 3.7128 | 30.9403 | 69.3062 | 111.385 | 190.5922 | 112.6227 | 167.0776 | 63.1182 | 23.5146 | 0 | 772.2696
4-5 | 0 | 14.8581 | 54.4798 | 69.3379 | 133.7232 | 130.7515 | 218.9098 | 222.8719 | 101.0353 | 18.8203 | 0 | 964.7878
5-6 | 0 | 0 | 11.1476 | 52.0219 | 93.6395 | 179.8473 | 212.5468 | 178.3609 | 88.4373 | 28.2405 | 0 | 844.2418
6-7 | 0 | 0 | 9.9115 | 52.0351 | 107.0437 | 125.3799 | 135.2914 | 200.707 | 101.0969 | 37.6635 | 0 | 769.1291
7-8 | 0 | 2.9739 | 11.1521 | 34.6954 | 37.9171 | 76.3298 | 83.7646 | 44.6084 | 58.9822 | 23.5433 | 0 | 373.9667
8-9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9-10 | 0 | 0.74347 | 3.7174 | 19.0825 | 40.1475 | 73.6038 | 64.4343 | 74.3473 | 37.9171 | 14.126 | 0 | 328.1192
10-11 | 0 | 4.4602 | 12.3893 | 31.2211 | 102.5836 | 109.026 | 206.1583 | 223.0078 | 176.9195 | 47.0794 | 20.8141 | 933.6593
11-12 | 0 | 2.2295 | 14.8634 | 83.2351 | 113.7051 | 237.0714 | 231.8692 | 278.689 | 138.9729 | 84.7214 | 15.6066 | 1200.9637
12-13 | 0 | 8.9149 | 44.5744 | 34.669 | 151.5529 | 196.1273 | 244.6639 | 312.0207 | 319.945 | 94.1015 | 0 | 1406.5695
13-14 | 0 | 18.5642 | 18.5642 | 103.9594 | 256.1856 | 190.5922 | 160.8895 | 167.0776 | 84.1576 | 23.5146 | 77.9695 | 1101.4743
14-15 | 0 | 8.9058 | 51.9506 | 62.3408 | 66.7937 | 228.5828 | 192.9595 | 289.4393 | 227.0985 | 56.4036 | 0 | 1184.4747
15-16 | 0 | 0 | 34.6109 | 145.3658 | 249.1984 | 171.3239 | 247.4679 | 311.498 | 88.2578 | 65.7607 | 0 | 1313.4834
16-17 | 0 | 0 | 19.7626 | 179.8395 | 88.9316 | 217.3884 | 128.4568 | 207.5071 | 134.3855 | 0 | 0 | 976.2715
17-18 | 0 | 0 | 99.9616 | 0 | 179.9309 | 122.1753 | 202.1446 | 33.3205 | 0 | 42.206 | 0 | 679.739
18-19 | 0 | 14.7948 | 24.658 | 138.085 | 155.3457 | 189.8669 | 128.2218 | 36.9871 | 41.9187 | 0 | 0 | 729.878
19-20 | 0 | 32.5139 | 13.5474 | 132.7649 | 121.9269 | 89.4131 | 105.67 | 121.9269 | 92.1226 | 0 | 0 | 709.8858
20-21 | 0 | 17.7141 | 14.7617 | 123.9985 | 79.7133 | 129.9032 | 38.3805 | 0 | 0 | 0 | 0 | 404.4714
21-22 | 0 | 19.1658 | 31.943 | 223.6013 | 143.7437 | 35.1374 | 0 | 0 | 0 | 0 | 0 | 453.5913
22-23 | 0 | 20.6117 | 51.5294 | 120.2352 | 92.7529 | 0 | 44.6588 | 0 | 0 | 0 | 0 | 329.7879
23-24 | 0 | 22.0514 | 18.3762 | 0 | 99.2312 | 80.8551 | 0 | 0 | 0 | 0 | 0 | 220.5138
24-25 | 0 | 46.9686 | 117.4215 | 27.3984 | 70.4529 | 0 | 0 | 0 | 0 | 0 | 0 | 262.2414
25-26 | 0 | 24.9101 | 145.3087 | 116.247 | 149.4604 | 0 | 0 | 0 | 0 | 0 | 0 | 435.9262
26-27 | 0 | 13.1641 | 21.9402 | 30.7163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.8206
27-28 | 0 | 27.7384 | 161.8074 | 97.0844 | 0 | 50.8537 | 0 | 0 | 0 | 0 | 0 | 337.4839
28-29 | 0 | 0 | 72.8503 | 135.9872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208.8375
29-30 | 0 | 30.5329 | 50.8882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.4212
30-31 | 0 | 31.9165 | 26.5971 | 186.1795 | 47.8747 | 0 | 0 | 0 | 0 | 0 | 0 | 292.5677
31-32 | 0 | 49.9354 | 83.2257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133.1612
32-33 | 0 | 51.9809 | 115.5132 | 40.4296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207.9238
33-34 | 0 | 36.0071 | 30.0059 | 0 | 54.0106 | 0 | 0 | 0 | 0 | 0 | 0 | 120.0236
34-35 | 0 | 74.6984 | 31.1244 | 0 | 56.0238 | 0 | 0 | 0 | 0 | 0 | 0 | 161.8466
35-36 | 0 | 0 | 64.4667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.4667
36-37 | 0 | 39.999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.999
37-38 | 0 | 41.3058 | 34.4215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.7273
38-39 | 0 | 21.3 | 35.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.8
39-40 | 0 | 43.8812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8812
40-41 | 0 | 22.5746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.5746
41-42 | 0 | 23.2016 | 38.6694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.871
42-43 | 0 | 47.6432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.6432
43-44 | 0 | 73.3031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3031
44-45 | 0 | 50.0793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.0793
45-46 | 0 | 25.6373 | 85.4577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.0951
46-47 | 0 | 26.2272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.2272
47-48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48-49 | 0 | 27.3828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.3828
49-50 | 0 | 83.8443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8443
51-52 | 0 | 87.1594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.1594
52-53 | 0 | 59.1849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.1849
54-55 | 0 | 30.6439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6439
55-56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57-58 | 0 | 32.1506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.1506
58-59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59-60 | 0 | 66.2128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.2128
60-61 | 0 | 33.5693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.5693
63-64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
64-65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
65-66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
66-67 | 0 | 36.1268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.1268
67-68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
68-69 | 0 | 73.7854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.7854
69-70 | 0 | 37.2588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.2588
71-72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72-73 | 0 | 38.2886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.2886
76-77 | 0 | 39.498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.498
77-78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78-79 | 0 | 40.0309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.0309
81-82 | 0 | 40.7386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.7386
84-85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
87-88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
89-90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90-91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91-92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
96-97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101-102 | 0 | 212.7081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212.7081
102-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104-105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109-110 | 0 | 41.8173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.8173
111-112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112-113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
113-114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
114-115 | 0 | 40.9497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.9497
115-116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
118-119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
120-121 | 0 | 39.498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.498
121-122 | 0 | 39.2135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.2135
127-128 | 0 | 37.2588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.2588
129-130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
131-132 | 0 | 35.7274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.7274
132-133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
133-134 | 0 | 0 | 58.1598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.1598
136-137 | 0 | 33.5693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.5693
138-139 | 0 | 65.267 | 54.3892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119.6561
139-140 | 0 | 64.3013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.3013
140-141 | 0 | 63.3159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63.3159
141-142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
142-143 | 0 | 91.9316 | 102.1463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194.0779
144-145 | 0 | 29.5924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.5924
145-146 | 0 | 29.0531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.0531
146-147 | 0 | 28.505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.505
148-149 | 0 | 54.7655 | 45.6379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.4034
149-150 | 0 | 26.809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.809
150-151 | 0 | 52.4544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.4544
151-152 | 0 | 25.6373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.6373
152-153 | 0 | 100.1586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.1586
153-154 | 0 | 0 | 40.7239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.7239
154-155 | 0 | 47.6432 | 39.7027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.3459
155-156 | 0 | 0 | 77.3387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.3387
156-157 | 0 | 45.1491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.1491
157-158 | 0 | 65.8219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.8219
158-159 | 0 | 42.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.6
159-160 | 0 | 103.2644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.2644
160-161 | 0 | 79.998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.998
161-162 | 0 | 0 | 32.2333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.2333
162-163 | 0 | 37.3492 | 62.2487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.5979
163-164 | 0 | 0 | 30.0059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.0059
164-165 | 0 | 17.327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.327
165-166 | 0 | 0 | 27.7419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.7419
166-167 | 0 | 0 | 0 | 37.2359 | 95.7494 | 0 | 0 | 0 | 0 | 0 | 0 | 132.9853
167-168 | 0 | 15.2665 | 50.8882 | 106.8653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173.02
168-169 | 0 | 0 | 48.5669 | 101.9904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150.5573
169-170 | 0 | 41.6076 | 23.1153 | 64.7229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129.4459
170-171 | 0 | 39.4924 | 21.9402 | 61.4326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.8652
171-172 | 0 | 37.3651 | 103.792 | 232.494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373.651
172-173 | 0 | 46.9686 | 19.5703 | 54.7967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.3356
173-174 | 0 | 22.0514 | 36.7523 | 0 | 66.1541 | 80.8551 | 0 | 0 | 0 | 0 | 0 | 205.8129
174-175 | 0 | 10.3059 | 68.7058 | 96.1881 | 309.1762 | 37.7882 | 44.6588 | 0 | 0 | 0 | 0 | 566.823
175-176 | 0 | 38.3317 | 63.8861 | 44.7203 | 172.4925 | 70.2747 | 41.526 | 143.7437 | 0 | 0 | 0 | 574.9749
176-177 | 0 | 53.1422 | 103.3321 | 103.3321 | 106.2845 | 162.379 | 0 | 0 | 0 | 0 | 0 | 528.4699
177-178 | 0 | 16.2569 | 94.8321 | 113.7985 | 73.1562 | 0 | 176.1167 | 0 | 0 | 0 | 0 | 474.1604
178-179 | 0 | 14.7948 | 98.6322 | 34.5213 | 133.1534 | 108.4954 | 64.1109 | 36.9871 | 0 | 0 | 0 | 490.695
179-180 | 0 | 13.3282 | 11.1068 | 108.8471 | 119.9539 | 146.6104 | 144.389 | 33.3205 | 0 | 0 | 0 | 577.556
180-181 | 0 | 5.9288 | 49.4065 | 69.169 | 373.5128 | 260.8661 | 205.5308 | 59.2877 | 67.1928 | 0 | 0 | 1090.8944
181-182 | 0 | 15.5749 | 34.6109 | 72.6829 | 249.1984 | 304.5759 | 449.9416 | 77.8745 | 29.4193 | 0 | 0 | 1233.8784
182-183 | 0 | 8.9058 | 29.6861 | 41.5605 | 267.1748 | 179.6008 | 231.5515 | 111.3228 | 25.2332 | 0 | 0 | 895.0354
183-184 | 0 | 25.9898 | 55.6925 | 103.9594 | 155.9391 | 299.502 | 386.1348 | 185.6417 | 63.1182 | 0 | 0 | 1275.9775
184-185 | 0 | 11.8865 | 29.7163 | 104.0069 | 160.4678 | 228.8152 | 193.1557 | 29.7163 | 50.5176 | 0 | 0 | 808.2822
185-186 | 0 | 6.6885 | 40.8744 | 52.0219 | 153.8363 | 277.9458 | 260.8529 | 55.7378 | 25.2678 | 0 | 0 | 873.2254
186-187 | 0 | 5.9469 | 7.4336 | 52.0351 | 102.5836 | 158.0877 | 225.4856 | 37.168 | 0 | 0 | 0 | 588.7405
187-188 | 0 | 2.2304 | 6.1956 | 22.552 | 57.9909 | 87.2341 | 77.3211 | 52.0431 | 8.426 | 0 | 0 | 313.9932
188-189 | 0 | 1.0438e-14 | 5.2191e-14 | 2.3138e-13 | 2.0355e-13 | 5.5497e-13 | 7.6895e-13 | 5.4801e-13 | 1.183e-13 | 0 | 0 | 2.4878e-12
189-190 | 0 | 0 | 6.1956 | 6.9391 | 40.1475 | 95.4123 | 61.2126 | 52.0431 | 12.639 | 0 | 0 | 274.5892
190-191 | 0 | 4.4602 | 4.9557 | 41.6281 | 124.8844 | 125.3799 | 219.0432 | 104.0703 | 8.4247 | 0 | 0 | 632.8465
191-192 | 0 | 4.459 | 18.5793 | 57.2241 | 127.0822 | 122.6231 | 280.1753 | 66.8854 | 0 | 0 | 0 | 677.0284
192-193 | 0 | 0 | 9.9054 | 55.4703 | 187.2124 | 141.6475 | 193.1557 | 163.4394 | 50.5176 | 0 | 0 | 801.3484
193-194 | 0 | 7.4257 | 12.3761 | 129.9492 | 167.0776 | 217.8196 | 193.0674 | 148.5134 | 21.0394 | 0 | 0 | 897.2684
194-195 | 0 | 13.3587 | 29.6861 | 114.2914 | 213.7398 | 163.2735 | 366.6231 | 133.5874 | 0 | 0 | 0 | 1034.56
195-196 | 0 | 15.5749 | 17.3054 | 169.5934 | 171.3239 | 152.2879 | 179.9766 | 51.9163 | 0 | 0 | 0 | 757.9786
196-197 | 0 | 11.8575 | 29.6439 | 96.8366 | 88.9316 | 173.9107 | 51.3827 | 0 | 0 | 0 | 0 | 452.5631
197-198 | 0 | 19.9923 | 55.5342 | 155.4959 | 159.9386 | 195.4805 | 57.7556 | 66.6411 | 0 | 0 | 0 | 710.8382
198-199 | 0 | 0 | 86.3031 | 189.8669 | 155.3457 | 108.4954 | 32.0555 | 0 | 0 | 0 | 0 | 572.0666
199-200 | 0 | 8.1285 | 54.1898 | 94.8321 | 219.4685 | 89.4131 | 0 | 0 | 0 | 0 | 0 | 466.0319
200-201 | 0 | 26.5711 | 44.2852 | 165.3314 | 212.5689 | 129.9032 | 0 | 0 | 0 | 0 | 0 | 578.6598
201-202 | 0 | 47.9146 | 15.9715 | 134.1608 | 143.7437 | 70.2747 | 0 | 0 | 0 | 0 | 0 | 412.0653
202-203 | 0 | 20.6117 | 34.3529 | 72.1411 | 278.2586 | 37.7882 | 0 | 0 | 0 | 0 | 0 | 443.1525
203-204 | 0 | 66.1541 | 18.3762 | 180.0863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 264.6166
204-205 | 0 | 23.4843 | 19.5703 | 136.9918 | 176.1323 | 0 | 0 | 0 | 0 | 0 | 0 | 356.1786
205-206 | 0 | 74.7302 | 62.2752 | 58.1235 | 261.5557 | 45.6685 | 0 | 0 | 0 | 0 | 0 | 502.3531
206-207 | 0 | 0 | 21.9402 | 0 | 78.9847 | 0 | 0 | 0 | 0 | 0 | 0 | 100.925
207-208 | 0 | 27.7384 | 92.4614 | 64.7229 | 83.2152 | 0 | 0 | 0 | 0 | 0 | 0 | 268.1379
208-209 | 0 | 29.1401 | 24.2834 | 101.9904 | 43.7102 | 0 | 0 | 0 | 0 | 0 | 0 | 199.1241
209-210 | 0 | 15.2665 | 152.6647 | 35.6218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203.553
210-211 | 0 | 15.9582 | 26.5971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.5553
211-212 | 0 | 0 | 166.4515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166.4515
212-213 | 0 | 34.654 | 28.8783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63.5323
213-214 | 0 | 72.0142 | 90.0177 | 84.0165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246.0484
214-215 | 0 | 37.3492 | 31.1244 | 43.5741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.0477
215-216 | 0 | 38.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.68
216-217 | 0 | 59.9985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9985
217-218 | 0 | 123.9173 | 137.6859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 261.6033
218-219 | 0 | 0 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71
219-220 | 0 | 21.9406 | 109.7031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131.6437
221-222 | 0 | 23.2016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.2016
222-223 | 0 | 0 | 0 | 55.5838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.5838
223-224 | 0 | 48.8687 | 40.7239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.5926
224-225 | 0 | 50.0793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.0793
225-226 | 0 | 102.5493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.5493
228-229 | 0 | 27.3828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.3828
229-230 | 0 | 27.9481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9481
230-231 | 0 | 28.505 | 47.5083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.0132
231-232 | 0 | 0 | 48.4219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.4219
232-233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
233-234 | 0 | 30.1227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.1227
234-235 | 0 | 30.6439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6439
235-236 | 0 | 31.1557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.1557
236-237 | 0 | 94.9739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.9739
237-238 | 0 | 32.1506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.1506
238-239 | 0 | 32.6335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.6335
240-241 | 0 | 67.1385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.1385
241-242 | 0 | 0 | 113.4062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.4062
242-243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
243-244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
245-246 | 0 | 71.4547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.4547
248-249 | 0 | 36.8927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.8927
249-250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
250-251 | 0 | 37.6136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.6136
252-253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
253-254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
254-255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256-257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257-258 | 0 | 79.5411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.5411
258-259 | 0 | 40.0309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.0309
263-264 | 0 | 82.2969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.2969
266-267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
267-268 | 0 | 41.8173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.8173
270-271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
271-272 | 0 | 42.2825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2825
277-278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
279-280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
285-286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
286-287 | 0 | 42.1854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1854
287-288 | 0 | 42.0755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.0755
293-294 | 0 | 41.1484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.1484
294-295 | 0 | 40.9497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.9497
300-301 | 0 | 39.498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.498
301-302 | 0 | 78.427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.427
302-303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
304-305 | 0 | 38.2886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.2886
306-307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
308-309 | 0 | 36.8927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.8927
309-310 | 0 | 146.0613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146.0613
310-311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311-312 | 0 | 35.7274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.7274
313-314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314-315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
315-316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
317-318 | 0 | 33.1064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.1064
319-320 | 0 | 32.1506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.1506
320-321 | 0 | 0 | 52.7633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.7633
321-322 | 0 | 155.7783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155.7783
322-323 | 0 | 30.6439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6439
323-324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
324-325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
325-326 | 0 | 58.1063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.1063
329-330 | 0 | 53.6181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6181
330-331 | 0 | 78.6815 | 0 | 0 | 0 | 0 | 0 | 262.2718 | 0 | 0 | 0 | 340.9533
331-332 | 0 | 76.912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.912
332-333 | 0 | 50.0793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.0793
333-334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
334-335 | 0 | 71.4649 | 39.7027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.1675
335-336 | 0 | 23.2016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.2016
336-337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
337-338 | 0 | 65.8219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.8219
338-339 | 0 | 42.6 | 35.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.1
339-340 | 0 | 0 | 34.4215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.4215
340-341 | 0 | 19.9995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.9995
341-342 | 0 | 38.68 | 32.2333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.9133
342-343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343-344 | 0 | 36.0071 | 30.0059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.013
344-345 | 0 | 34.654 | 28.8783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63.5323
345-346 | 0 | 16.6451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6451
346-347 | 0 | 63.833 | 79.7912 | 37.2359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180.8601
347-348 | 0 | 61.0659 | 178.1089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239.1748
348-349 | 0 | 29.1401 | 97.1337 | 67.9936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194.2674
349-350 | 0 | 55.4768 | 46.2307 | 32.3615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134.069
350-351 | 0 | 52.6565 | 87.7608 | 0 | 39.4924 | 0 | 0 | 0 | 0 | 0 | 0 | 179.9097
351-352 | 0 | 62.2752 | 20.7584 | 0 | 0 | 0 | 53.9718 | 0 | 0 | 0 | 0 | 137.0054
352-353 | 0 | 35.2265 | 39.1405 | 0 | 35.2265 | 0 | 0 | 0 | 0 | 0 | 0 | 109.5934
353-354 | 0 | 33.0771 | 55.1285 | 51.4532 | 132.3083 | 0 | 0 | 0 | 0 | 0 | 0 | 271.9671
354-355 | 0 | 10.3059 | 103.0587 | 0 | 61.8352 | 0 | 0 | 0 | 0 | 0 | 0 | 175.1998
355-356 | 0 | 28.7487 | 63.8861 | 44.7203 | 28.7487 | 35.1374 | 0 | 0 | 0 | 0 | 0 | 201.2412
356-357 | 0 | 53.1422 | 29.5235 | 20.6664 | 53.1422 | 0 | 0 | 0 | 0 | 0 | 0 | 156.4743
357-358 | 0 | 24.3854 | 54.1898 | 37.9328 | 48.7708 | 59.6087 | 35.2233 | 0 | 0 | 0 | 0 | 260.1108
358-359 | 0 | 7.3974 | 36.9871 | 69.0425 | 88.7689 | 54.2477 | 0 | 0 | 0 | 0 | 0 | 256.4436
359-360 | 0 | 13.3282 | 66.6411 | 77.7479 | 79.9693 | 0 | 0 | 66.6411 | 0 | 0 | 0 | 304.3276
draw excl slacks | 0: 53488.4855; 0.15: ok |  |  | 33.75 | 0.99579
slacks | 0: 15571.065
total draw | 0: 69059.5505
divisor | 0: 2054.85
Average | 0: 33.6081; 0.15: m2; 0.45: 0.28603

## southern slk 0.2
SZC southern slk 0.2 |  |  | SZC intake alignment: |  |  | 8.5
Count of Direction at 2.09m above bed (deg) | Column Labels | [13 empty] | 284
Row Labels | 0-0.1 | 0.1-0.2 | 0.2-0.3 | 0.3-0.4 | 0.4-0.5 | 0.5-0.6 | 0.6-0.7 | 0.7-0.8 | 0.8-0.9 | 0.9-1 | 1-1.1 | Grand Total |  | mid bin | area m2
0-1 | 3 | 7 | 10 | 11 | 8 | 6 | 3 | 1 |  |  |  | 49 | 49 | 0.5 | 39.5252
1-2 |  | 3 | 11 | 5 | 12 | 9 | 4 |  | 1 |  |  | 45 | 45 | 1.5 | 34.6109
2-3 |  | 3 | 11 | 14 | 14 | 8 | 12 | 6 | 3 |  |  | 71 | 71 | 2.5 | 29.6861
3-4 |  | 1 | 5 | 8 | 10 | 14 | 7 | 9 | 3 | 1 |  | 58 | 58 | 3.5 | 24.7522
4-5 |  | 5 | 11 | 10 | 15 | 12 | 17 | 15 | 6 | 1 |  | 92 | 92 | 4.5 | 19.8108
5-6 | 5 |  | 3 | 10 | 14 | 22 | 22 | 16 | 7 | 2 |  | 101 | 101 | 5.5 | 14.8634
6-7 | 3 |  | 4 | 15 | 24 | 23 | 21 | 27 | 12 | 4 |  | 133 | 133 | 6.5 | 9.9115
7-8 |  | 4 | 9 | 20 | 17 | 28 | 26 | 12 | 14 | 5 |  | 135 | 135 | 7.5 | 4.9565
8-9 |  | 3 | 5 | 11 | 20 | 16 | 37 | 29 | 15 | 4 | 2 | 142 | 142 | 8.5 | 0
9-10 |  | 1 | 3 | 11 | 18 | 27 | 20 | 20 | 9 | 3 |  | 112 | 112 | 9.5 | 4.9565
10-11 | 1 | 3 | 5 | 9 | 23 | 20 | 32 | 30 | 21 | 5 | 2 | 151 | 151 | 10.5 | 9.9115
11-12 |  | 1 | 4 | 16 | 17 | 29 | 24 | 25 | 11 | 6 | 1 | 134 | 134 | 11.5 | 14.8634
12-13 | 3 | 3 | 9 | 5 | 17 | 18 | 19 | 21 | 19 | 5 |  | 119 | 119 | 12.5 | 19.8108
13-14 |  | 5 | 3 | 12 | 23 | 14 | 10 | 9 | 4 | 1 | 3 | 84 | 84 | 13.5 | 24.7522
14-15 | 1 | 2 | 7 | 6 | 5 | 14 | 10 | 13 | 9 | 2 |  | 69 | 69 | 14.5 | 29.6861
15-16 |  |  | 4 | 12 | 16 | 9 | 11 | 12 | 3 | 2 |  | 69 | 69 | 15.5 | 34.6109
16-17 |  |  | 2 | 13 | 5 | 10 | 5 | 7 | 4 |  |  | 46 | 46 | 16.5 | 39.5252
17-18 |  |  | 9 |  | 9 | 5 | 7 | 1 |  | 1 |  | 32 | 32 | 17.5 | 44.4274
18-19 | 1 | 2 | 2 | 8 | 7 | 7 | 4 | 1 | 1 |  |  | 33 | 33 | 18.5 | 49.3161
19-20 |  | 4 | 1 | 7 | 5 | 3 | 3 | 3 | 2 |  |  | 28 | 28 | 19.5 | 54.1898
20-21 |  | 2 | 1 | 6 | 3 | 4 | 1 |  |  |  |  | 17 | 17 | 20.5 | 59.0469
21-22 | 2 | 2 | 2 | 10 | 5 | 1 | [5 empty] | 22 | 22 | 21.5 | 63.8861
22-23 | 2 | 2 | 3 | 5 | 3 |  | 1 |  |  |  |  | 16 | 16 | 22.5 | 68.7058
23-24 |  | 2 | 1 |  | 3 | 2 | [5 empty] | 8 | 8 | 23.5 | 73.5046
24-25 | 1 | 4 | 6 | 1 | 2 | [6 empty] | 14 | 14 | 24.5 | 78.281
25-26 |  | 2 | 7 | 4 | 4 | [6 empty] | 17 | 17 | 25.5 | 83.0336
26-27 | 3 | 1 | 1 | 1 | [7 empty] | 6 | 6 | 26.5 | 87.7608
27-28 |  | 2 | 7 | 3 |  | 1 | [5 empty] | 13 | 13 | 27.5 | 92.4614
28-29 |  |  | 3 | 4 | [7 empty] | 7 | 7 | 28.5 | 97.1337
29-30 |  | 2 | 2 | [8 empty] | 4 | 4 | 29.5 | 101.7765
30-31 |  | 2 | 1 | 5 | 1 | [6 empty] | 9 | 9 | 30.5 | 106.3883
31-32 |  | 3 | 3 | [8 empty] | 6 | 6 | 31.5 | 110.9676
32-33 |  | 3 | 4 | 1 | [7 empty] | 8 | 8 | 32.5 | 115.5132
33-34 |  | 2 | 1 |  | 1 | [6 empty] | 4 | 4 | 33.5 | 120.0236
34-35 | 1 | 4 | 1 |  | 1 | [6 empty] | 7 | 7 | 34.5 | 124.4974
35-36 | 1 |  | 2 | [8 empty] | 3 | 3 | 35.5 | 128.9333
36-37 | 1 | 2 | [9 empty] | 3 | 3 | 36.5 | 133.3299
37-38 | 1 | 2 | 1 | [8 empty] | 4 | 4 | 37.5 | 137.6859
38-39 | 1 | 1 | 1 | [8 empty] | 3 | 3 | 38.5 | 142
39-40 |  | 2 | [9 empty] | 2 | 2 | 39.5 | 146.2708
40-41 |  | 1 | [9 empty] | 1 | 1 | 40.5 | 150.4971
41-42 |  | 1 | 1 | [8 empty] | 2 | 2 | 41.5 | 154.6775
42-43 |  | 2 | [9 empty] | 2 | 2 | 42.5 | 158.8108
43-44 | 3 | 3 | [9 empty] | 6 | 6 | 43.5 | 162.8957
44-45 |  | 2 | [9 empty] | 2 | 2 | 44.5 | 166.931
45-46 | 3 | 1 | 2 | [8 empty] | 6 | 6 | 45.5 | 170.9155
46-47 |  | 1 | [9 empty] | 1 | 1 | 46.5 | 174.8479
47-48 | 1 | [10 empty] | 1 | 1 | 47.5 | 178.727
48-49 |  | 1 | [9 empty] | 1 | 1 | 48.5 | 182.5517
49-50 | 2 | 3 | [9 empty] | 5 | 5 | 49.5 | 186.3208
51-52 |  | 3 | [9 empty] | 3 | 3 | 51.5 | 193.6875
52-53 |  | 2 | [9 empty] | 2 | 2 | 52.5 | 197.283
54-55 |  | 1 | [9 empty] | 1 | 1 | 54.5 | 204.2925
55-56 | 1 | [10 empty] | 1 | 1 | 55.5 | 207.7045
57-58 |  | 1 | [9 empty] | 1 | 1 | 57.5 | 214.3375
58-59 | 1 | [10 empty] | 1 | 1 | 58.5 | 217.5566
59-60 |  | 2 | [9 empty] | 2 | 2 | 59.5 | 220.7095
60-61 |  | 1 | [9 empty] | 1 | 1 | 60.5 | 223.7951
63-64 | 1 | [10 empty] | 1 | 1 | 63.5 | 232.6392
64-65 | 1 | [10 empty] | 1 | 1 | 64.5 | 235.4467
65-66 | 1 | [10 empty] | 1 | 1 | 65.5 | 238.1824
66-67 | 1 | 1 | [9 empty] | 2 | 2 | 66.5 | 240.8457
67-68 | 2 | [10 empty] | 2 | 2 | 67.5 | 243.4355
68-69 | 1 | 2 | [9 empty] | 3 | 3 | 68.5 | 245.9512
69-70 |  | 1 | [9 empty] | 1 | 1 | 69.5 | 248.392
71-72 | 1 | [10 empty] | 1 | 1 | 71.5 | 253.0459
72-73 |  | 1 | [9 empty] | 1 | 1 | 72.5 | 255.2575
76-77 | 5 | 1 | [9 empty] | 6 | 6 | 76.5 | 263.3202
77-78 | 1 | [10 empty] | 1 | 1 | 77.5 | 265.1368
78-79 |  | 1 | [9 empty] | 1 | 1 | 78.5 | 266.8727
81-82 |  | 1 | [9 empty] | 1 | 1 | 81.5 | 271.5906
84-85 | 1 | [10 empty] | 1 | 1 | 84.5 | 275.564
87-88 | 1 | [10 empty] | 1 | 1 | 87.5 | 278.7821
89-90 | 2 | [10 empty] | 2 | 2 | 89.5 | 280.5035
90-91 | 1 | [10 empty] | 1 | 1 | 90.5 | 281.2361
91-92 | 1 | [10 empty] | 1 | 1 | 91.5 | 281.8831
96-97 | 1 | [10 empty] | 1 | 1 | 96.5 | 283.827
101-102 | 1 | 5 | [9 empty] | 6 | 6 | 101.5 | 283.6108
102-103 | 1 | [10 empty] | 1 | 1 | 102.5 | 283.3082
104-105 | 1 | [10 empty] | 1 | 1 | 103.5 | 282.9193
109-110 | 2 | 1 | [9 empty] | 3 | 3 | 109.5 | 278.7821
111-112 | 1 | [10 empty] | 1 | 1 | 111.5 | 276.7211
112-113 | 2 | [10 empty] | 2 | 2 | 112.5 | 275.564
113-114 | 2 | [10 empty] | 2 | 2 | 113.5 | 274.3229
114-115 | 1 | 1 | [9 empty] | 2 | 2 | 114.5 | 272.9983
115-116 | 2 | [10 empty] | 2 | 2 | 115.5 | 271.5906
118-119 | 1 | [10 empty] | 1 | 1 | 118.5 | 266.8727
120-121 | 2 | 1 | [9 empty] | 3 | 3 | 120.5 | 263.3202
121-122 |  | 1 | [9 empty] | 1 | 1 | 121.5 | 261.4234
127-128 |  | 1 | [9 empty] | 1 | 1 | 127.5 | 248.392
129-130 | 1 | [10 empty] | 1 | 1 | 129.5 | 243.4355
131-132 |  | 1 | [9 empty] | 1 | 1 | 131.5 | 238.1824
132-133 | 1 | [10 empty] | 1 | 1 | 132.5 | 235.4467
133-134 |  |  | 1 | [8 empty] | 1 | 1 | 133.5 | 232.6392
136-137 | 2 | 1 | [9 empty] | 3 | 3 | 136.5 | 223.7951
138-139 |  | 2 | 1 | [8 empty] | 3 | 3 | 138.5 | 217.5566
139-140 |  | 2 | [9 empty] | 2 | 2 | 139.5 | 214.3375
140-141 | 3 | 2 | [9 empty] | 5 | 5 | 140.5 | 211.0531
141-142 | 3 | [10 empty] | 3 | 3 | 141.5 | 207.7045
142-143 |  | 3 | 2 | [8 empty] | 5 | 5 | 142.5 | 204.2925
144-145 | 1 | 1 | [9 empty] | 2 | 2 | 144.5 | 197.283
145-146 | 1 | 1 | [9 empty] | 2 | 2 | 145.5 | 193.6875
146-147 |  | 1 | [9 empty] | 1 | 1 | 146.5 | 190.0331
148-149 | 1 | 2 | 1 | [8 empty] | 4 | 4 | 148.5 | 182.5517
149-150 |  | 1 | [9 empty] | 1 | 1 | 149.5 | 178.727
150-151 |  | 2 | [9 empty] | 2 | 2 | 150.5 | 174.8479
151-152 | 5 | 1 | [9 empty] | 6 | 6 | 151.5 | 170.9155
152-153 | 3 | 4 | [9 empty] | 7 | 7 | 152.5 | 166.931
153-154 |  |  | 1 | [8 empty] | 1 | 1 | 153.5 | 162.8957
154-155 |  | 2 | 1 | [8 empty] | 3 | 3 | 154.5 | 158.8108
155-156 |  |  | 2 | [8 empty] | 2 | 2 | 155.5 | 154.6775
156-157 | 1 | 2 | [9 empty] | 3 | 3 | 156.5 | 150.4971
157-158 |  | 3 | [9 empty] | 3 | 3 | 157.5 | 146.2708
158-159 | 2 | 2 | [9 empty] | 4 | 4 | 158.5 | 142
159-160 |  | 5 | [9 empty] | 5 | 5 | 159.5 | 137.6859
160-161 | 1 | 4 | [9 empty] | 5 | 5 | 160.5 | 133.3299
161-162 | 3 |  | 1 | [8 empty] | 4 | 4 | 161.5 | 128.9333
162-163 |  | 2 | 2 | [8 empty] | 4 | 4 | 162.5 | 124.4974
163-164 |  |  | 1 | [8 empty] | 1 | 1 | 163.5 | 120.0236
164-165 |  | 1 | [9 empty] | 1 | 1 | 164.5 | 115.5132
165-166 |  |  | 1 | [8 empty] | 1 | 1 | 165.5 | 110.9676
166-167 |  |  |  | 1 | 2 | [6 empty] | 3 | 3 | 166.5 | 106.3883
167-168 | 1 | 1 | 2 | 3 | [7 empty] | 7 | 7 | 167.5 | 101.7765
168-169 |  |  | 2 | 3 | [7 empty] | 5 | 5 | 168.5 | 97.1337
169-170 | 1 | 3 | 1 | 2 | [7 empty] | 7 | 7 | 169.5 | 92.4614
170-171 |  | 3 | 1 | 2 | [7 empty] | 6 | 6 | 170.5 | 87.7608
171-172 |  | 3 | 5 | 8 | [7 empty] | 16 | 16 | 171.5 | 83.0336
172-173 | 2 | 4 | 1 | 2 | [7 empty] | 9 | 9 | 172.5 | 78.281
173-174 | 1 | 2 | 2 |  | 2 | 2 | [5 empty] | 9 | 9 | 173.5 | 73.5046
174-175 |  | 1 | 4 | 4 | 10 | 1 | 1 |  |  |  |  | 21 | 21 | 174.5 | 68.7058
175-176 |  | 4 | 4 | 2 | 6 | 2 | 1 | 3 |  |  |  | 22 | 22 | 175.5 | 63.8861
176-177 | 1 | 6 | 7 | 5 | 4 | 5 | [5 empty] | 28 | 28 | 176.5 | 59.0469
177-178 |  | 2 | 7 | 6 | 3 |  | 5 |  |  |  |  | 23 | 23 | 177.5 | 54.1898
178-179 | 1 | 2 | 8 | 2 | 6 | 4 | 2 | 1 |  |  |  | 26 | 26 | 178.5 | 49.3161
179-180 |  | 2 | 1 | 7 | 6 | 6 | 5 | 1 |  |  |  | 28 | 28 | 179.5 | 44.4274
180-181 | 3 | 1 | 5 | 5 | 21 | 12 | 8 | 2 | 2 |  |  | 59 | 59 | 180.5 | 39.5252
181-182 |  | 3 | 4 | 6 | 16 | 16 | 20 | 3 | 1 |  |  | 69 | 69 | 181.5 | 34.6109
182-183 |  | 2 | 4 | 4 | 20 | 11 | 12 | 5 | 1 |  |  | 59 | 59 | 182.5 | 29.6861
183-184 |  | 7 | 9 | 12 | 14 | 22 | 24 | 10 | 3 |  |  | 101 | 101 | 183.5 | 24.7522
184-185 |  | 4 | 6 | 15 | 18 | 21 | 15 | 2 | 3 |  |  | 84 | 84 | 184.5 | 19.8108
185-186 |  | 3 | 11 | 10 | 23 | 34 | 27 | 5 | 2 |  |  | 115 | 115 | 185.5 | 14.8634
186-187 |  | 4 | 3 | 15 | 23 | 29 | 35 | 5 |  |  |  | 114 | 114 | 186.5 | 9.9115
187-188 |  | 3 | 5 | 13 | 26 | 32 | 24 | 14 | 2 |  |  | 119 | 119 | 187.5 | 4.9565
188-189 | 1 | 2 | 6 | 19 | 13 | 29 | 34 | 21 | 4 |  |  | 129 | 129 | 188.5 | 3.4794e-14
189-190 |  |  | 5 | 4 | 18 | 35 | 19 | 14 | 3 |  |  | 98 | 98 | 189.5 | 4.9565
190-191 |  | 3 | 2 | 12 | 28 | 23 | 34 | 14 | 1 |  |  | 117 | 117 | 190.5 | 9.9115
191-192 | 2 | 2 | 5 | 11 | 19 | 15 | 29 | 6 |  |  |  | 89 | 89 | 191.5 | 14.8634
192-193 | 1 |  | 2 | 8 | 21 | 13 | 15 | 11 | 3 |  |  | 74 | 74 | 192.5 | 19.8108
193-194 |  | 2 | 2 | 15 | 15 | 16 | 12 | 8 | 1 |  |  | 71 | 71 | 193.5 | 24.7522
194-195 | 1 | 3 | 4 | 11 | 16 | 10 | 19 | 6 |  |  |  | 70 | 70 | 194.5 | 29.6861
195-196 |  | 3 | 2 | 14 | 11 | 8 | 8 | 2 |  |  |  | 48 | 48 | 195.5 | 34.6109
196-197 | 1 | 2 | 3 | 7 | 5 | 8 | 2 |  |  |  |  | 28 | 28 | 196.5 | 39.5252
197-198 |  | 3 | 5 | 10 | 8 | 8 | 2 | 2 |  |  |  | 38 | 38 | 197.5 | 44.4274
198-199 | 1 |  | 7 | 11 | 7 | 4 | 1 |  |  |  |  | 31 | 31 | 198.5 | 49.3161
199-200 | 1 | 1 | 4 | 5 | 9 | 3 | [5 empty] | 23 | 23 | 199.5 | 54.1898
200-201 | 1 | 3 | 3 | 8 | 8 | 4 | [5 empty] | 27 | 27 | 200.5 | 59.0469
201-202 | 2 | 5 | 1 | 6 | 5 | 2 | [5 empty] | 21 | 21 | 201.5 | 63.8861
202-203 | 3 | 2 | 2 | 3 | 9 | 1 | [5 empty] | 20 | 20 | 202.5 | 68.7058
203-204 | 2 | 6 | 1 | 7 | [7 empty] | 16 | 16 | 203.5 | 73.5046
204-205 |  | 2 | 1 | 5 | 5 | [6 empty] | 13 | 13 | 204.5 | 78.281
205-206 |  | 6 | 3 | 2 | 7 | 1 | [5 empty] | 19 | 19 | 205.5 | 83.0336
206-207 |  |  | 1 |  | 2 | [6 empty] | 3 | 3 | 206.5 | 87.7608
207-208 |  | 2 | 4 | 2 | 2 | [6 empty] | 10 | 10 | 207.5 | 92.4614
208-209 | 3 | 2 | 1 | 3 | 1 | [6 empty] | 10 | 10 | 208.5 | 97.1337
209-210 |  | 1 | 6 | 1 | [7 empty] | 8 | 8 | 209.5 | 101.7765
210-211 | 4 | 1 | 1 | [8 empty] | 6 | 6 | 210.5 | 106.3883
211-212 |  |  | 6 | [8 empty] | 6 | 6 | 211.5 | 110.9676
212-213 | 1 | 2 | 1 | [8 empty] | 4 | 4 | 212.5 | 115.5132
213-214 |  | 4 | 3 | 2 | [7 empty] | 9 | 9 | 213.5 | 120.0236
214-215 |  | 2 | 1 | 1 | [7 empty] | 4 | 4 | 214.5 | 124.4974
215-216 | 1 | 2 | [9 empty] | 3 | 3 | 215.5 | 128.9333
216-217 | 1 | 3 | [9 empty] | 4 | 4 | 216.5 | 133.3299
217-218 |  | 6 | 4 | [8 empty] | 10 | 10 | 217.5 | 137.6859
218-219 |  |  | 2 | [8 empty] | 2 | 2 | 218.5 | 142
219-220 | 1 | 1 | 3 | [8 empty] | 5 | 5 | 219.5 | 146.2708
221-222 |  | 1 | [9 empty] | 1 | 1 | 221.5 | 154.6775
222-223 |  |  |  | 1 | [7 empty] | 1 | 1 | 222.5 | 158.8108
223-224 |  | 2 | 1 | [8 empty] | 3 | 3 | 223.5 | 162.8957
224-225 |  | 2 | [9 empty] | 2 | 2 | 224.5 | 166.931
225-226 | 1 | 4 | [9 empty] | 5 | 5 | 225.5 | 170.9155
228-229 | 1 | 1 | [9 empty] | 2 | 2 | 228.5 | 182.5517
229-230 |  | 1 | [9 empty] | 1 | 1 | 229.5 | 186.3208
230-231 | 1 | 1 | 1 | [8 empty] | 3 | 3 | 230.5 | 190.0331
231-232 |  |  | 1 | [8 empty] | 1 | 1 | 231.5 | 193.6875
232-233 | 2 | [10 empty] | 2 | 2 | 232.5 | 197.283
233-234 | 2 | 1 | [9 empty] | 3 | 3 | 233.5 | 200.8183
234-235 | 1 | 1 | [9 empty] | 2 | 2 | 234.5 | 204.2925
235-236 | 2 | 1 | [9 empty] | 3 | 3 | 235.5 | 207.7045
236-237 |  | 3 | [9 empty] | 3 | 3 | 236.5 | 211.0531
237-238 | 1 | 1 | [9 empty] | 2 | 2 | 237.5 | 214.3375
238-239 | 1 | 1 | [9 empty] | 2 | 2 | 238.5 | 217.5566
240-241 |  | 2 | [9 empty] | 2 | 2 | 240.5 | 223.7951
241-242 | 2 |  | 2 | [8 empty] | 4 | 4 | 241.5 | 226.8125
242-243 | 1 | [10 empty] | 1 | 1 | 242.5 | 229.7608
243-244 | 2 | [10 empty] | 2 | 2 | 243.5 | 232.6392
245-246 | 1 | 2 | [9 empty] | 3 | 3 | 245.5 | 238.1824
248-249 |  | 1 | [9 empty] | 1 | 1 | 248.5 | 245.9512
249-250 | 1 | [10 empty] | 1 | 1 | 249.5 | 248.392
250-251 | 1 | 1 | [9 empty] | 2 | 2 | 250.5 | 250.7571
252-253 | 1 | [10 empty] | 1 | 1 | 252.5 | 255.2575
253-254 | 1 | [10 empty] | 1 | 1 | 253.5 | 257.3914
254-255 | 1 | [10 empty] | 1 | 1 | 254.5 | 259.4469
256-257 | 2 | [10 empty] | 2 | 2 | 256.5 | 263.3202
257-258 |  | 2 | [9 empty] | 2 | 2 | 257.5 | 265.1368
258-259 |  | 1 | [9 empty] | 1 | 1 | 258.5 | 266.8727
263-264 | 3 | 2 | [9 empty] | 5 | 5 | 263.5 | 274.3229
266-267 | 1 | [10 empty] | 1 | 1 | 266.5 | 277.7939
267-268 |  | 1 | [9 empty] | 1 | 1 | 267.5 | 278.7821
270-271 | 3 | [10 empty] | 3 | 3 | 270.5 | 281.2361
271-272 |  | 1 | [9 empty] | 1 | 1 | 271.5 | 281.8831
277-278 | 1 | [10 empty] | 1 | 1 | 277.5 | 283.9567
279-280 | 1 | [10 empty] | 1 | 1 | 279.5 | 283.9567
285-286 | 1 | [10 empty] | 1 | 1 | 285.5 | 281.8831
286-287 | 1 | 1 | [9 empty] | 2 | 2 | 286.5 | 281.2361
287-288 | 2 | 1 | [9 empty] | 3 | 3 | 287.5 | 280.5035
293-294 | 1 | 1 | [9 empty] | 2 | 2 | 293.5 | 274.3229
294-295 |  | 1 | [9 empty] | 1 | 1 | 294.5 | 272.9983
300-301 | 1 | 1 | [9 empty] | 2 | 2 | 300.5 | 263.3202
301-302 |  | 2 | [9 empty] | 2 | 2 | 301.5 | 261.4234
302-303 | 1 | [10 empty] | 1 | 1 | 302.5 | 259.4469
304-305 |  | 1 | [9 empty] | 1 | 1 | 304.5 | 255.2575
306-307 | 1 | [10 empty] | 1 | 1 | 306.5 | 250.7571
308-309 | 1 | 1 | [9 empty] | 2 | 2 | 308.5 | 245.9512
309-310 | 4 | 4 | [9 empty] | 8 | 8 | 309.5 | 243.4355
310-311 | 1 | [10 empty] | 1 | 1 | 310.5 | 240.8457
311-312 | 1 | 1 | [9 empty] | 2 | 2 | 311.5 | 238.1824
313-314 | 1 | [10 empty] | 1 | 1 | 313.5 | 232.6392
314-315 | 2 | [10 empty] | 2 | 2 | 314.5 | 229.7608
315-316 | 2 | [10 empty] | 2 | 2 | 315.5 | 226.8125
317-318 |  | 1 | [9 empty] | 1 | 1 | 317.5 | 220.7095
319-320 | 1 | 1 | [9 empty] | 2 | 2 | 319.5 | 214.3375
320-321 |  |  | 1 | [8 empty] | 1 | 1 | 320.5 | 211.0531
321-322 |  | 5 | [9 empty] | 5 | 5 | 321.5 | 207.7045
322-323 |  | 1 | [9 empty] | 1 | 1 | 322.5 | 204.2925
323-324 | 2 | [10 empty] | 2 | 2 | 323.5 | 200.8183
324-325 | 2 | [10 empty] | 2 | 2 | 324.5 | 197.283
325-326 | 1 | 2 | [9 empty] | 3 | 3 | 325.5 | 193.6875
329-330 | 2 | 2 | [9 empty] | 4 | 4 | 329.5 | 178.727
330-331 | 1 | 3 | [5 empty] | 2 |  |  |  | 6 | 6 | 330.5 | 174.8479
331-332 | 1 | 3 | [9 empty] | 4 | 4 | 331.5 | 170.9155
332-333 | 2 | 2 | [9 empty] | 4 | 4 | 332.5 | 166.931
333-334 | 2 | [10 empty] | 2 | 2 | 333.5 | 162.8957
334-335 |  | 3 | 1 | [8 empty] | 4 | 4 | 334.5 | 158.8108
335-336 | 2 | 1 | [9 empty] | 3 | 3 | 335.5 | 154.6775
336-337 | 1 | [10 empty] | 1 | 1 | 336.5 | 150.4971
337-338 | 2 | 3 | [9 empty] | 5 | 5 | 337.5 | 146.2708
338-339 |  | 2 | 1 | [8 empty] | 3 | 3 | 338.5 | 142
339-340 |  |  | 1 | [8 empty] | 1 | 1 | 339.5 | 137.6859
340-341 |  | 1 | [9 empty] | 1 | 1 | 340.5 | 133.3299
341-342 |  | 2 | 1 | [8 empty] | 3 | 3 | 341.5 | 128.9333
342-343 | 1 | [10 empty] | 1 | 1 | 342.5 | 124.4974
343-344 | 1 | 2 | 1 | [8 empty] | 4 | 4 | 343.5 | 120.0236
344-345 | 1 | 2 | 1 | [8 empty] | 4 | 4 | 344.5 | 115.5132
345-346 | 1 | 1 | [9 empty] | 2 | 2 | 345.5 | 110.9676
346-347 | 1 | 4 | 3 | 1 | [7 empty] | 9 | 9 | 346.5 | 106.3883
347-348 | 2 | 4 | 7 | [8 empty] | 13 | 13 | 347.5 | 101.7765
348-349 | 1 | 2 | 4 | 2 | [7 empty] | 9 | 9 | 348.5 | 97.1337
349-350 |  | 4 | 2 | 1 | [7 empty] | 7 | 7 | 349.5 | 92.4614
350-351 | 1 | 4 | 4 |  | 1 | [6 empty] | 10 | 10 | 350.5 | 87.7608
351-352 | 2 | 5 | 1 |  |  |  | 1 |  |  |  |  | 9 | 9 | 351.5 | 83.0336
352-353 |  | 3 | 2 |  | 1 | [6 empty] | 6 | 6 | 352.5 | 78.281
353-354 |  | 3 | 3 | 2 | 4 | [6 empty] | 12 | 12 | 353.5 | 73.5046
354-355 |  | 1 | 6 |  | 2 | [6 empty] | 9 | 9 | 354.5 | 68.7058
355-356 |  | 3 | 4 | 2 | 1 | 1 | [5 empty] | 11 | 11 | 355.5 | 63.8861
356-357 |  | 6 | 2 | 1 | 2 | [6 empty] | 11 | 11 | 356.5 | 59.0469
357-358 |  | 3 | 4 | 2 | 2 | 2 | 1 |  |  |  |  | 14 | 14 | 357.5 | 54.1898
358-359 |  | 1 | 3 | 4 | 4 | 2 | [5 empty] | 14 | 14 | 358.5 | 49.3161
359-360 |  | 2 | 6 | 5 | 4 |  |  | 2 |  |  |  | 19 | 19 | 359.5 | 44.4274
Grand Total | 227 | 435 | 428 | 558 | 732 | 684 | 652 | 396 | 170 | 42 | 8 | 4332
| 227 | 435 | 428 | 558 | 732 | 684 | 652 | 396 | 170 | 42 | 8 | 4332 | 722
"weight" speed | 0 | 0 | 0.25 | 0.35 | 0.45 | 0.55 | 0.65 | 0.75 | 0.85 | 0.95 | 1.05
slack weight | 0: 662; 0.35: slack area; 0.45: 228.65; 0.55: ratio; 0.65: 15.28%
|  |  |  | slack speed (intake velocity) | 0.3
Inflow = area * weight speed * count
Direction | 0-0.1 | 0.1-0.2 | 0.2-0.3 | 0.3-0.4 | 0.4-0.5 | 0.5-0.6 | 0.6-0.7 | 0.7-0.8 | 0.8-0.9 | 0.9-1 | 1-1.1 | direction total
0-1 | 0 | 0 | 98.8129 | 152.1719 | 142.2906 | 130.433 | 77.0741 | 29.6439 | 0 | 0 | 0 | 630.4263 |  | southern area |  | 43.0418 | m2
1-2 | 0 | 0 | 95.18 | 60.5691 | 186.8988 | 171.3239 | 89.9883 | 0 | 29.4193 | 0 | 0 | 633.3794
2-3 | 0 | 0 | 81.6367 | 145.4618 | 187.0223 | 130.6188 | 231.5515 | 133.5874 | 75.6995 | 0 | 0 | 985.578
3-4 | 0 | 0 | 30.9403 | 69.3062 | 111.385 | 190.5922 | 112.6227 | 167.0776 | 63.1182 | 23.5146 | 0 | 768.5568
4-5 | 0 | 0 | 54.4798 | 69.3379 | 133.7232 | 130.7515 | 218.9098 | 222.8719 | 101.0353 | 18.8203 | 0 | 949.9297
5-6 | 0 | 0 | 11.1476 | 52.0219 | 93.6395 | 179.8473 | 212.5468 | 178.3609 | 88.4373 | 28.2405 | 0 | 844.2418
6-7 | 0 | 0 | 9.9115 | 52.0351 | 107.0437 | 125.3799 | 135.2914 | 200.707 | 101.0969 | 37.6635 | 0 | 769.1291
7-8 | 0 | 0 | 11.1521 | 34.6954 | 37.9171 | 76.3298 | 83.7646 | 44.6084 | 58.9822 | 23.5433 | 0 | 370.9928
8-9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9-10 | 0 | 0 | 3.7174 | 19.0825 | 40.1475 | 73.6038 | 64.4343 | 74.3473 | 37.9171 | 14.126 | 0 | 327.3757
10-11 | 0 | 0 | 12.3893 | 31.2211 | 102.5836 | 109.026 | 206.1583 | 223.0078 | 176.9195 | 47.0794 | 20.8141 | 929.1991
11-12 | 0 | 0 | 14.8634 | 83.2351 | 113.7051 | 237.0714 | 231.8692 | 278.689 | 138.9729 | 84.7214 | 15.6066 | 1198.7341
12-13 | 0 | 0 | 44.5744 | 34.669 | 151.5529 | 196.1273 | 244.6639 | 312.0207 | 319.945 | 94.1015 | 0 | 1397.6547
13-14 | 0 | 0 | 18.5642 | 103.9594 | 256.1856 | 190.5922 | 160.8895 | 167.0776 | 84.1576 | 23.5146 | 77.9695 | 1082.9101
14-15 | 0 | 0 | 51.9506 | 62.3408 | 66.7937 | 228.5828 | 192.9595 | 289.4393 | 227.0985 | 56.4036 | 0 | 1175.5689
15-16 | 0 | 0 | 34.6109 | 145.3658 | 249.1984 | 171.3239 | 247.4679 | 311.498 | 88.2578 | 65.7607 | 0 | 1313.4834
16-17 | 0 | 0 | 19.7626 | 179.8395 | 88.9316 | 217.3884 | 128.4568 | 207.5071 | 134.3855 | 0 | 0 | 976.2715
17-18 | 0 | 0 | 99.9616 | 0 | 179.9309 | 122.1753 | 202.1446 | 33.3205 | 0 | 42.206 | 0 | 679.739
18-19 | 0 | 0 | 24.658 | 138.085 | 155.3457 | 189.8669 | 128.2218 | 36.9871 | 41.9187 | 0 | 0 | 715.0832
19-20 | 0 | 0 | 13.5474 | 132.7649 | 121.9269 | 89.4131 | 105.67 | 121.9269 | 92.1226 | 0 | 0 | 677.3719
20-21 | 0 | 0 | 14.7617 | 123.9985 | 79.7133 | 129.9032 | 38.3805 | 0 | 0 | 0 | 0 | 386.7573
21-22 | 0 | 0 | 31.943 | 223.6013 | 143.7437 | 35.1374 | 0 | 0 | 0 | 0 | 0 | 434.4255
22-23 | 0 | 0 | 51.5294 | 120.2352 | 92.7529 | 0 | 44.6588 | 0 | 0 | 0 | 0 | 309.1762
23-24 | 0 | 0 | 18.3762 | 0 | 99.2312 | 80.8551 | 0 | 0 | 0 | 0 | 0 | 198.4624
24-25 | 0 | 0 | 117.4215 | 27.3984 | 70.4529 | 0 | 0 | 0 | 0 | 0 | 0 | 215.2728
25-26 | 0 | 0 | 145.3087 | 116.247 | 149.4604 | 0 | 0 | 0 | 0 | 0 | 0 | 411.0161
26-27 | 0 | 0 | 21.9402 | 30.7163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.6565
27-28 | 0 | 0 | 161.8074 | 97.0844 | 0 | 50.8537 | 0 | 0 | 0 | 0 | 0 | 309.7455
28-29 | 0 | 0 | 72.8503 | 135.9872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208.8375
29-30 | 0 | 0 | 50.8882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.8882
30-31 | 0 | 0 | 26.5971 | 186.1795 | 47.8747 | 0 | 0 | 0 | 0 | 0 | 0 | 260.6513
31-32 | 0 | 0 | 83.2257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.2257
32-33 | 0 | 0 | 115.5132 | 40.4296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155.9428
33-34 | 0 | 0 | 30.0059 | 0 | 54.0106 | 0 | 0 | 0 | 0 | 0 | 0 | 84.0165
34-35 | 0 | 0 | 31.1244 | 0 | 56.0238 | 0 | 0 | 0 | 0 | 0 | 0 | 87.1482
35-36 | 0 | 0 | 64.4667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.4667
36-37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37-38 | 0 | 0 | 34.4215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.4215
38-39 | 0 | 0 | 35.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.5
39-40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40-41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41-42 | 0 | 0 | 38.6694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.6694
42-43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43-44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44-45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45-46 | 0 | 0 | 85.4577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.4577
46-47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47-48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48-49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
49-50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51-52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
52-53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54-55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55-56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57-58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58-59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59-60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60-61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
63-64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
64-65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
65-66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
66-67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67-68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
68-69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
69-70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
71-72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72-73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
76-77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
77-78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78-79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
81-82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
84-85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
87-88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
89-90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90-91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91-92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
96-97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104-105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109-110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111-112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112-113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
113-114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
114-115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
115-116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
118-119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
120-121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
121-122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
127-128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
129-130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
131-132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
132-133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
133-134 | 0 | 0 | 58.1598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.1598
136-137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
138-139 | 0 | 0 | 54.3892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.3892
139-140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
140-141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
141-142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
142-143 | 0 | 0 | 102.1463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.1463
144-145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
145-146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
146-147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
148-149 | 0 | 0 | 45.6379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.6379
149-150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150-151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
151-152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
152-153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153-154 | 0 | 0 | 40.7239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.7239
154-155 | 0 | 0 | 39.7027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.7027
155-156 | 0 | 0 | 77.3387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.3387
156-157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157-158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
158-159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
159-160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160-161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
161-162 | 0 | 0 | 32.2333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.2333
162-163 | 0 | 0 | 62.2487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.2487
163-164 | 0 | 0 | 30.0059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.0059
164-165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
165-166 | 0 | 0 | 27.7419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.7419
166-167 | 0 | 0 | 0 | 37.2359 | 95.7494 | 0 | 0 | 0 | 0 | 0 | 0 | 132.9853
167-168 | 0 | 0 | 50.8882 | 106.8653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157.7536
168-169 | 0 | 0 | 48.5669 | 101.9904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150.5573
169-170 | 0 | 0 | 23.1153 | 64.7229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.8383
170-171 | 0 | 0 | 21.9402 | 61.4326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.3728
171-172 | 0 | 0 | 103.792 | 232.494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336.2859
172-173 | 0 | 0 | 19.5703 | 54.7967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.367
173-174 | 0 | 0 | 36.7523 | 0 | 66.1541 | 80.8551 | 0 | 0 | 0 | 0 | 0 | 183.7615
174-175 | 0 | 0 | 68.7058 | 96.1881 | 309.1762 | 37.7882 | 44.6588 | 0 | 0 | 0 | 0 | 556.5171
175-176 | 0 | 0 | 63.8861 | 44.7203 | 172.4925 | 70.2747 | 41.526 | 143.7437 | 0 | 0 | 0 | 536.6432
176-177 | 0 | 0 | 103.3321 | 103.3321 | 106.2845 | 162.379 | 0 | 0 | 0 | 0 | 0 | 475.3277
177-178 | 0 | 0 | 94.8321 | 113.7985 | 73.1562 | 0 | 176.1167 | 0 | 0 | 0 | 0 | 457.9034
178-179 | 0 | 0 | 98.6322 | 34.5213 | 133.1534 | 108.4954 | 64.1109 | 36.9871 | 0 | 0 | 0 | 475.9002
179-180 | 0 | 0 | 11.1068 | 108.8471 | 119.9539 | 146.6104 | 144.389 | 33.3205 | 0 | 0 | 0 | 564.2278
180-181 | 0 | 0 | 49.4065 | 69.169 | 373.5128 | 260.8661 | 205.5308 | 59.2877 | 67.1928 | 0 | 0 | 1084.9657
181-182 | 0 | 0 | 34.6109 | 72.6829 | 249.1984 | 304.5759 | 449.9416 | 77.8745 | 29.4193 | 0 | 0 | 1218.3035
182-183 | 0 | 0 | 29.6861 | 41.5605 | 267.1748 | 179.6008 | 231.5515 | 111.3228 | 25.2332 | 0 | 0 | 886.1296
183-184 | 0 | 0 | 55.6925 | 103.9594 | 155.9391 | 299.502 | 386.1348 | 185.6417 | 63.1182 | 0 | 0 | 1249.9877
184-185 | 0 | 0 | 29.7163 | 104.0069 | 160.4678 | 228.8152 | 193.1557 | 29.7163 | 50.5176 | 0 | 0 | 796.3957
185-186 | 0 | 0 | 40.8744 | 52.0219 | 153.8363 | 277.9458 | 260.8529 | 55.7378 | 25.2678 | 0 | 0 | 866.5369
186-187 | 0 | 0 | 7.4336 | 52.0351 | 102.5836 | 158.0877 | 225.4856 | 37.168 | 0 | 0 | 0 | 582.7937
187-188 | 0 | 0 | 6.1956 | 22.552 | 57.9909 | 87.2341 | 77.3211 | 52.0431 | 8.426 | 0 | 0 | 311.7628
188-189 | 0 | 0 | 5.2191e-14 | 2.3138e-13 | 2.0355e-13 | 5.5497e-13 | 7.6895e-13 | 5.4801e-13 | 1.183e-13 | 0 | 0 | 2.4773e-12
189-190 | 0 | 0 | 6.1956 | 6.9391 | 40.1475 | 95.4123 | 61.2126 | 52.0431 | 12.639 | 0 | 0 | 274.5892
190-191 | 0 | 0 | 4.9557 | 41.6281 | 124.8844 | 125.3799 | 219.0432 | 104.0703 | 8.4247 | 0 | 0 | 628.3864
191-192 | 0 | 0 | 18.5793 | 57.2241 | 127.0822 | 122.6231 | 280.1753 | 66.8854 | 0 | 0 | 0 | 672.5694
192-193 | 0 | 0 | 9.9054 | 55.4703 | 187.2124 | 141.6475 | 193.1557 | 163.4394 | 50.5176 | 0 | 0 | 801.3484
193-194 | 0 | 0 | 12.3761 | 129.9492 | 167.0776 | 217.8196 | 193.0674 | 148.5134 | 21.0394 | 0 | 0 | 889.8427
194-195 | 0 | 0 | 29.6861 | 114.2914 | 213.7398 | 163.2735 | 366.6231 | 133.5874 | 0 | 0 | 0 | 1021.2013
195-196 | 0 | 0 | 17.3054 | 169.5934 | 171.3239 | 152.2879 | 179.9766 | 51.9163 | 0 | 0 | 0 | 742.4037
196-197 | 0 | 0 | 29.6439 | 96.8366 | 88.9316 | 173.9107 | 51.3827 | 0 | 0 | 0 | 0 | 440.7055
197-198 | 0 | 0 | 55.5342 | 155.4959 | 159.9386 | 195.4805 | 57.7556 | 66.6411 | 0 | 0 | 0 | 690.8459
198-199 | 0 | 0 | 86.3031 | 189.8669 | 155.3457 | 108.4954 | 32.0555 | 0 | 0 | 0 | 0 | 572.0666
199-200 | 0 | 0 | 54.1898 | 94.8321 | 219.4685 | 89.4131 | 0 | 0 | 0 | 0 | 0 | 457.9034
200-201 | 0 | 0 | 44.2852 | 165.3314 | 212.5689 | 129.9032 | 0 | 0 | 0 | 0 | 0 | 552.0887
201-202 | 0 | 0 | 15.9715 | 134.1608 | 143.7437 | 70.2747 | 0 | 0 | 0 | 0 | 0 | 364.1508
202-203 | 0 | 0 | 34.3529 | 72.1411 | 278.2586 | 37.7882 | 0 | 0 | 0 | 0 | 0 | 422.5408
203-204 | 0 | 0 | 18.3762 | 180.0863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198.4624
204-205 | 0 | 0 | 19.5703 | 136.9918 | 176.1323 | 0 | 0 | 0 | 0 | 0 | 0 | 332.6943
205-206 | 0 | 0 | 62.2752 | 58.1235 | 261.5557 | 45.6685 | 0 | 0 | 0 | 0 | 0 | 427.6229
206-207 | 0 | 0 | 21.9402 | 0 | 78.9847 | 0 | 0 | 0 | 0 | 0 | 0 | 100.925
207-208 | 0 | 0 | 92.4614 | 64.7229 | 83.2152 | 0 | 0 | 0 | 0 | 0 | 0 | 240.3995
208-209 | 0 | 0 | 24.2834 | 101.9904 | 43.7102 | 0 | 0 | 0 | 0 | 0 | 0 | 169.984
209-210 | 0 | 0 | 152.6647 | 35.6218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188.2865
210-211 | 0 | 0 | 26.5971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.5971
211-212 | 0 | 0 | 166.4515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166.4515
212-213 | 0 | 0 | 28.8783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.8783
213-214 | 0 | 0 | 90.0177 | 84.0165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174.0342
214-215 | 0 | 0 | 31.1244 | 43.5741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6984
215-216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
216-217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
217-218 | 0 | 0 | 137.6859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137.6859
218-219 | 0 | 0 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71
219-220 | 0 | 0 | 109.7031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.7031
221-222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
222-223 | 0 | 0 | 0 | 55.5838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.5838
223-224 | 0 | 0 | 40.7239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.7239
224-225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
225-226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
228-229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
229-230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
230-231 | 0 | 0 | 47.5083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.5083
231-232 | 0 | 0 | 48.4219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.4219
232-233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
233-234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
234-235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
235-236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
236-237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
237-238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
238-239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
240-241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
241-242 | 0 | 0 | 113.4062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.4062
242-243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
243-244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
245-246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
248-249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
249-250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
250-251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
252-253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
253-254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
254-255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256-257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257-258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
258-259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
263-264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
266-267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
267-268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
270-271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
271-272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
277-278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
279-280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
285-286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
286-287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
287-288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
293-294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
294-295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
300-301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
301-302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
302-303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
304-305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
306-307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
308-309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
309-310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
310-311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311-312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313-314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314-315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
315-316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
317-318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
319-320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
320-321 | 0 | 0 | 52.7633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.7633
321-322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
322-323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
323-324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
324-325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
325-326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
329-330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
330-331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 262.2718 | 0 | 0 | 0 | 262.2718
331-332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
332-333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333-334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
334-335 | 0 | 0 | 39.7027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.7027
335-336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
336-337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
337-338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
338-339 | 0 | 0 | 35.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.5
339-340 | 0 | 0 | 34.4215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.4215
340-341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
341-342 | 0 | 0 | 32.2333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.2333
342-343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343-344 | 0 | 0 | 30.0059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.0059
344-345 | 0 | 0 | 28.8783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.8783
345-346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346-347 | 0 | 0 | 79.7912 | 37.2359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.0271
347-348 | 0 | 0 | 178.1089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178.1089
348-349 | 0 | 0 | 97.1337 | 67.9936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165.1273
349-350 | 0 | 0 | 46.2307 | 32.3615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.5922
350-351 | 0 | 0 | 87.7608 | 0 | 39.4924 | 0 | 0 | 0 | 0 | 0 | 0 | 127.2532
351-352 | 0 | 0 | 20.7584 | 0 | 0 | 0 | 53.9718 | 0 | 0 | 0 | 0 | 74.7302
352-353 | 0 | 0 | 39.1405 | 0 | 35.2265 | 0 | 0 | 0 | 0 | 0 | 0 | 74.367
353-354 | 0 | 0 | 55.1285 | 51.4532 | 132.3083 | 0 | 0 | 0 | 0 | 0 | 0 | 238.89
354-355 | 0 | 0 | 103.0587 | 0 | 61.8352 | 0 | 0 | 0 | 0 | 0 | 0 | 164.894
355-356 | 0 | 0 | 63.8861 | 44.7203 | 28.7487 | 35.1374 | 0 | 0 | 0 | 0 | 0 | 172.4925
356-357 | 0 | 0 | 29.5235 | 20.6664 | 53.1422 | 0 | 0 | 0 | 0 | 0 | 0 | 103.3321
357-358 | 0 | 0 | 54.1898 | 37.9328 | 48.7708 | 59.6087 | 35.2233 | 0 | 0 | 0 | 0 | 235.7254
358-359 | 0 | 0 | 36.9871 | 69.0425 | 88.7689 | 54.2477 | 0 | 0 | 0 | 0 | 0 | 249.0462
359-360 | 0 | 0 | 66.6411 | 77.7479 | 79.9693 | 0 | 0 | 66.6411 | 0 | 0 | 0 | 290.9994
draw excl slacks | 0: 45843.0803; 0: ok
slacks | 0: 45409.89
total draw | 0: 91252.9703
divisor | 0: 2120.1
Average | 0: 43.0418; 0: m2; 0.45: 0.36631

## southern slk 0.3
SZC southern slk 0.3 |  |  | SZC intake alignment: |  |  | 8.5
Count of Direction at 2.09m above bed (deg) | Column Labels | [13 empty] | 284
Row Labels | 0-0.1 | 0.1-0.2 | 0.2-0.3 | 0.3-0.4 | 0.4-0.5 | 0.5-0.6 | 0.6-0.7 | 0.7-0.8 | 0.8-0.9 | 0.9-1 | 1-1.1 | Grand Total |  | mid bin | area m2
0-1 | 3 | 7 | 10 | 11 | 8 | 6 | 3 | 1 |  |  |  | 49 | 49 | 0.5 | 39.5252
1-2 |  | 3 | 11 | 5 | 12 | 9 | 4 |  | 1 |  |  | 45 | 45 | 1.5 | 34.6109
2-3 |  | 3 | 11 | 14 | 14 | 8 | 12 | 6 | 3 |  |  | 71 | 71 | 2.5 | 29.6861
3-4 |  | 1 | 5 | 8 | 10 | 14 | 7 | 9 | 3 | 1 |  | 58 | 58 | 3.5 | 24.7522
4-5 |  | 5 | 11 | 10 | 15 | 12 | 17 | 15 | 6 | 1 |  | 92 | 92 | 4.5 | 19.8108
5-6 | 5 |  | 3 | 10 | 14 | 22 | 22 | 16 | 7 | 2 |  | 101 | 101 | 5.5 | 14.8634
6-7 | 3 |  | 4 | 15 | 24 | 23 | 21 | 27 | 12 | 4 |  | 133 | 133 | 6.5 | 9.9115
7-8 |  | 4 | 9 | 20 | 17 | 28 | 26 | 12 | 14 | 5 |  | 135 | 135 | 7.5 | 4.9565
8-9 |  | 3 | 5 | 11 | 20 | 16 | 37 | 29 | 15 | 4 | 2 | 142 | 142 | 8.5 | 0
9-10 |  | 1 | 3 | 11 | 18 | 27 | 20 | 20 | 9 | 3 |  | 112 | 112 | 9.5 | 4.9565
10-11 | 1 | 3 | 5 | 9 | 23 | 20 | 32 | 30 | 21 | 5 | 2 | 151 | 151 | 10.5 | 9.9115
11-12 |  | 1 | 4 | 16 | 17 | 29 | 24 | 25 | 11 | 6 | 1 | 134 | 134 | 11.5 | 14.8634
12-13 | 3 | 3 | 9 | 5 | 17 | 18 | 19 | 21 | 19 | 5 |  | 119 | 119 | 12.5 | 19.8108
13-14 |  | 5 | 3 | 12 | 23 | 14 | 10 | 9 | 4 | 1 | 3 | 84 | 84 | 13.5 | 24.7522
14-15 | 1 | 2 | 7 | 6 | 5 | 14 | 10 | 13 | 9 | 2 |  | 69 | 69 | 14.5 | 29.6861
15-16 |  |  | 4 | 12 | 16 | 9 | 11 | 12 | 3 | 2 |  | 69 | 69 | 15.5 | 34.6109
16-17 |  |  | 2 | 13 | 5 | 10 | 5 | 7 | 4 |  |  | 46 | 46 | 16.5 | 39.5252
17-18 |  |  | 9 |  | 9 | 5 | 7 | 1 |  | 1 |  | 32 | 32 | 17.5 | 44.4274
18-19 | 1 | 2 | 2 | 8 | 7 | 7 | 4 | 1 | 1 |  |  | 33 | 33 | 18.5 | 49.3161
19-20 |  | 4 | 1 | 7 | 5 | 3 | 3 | 3 | 2 |  |  | 28 | 28 | 19.5 | 54.1898
20-21 |  | 2 | 1 | 6 | 3 | 4 | 1 |  |  |  |  | 17 | 17 | 20.5 | 59.0469
21-22 | 2 | 2 | 2 | 10 | 5 | 1 | [5 empty] | 22 | 22 | 21.5 | 63.8861
22-23 | 2 | 2 | 3 | 5 | 3 |  | 1 |  |  |  |  | 16 | 16 | 22.5 | 68.7058
23-24 |  | 2 | 1 |  | 3 | 2 | [5 empty] | 8 | 8 | 23.5 | 73.5046
24-25 | 1 | 4 | 6 | 1 | 2 | [6 empty] | 14 | 14 | 24.5 | 78.281
25-26 |  | 2 | 7 | 4 | 4 | [6 empty] | 17 | 17 | 25.5 | 83.0336
26-27 | 3 | 1 | 1 | 1 | [7 empty] | 6 | 6 | 26.5 | 87.7608
27-28 |  | 2 | 7 | 3 |  | 1 | [5 empty] | 13 | 13 | 27.5 | 92.4614
28-29 |  |  | 3 | 4 | [7 empty] | 7 | 7 | 28.5 | 97.1337
29-30 |  | 2 | 2 | [8 empty] | 4 | 4 | 29.5 | 101.7765
30-31 |  | 2 | 1 | 5 | 1 | [6 empty] | 9 | 9 | 30.5 | 106.3883
31-32 |  | 3 | 3 | [8 empty] | 6 | 6 | 31.5 | 110.9676
32-33 |  | 3 | 4 | 1 | [7 empty] | 8 | 8 | 32.5 | 115.5132
33-34 |  | 2 | 1 |  | 1 | [6 empty] | 4 | 4 | 33.5 | 120.0236
34-35 | 1 | 4 | 1 |  | 1 | [6 empty] | 7 | 7 | 34.5 | 124.4974
35-36 | 1 |  | 2 | [8 empty] | 3 | 3 | 35.5 | 128.9333
36-37 | 1 | 2 | [9 empty] | 3 | 3 | 36.5 | 133.3299
37-38 | 1 | 2 | 1 | [8 empty] | 4 | 4 | 37.5 | 137.6859
38-39 | 1 | 1 | 1 | [8 empty] | 3 | 3 | 38.5 | 142
39-40 |  | 2 | [9 empty] | 2 | 2 | 39.5 | 146.2708
40-41 |  | 1 | [9 empty] | 1 | 1 | 40.5 | 150.4971
41-42 |  | 1 | 1 | [8 empty] | 2 | 2 | 41.5 | 154.6775
42-43 |  | 2 | [9 empty] | 2 | 2 | 42.5 | 158.8108
43-44 | 3 | 3 | [9 empty] | 6 | 6 | 43.5 | 162.8957
44-45 |  | 2 | [9 empty] | 2 | 2 | 44.5 | 166.931
45-46 | 3 | 1 | 2 | [8 empty] | 6 | 6 | 45.5 | 170.9155
46-47 |  | 1 | [9 empty] | 1 | 1 | 46.5 | 174.8479
47-48 | 1 | [10 empty] | 1 | 1 | 47.5 | 178.727
48-49 |  | 1 | [9 empty] | 1 | 1 | 48.5 | 182.5517
49-50 | 2 | 3 | [9 empty] | 5 | 5 | 49.5 | 186.3208
51-52 |  | 3 | [9 empty] | 3 | 3 | 51.5 | 193.6875
52-53 |  | 2 | [9 empty] | 2 | 2 | 52.5 | 197.283
54-55 |  | 1 | [9 empty] | 1 | 1 | 54.5 | 204.2925
55-56 | 1 | [10 empty] | 1 | 1 | 55.5 | 207.7045
57-58 |  | 1 | [9 empty] | 1 | 1 | 57.5 | 214.3375
58-59 | 1 | [10 empty] | 1 | 1 | 58.5 | 217.5566
59-60 |  | 2 | [9 empty] | 2 | 2 | 59.5 | 220.7095
60-61 |  | 1 | [9 empty] | 1 | 1 | 60.5 | 223.7951
63-64 | 1 | [10 empty] | 1 | 1 | 63.5 | 232.6392
64-65 | 1 | [10 empty] | 1 | 1 | 64.5 | 235.4467
65-66 | 1 | [10 empty] | 1 | 1 | 65.5 | 238.1824
66-67 | 1 | 1 | [9 empty] | 2 | 2 | 66.5 | 240.8457
67-68 | 2 | [10 empty] | 2 | 2 | 67.5 | 243.4355
68-69 | 1 | 2 | [9 empty] | 3 | 3 | 68.5 | 245.9512
69-70 |  | 1 | [9 empty] | 1 | 1 | 69.5 | 248.392
71-72 | 1 | [10 empty] | 1 | 1 | 71.5 | 253.0459
72-73 |  | 1 | [9 empty] | 1 | 1 | 72.5 | 255.2575
76-77 | 5 | 1 | [9 empty] | 6 | 6 | 76.5 | 263.3202
77-78 | 1 | [10 empty] | 1 | 1 | 77.5 | 265.1368
78-79 |  | 1 | [9 empty] | 1 | 1 | 78.5 | 266.8727
81-82 |  | 1 | [9 empty] | 1 | 1 | 81.5 | 271.5906
84-85 | 1 | [10 empty] | 1 | 1 | 84.5 | 275.564
87-88 | 1 | [10 empty] | 1 | 1 | 87.5 | 278.7821
89-90 | 2 | [10 empty] | 2 | 2 | 89.5 | 280.5035
90-91 | 1 | [10 empty] | 1 | 1 | 90.5 | 281.2361
91-92 | 1 | [10 empty] | 1 | 1 | 91.5 | 281.8831
96-97 | 1 | [10 empty] | 1 | 1 | 96.5 | 283.827
101-102 | 1 | 5 | [9 empty] | 6 | 6 | 101.5 | 283.6108
102-103 | 1 | [10 empty] | 1 | 1 | 102.5 | 283.3082
104-105 | 1 | [10 empty] | 1 | 1 | 103.5 | 282.9193
109-110 | 2 | 1 | [9 empty] | 3 | 3 | 109.5 | 278.7821
111-112 | 1 | [10 empty] | 1 | 1 | 111.5 | 276.7211
112-113 | 2 | [10 empty] | 2 | 2 | 112.5 | 275.564
113-114 | 2 | [10 empty] | 2 | 2 | 113.5 | 274.3229
114-115 | 1 | 1 | [9 empty] | 2 | 2 | 114.5 | 272.9983
115-116 | 2 | [10 empty] | 2 | 2 | 115.5 | 271.5906
118-119 | 1 | [10 empty] | 1 | 1 | 118.5 | 266.8727
120-121 | 2 | 1 | [9 empty] | 3 | 3 | 120.5 | 263.3202
121-122 |  | 1 | [9 empty] | 1 | 1 | 121.5 | 261.4234
127-128 |  | 1 | [9 empty] | 1 | 1 | 127.5 | 248.392
129-130 | 1 | [10 empty] | 1 | 1 | 129.5 | 243.4355
131-132 |  | 1 | [9 empty] | 1 | 1 | 131.5 | 238.1824
132-133 | 1 | [10 empty] | 1 | 1 | 132.5 | 235.4467
133-134 |  |  | 1 | [8 empty] | 1 | 1 | 133.5 | 232.6392
136-137 | 2 | 1 | [9 empty] | 3 | 3 | 136.5 | 223.7951
138-139 |  | 2 | 1 | [8 empty] | 3 | 3 | 138.5 | 217.5566
139-140 |  | 2 | [9 empty] | 2 | 2 | 139.5 | 214.3375
140-141 | 3 | 2 | [9 empty] | 5 | 5 | 140.5 | 211.0531
141-142 | 3 | [10 empty] | 3 | 3 | 141.5 | 207.7045
142-143 |  | 3 | 2 | [8 empty] | 5 | 5 | 142.5 | 204.2925
144-145 | 1 | 1 | [9 empty] | 2 | 2 | 144.5 | 197.283
145-146 | 1 | 1 | [9 empty] | 2 | 2 | 145.5 | 193.6875
146-147 |  | 1 | [9 empty] | 1 | 1 | 146.5 | 190.0331
148-149 | 1 | 2 | 1 | [8 empty] | 4 | 4 | 148.5 | 182.5517
149-150 |  | 1 | [9 empty] | 1 | 1 | 149.5 | 178.727
150-151 |  | 2 | [9 empty] | 2 | 2 | 150.5 | 174.8479
151-152 | 5 | 1 | [9 empty] | 6 | 6 | 151.5 | 170.9155
152-153 | 3 | 4 | [9 empty] | 7 | 7 | 152.5 | 166.931
153-154 |  |  | 1 | [8 empty] | 1 | 1 | 153.5 | 162.8957
154-155 |  | 2 | 1 | [8 empty] | 3 | 3 | 154.5 | 158.8108
155-156 |  |  | 2 | [8 empty] | 2 | 2 | 155.5 | 154.6775
156-157 | 1 | 2 | [9 empty] | 3 | 3 | 156.5 | 150.4971
157-158 |  | 3 | [9 empty] | 3 | 3 | 157.5 | 146.2708
158-159 | 2 | 2 | [9 empty] | 4 | 4 | 158.5 | 142
159-160 |  | 5 | [9 empty] | 5 | 5 | 159.5 | 137.6859
160-161 | 1 | 4 | [9 empty] | 5 | 5 | 160.5 | 133.3299
161-162 | 3 |  | 1 | [8 empty] | 4 | 4 | 161.5 | 128.9333
162-163 |  | 2 | 2 | [8 empty] | 4 | 4 | 162.5 | 124.4974
163-164 |  |  | 1 | [8 empty] | 1 | 1 | 163.5 | 120.0236
164-165 |  | 1 | [9 empty] | 1 | 1 | 164.5 | 115.5132
165-166 |  |  | 1 | [8 empty] | 1 | 1 | 165.5 | 110.9676
166-167 |  |  |  | 1 | 2 | [6 empty] | 3 | 3 | 166.5 | 106.3883
167-168 | 1 | 1 | 2 | 3 | [7 empty] | 7 | 7 | 167.5 | 101.7765
168-169 |  |  | 2 | 3 | [7 empty] | 5 | 5 | 168.5 | 97.1337
169-170 | 1 | 3 | 1 | 2 | [7 empty] | 7 | 7 | 169.5 | 92.4614
170-171 |  | 3 | 1 | 2 | [7 empty] | 6 | 6 | 170.5 | 87.7608
171-172 |  | 3 | 5 | 8 | [7 empty] | 16 | 16 | 171.5 | 83.0336
172-173 | 2 | 4 | 1 | 2 | [7 empty] | 9 | 9 | 172.5 | 78.281
173-174 | 1 | 2 | 2 |  | 2 | 2 | [5 empty] | 9 | 9 | 173.5 | 73.5046
174-175 |  | 1 | 4 | 4 | 10 | 1 | 1 |  |  |  |  | 21 | 21 | 174.5 | 68.7058
175-176 |  | 4 | 4 | 2 | 6 | 2 | 1 | 3 |  |  |  | 22 | 22 | 175.5 | 63.8861
176-177 | 1 | 6 | 7 | 5 | 4 | 5 | [5 empty] | 28 | 28 | 176.5 | 59.0469
177-178 |  | 2 | 7 | 6 | 3 |  | 5 |  |  |  |  | 23 | 23 | 177.5 | 54.1898
178-179 | 1 | 2 | 8 | 2 | 6 | 4 | 2 | 1 |  |  |  | 26 | 26 | 178.5 | 49.3161
179-180 |  | 2 | 1 | 7 | 6 | 6 | 5 | 1 |  |  |  | 28 | 28 | 179.5 | 44.4274
180-181 | 3 | 1 | 5 | 5 | 21 | 12 | 8 | 2 | 2 |  |  | 59 | 59 | 180.5 | 39.5252
181-182 |  | 3 | 4 | 6 | 16 | 16 | 20 | 3 | 1 |  |  | 69 | 69 | 181.5 | 34.6109
182-183 |  | 2 | 4 | 4 | 20 | 11 | 12 | 5 | 1 |  |  | 59 | 59 | 182.5 | 29.6861
183-184 |  | 7 | 9 | 12 | 14 | 22 | 24 | 10 | 3 |  |  | 101 | 101 | 183.5 | 24.7522
184-185 |  | 4 | 6 | 15 | 18 | 21 | 15 | 2 | 3 |  |  | 84 | 84 | 184.5 | 19.8108
185-186 |  | 3 | 11 | 10 | 23 | 34 | 27 | 5 | 2 |  |  | 115 | 115 | 185.5 | 14.8634
186-187 |  | 4 | 3 | 15 | 23 | 29 | 35 | 5 |  |  |  | 114 | 114 | 186.5 | 9.9115
187-188 |  | 3 | 5 | 13 | 26 | 32 | 24 | 14 | 2 |  |  | 119 | 119 | 187.5 | 4.9565
188-189 | 1 | 2 | 6 | 19 | 13 | 29 | 34 | 21 | 4 |  |  | 129 | 129 | 188.5 | 3.4794e-14
189-190 |  |  | 5 | 4 | 18 | 35 | 19 | 14 | 3 |  |  | 98 | 98 | 189.5 | 4.9565
190-191 |  | 3 | 2 | 12 | 28 | 23 | 34 | 14 | 1 |  |  | 117 | 117 | 190.5 | 9.9115
191-192 | 2 | 2 | 5 | 11 | 19 | 15 | 29 | 6 |  |  |  | 89 | 89 | 191.5 | 14.8634
192-193 | 1 |  | 2 | 8 | 21 | 13 | 15 | 11 | 3 |  |  | 74 | 74 | 192.5 | 19.8108
193-194 |  | 2 | 2 | 15 | 15 | 16 | 12 | 8 | 1 |  |  | 71 | 71 | 193.5 | 24.7522
194-195 | 1 | 3 | 4 | 11 | 16 | 10 | 19 | 6 |  |  |  | 70 | 70 | 194.5 | 29.6861
195-196 |  | 3 | 2 | 14 | 11 | 8 | 8 | 2 |  |  |  | 48 | 48 | 195.5 | 34.6109
196-197 | 1 | 2 | 3 | 7 | 5 | 8 | 2 |  |  |  |  | 28 | 28 | 196.5 | 39.5252
197-198 |  | 3 | 5 | 10 | 8 | 8 | 2 | 2 |  |  |  | 38 | 38 | 197.5 | 44.4274
198-199 | 1 |  | 7 | 11 | 7 | 4 | 1 |  |  |  |  | 31 | 31 | 198.5 | 49.3161
199-200 | 1 | 1 | 4 | 5 | 9 | 3 | [5 empty] | 23 | 23 | 199.5 | 54.1898
200-201 | 1 | 3 | 3 | 8 | 8 | 4 | [5 empty] | 27 | 27 | 200.5 | 59.0469
201-202 | 2 | 5 | 1 | 6 | 5 | 2 | [5 empty] | 21 | 21 | 201.5 | 63.8861
202-203 | 3 | 2 | 2 | 3 | 9 | 1 | [5 empty] | 20 | 20 | 202.5 | 68.7058
203-204 | 2 | 6 | 1 | 7 | [7 empty] | 16 | 16 | 203.5 | 73.5046
204-205 |  | 2 | 1 | 5 | 5 | [6 empty] | 13 | 13 | 204.5 | 78.281
205-206 |  | 6 | 3 | 2 | 7 | 1 | [5 empty] | 19 | 19 | 205.5 | 83.0336
206-207 |  |  | 1 |  | 2 | [6 empty] | 3 | 3 | 206.5 | 87.7608
207-208 |  | 2 | 4 | 2 | 2 | [6 empty] | 10 | 10 | 207.5 | 92.4614
208-209 | 3 | 2 | 1 | 3 | 1 | [6 empty] | 10 | 10 | 208.5 | 97.1337
209-210 |  | 1 | 6 | 1 | [7 empty] | 8 | 8 | 209.5 | 101.7765
210-211 | 4 | 1 | 1 | [8 empty] | 6 | 6 | 210.5 | 106.3883
211-212 |  |  | 6 | [8 empty] | 6 | 6 | 211.5 | 110.9676
212-213 | 1 | 2 | 1 | [8 empty] | 4 | 4 | 212.5 | 115.5132
213-214 |  | 4 | 3 | 2 | [7 empty] | 9 | 9 | 213.5 | 120.0236
214-215 |  | 2 | 1 | 1 | [7 empty] | 4 | 4 | 214.5 | 124.4974
215-216 | 1 | 2 | [9 empty] | 3 | 3 | 215.5 | 128.9333
216-217 | 1 | 3 | [9 empty] | 4 | 4 | 216.5 | 133.3299
217-218 |  | 6 | 4 | [8 empty] | 10 | 10 | 217.5 | 137.6859
218-219 |  |  | 2 | [8 empty] | 2 | 2 | 218.5 | 142
219-220 | 1 | 1 | 3 | [8 empty] | 5 | 5 | 219.5 | 146.2708
221-222 |  | 1 | [9 empty] | 1 | 1 | 221.5 | 154.6775
222-223 |  |  |  | 1 | [7 empty] | 1 | 1 | 222.5 | 158.8108
223-224 |  | 2 | 1 | [8 empty] | 3 | 3 | 223.5 | 162.8957
224-225 |  | 2 | [9 empty] | 2 | 2 | 224.5 | 166.931
225-226 | 1 | 4 | [9 empty] | 5 | 5 | 225.5 | 170.9155
228-229 | 1 | 1 | [9 empty] | 2 | 2 | 228.5 | 182.5517
229-230 |  | 1 | [9 empty] | 1 | 1 | 229.5 | 186.3208
230-231 | 1 | 1 | 1 | [8 empty] | 3 | 3 | 230.5 | 190.0331
231-232 |  |  | 1 | [8 empty] | 1 | 1 | 231.5 | 193.6875
232-233 | 2 | [10 empty] | 2 | 2 | 232.5 | 197.283
233-234 | 2 | 1 | [9 empty] | 3 | 3 | 233.5 | 200.8183
234-235 | 1 | 1 | [9 empty] | 2 | 2 | 234.5 | 204.2925
235-236 | 2 | 1 | [9 empty] | 3 | 3 | 235.5 | 207.7045
236-237 |  | 3 | [9 empty] | 3 | 3 | 236.5 | 211.0531
237-238 | 1 | 1 | [9 empty] | 2 | 2 | 237.5 | 214.3375
238-239 | 1 | 1 | [9 empty] | 2 | 2 | 238.5 | 217.5566
240-241 |  | 2 | [9 empty] | 2 | 2 | 240.5 | 223.7951
241-242 | 2 |  | 2 | [8 empty] | 4 | 4 | 241.5 | 226.8125
242-243 | 1 | [10 empty] | 1 | 1 | 242.5 | 229.7608
243-244 | 2 | [10 empty] | 2 | 2 | 243.5 | 232.6392
245-246 | 1 | 2 | [9 empty] | 3 | 3 | 245.5 | 238.1824
248-249 |  | 1 | [9 empty] | 1 | 1 | 248.5 | 245.9512
249-250 | 1 | [10 empty] | 1 | 1 | 249.5 | 248.392
250-251 | 1 | 1 | [9 empty] | 2 | 2 | 250.5 | 250.7571
252-253 | 1 | [10 empty] | 1 | 1 | 252.5 | 255.2575
253-254 | 1 | [10 empty] | 1 | 1 | 253.5 | 257.3914
254-255 | 1 | [10 empty] | 1 | 1 | 254.5 | 259.4469
256-257 | 2 | [10 empty] | 2 | 2 | 256.5 | 263.3202
257-258 |  | 2 | [9 empty] | 2 | 2 | 257.5 | 265.1368
258-259 |  | 1 | [9 empty] | 1 | 1 | 258.5 | 266.8727
263-264 | 3 | 2 | [9 empty] | 5 | 5 | 263.5 | 274.3229
266-267 | 1 | [10 empty] | 1 | 1 | 266.5 | 277.7939
267-268 |  | 1 | [9 empty] | 1 | 1 | 267.5 | 278.7821
270-271 | 3 | [10 empty] | 3 | 3 | 270.5 | 281.2361
271-272 |  | 1 | [9 empty] | 1 | 1 | 271.5 | 281.8831
277-278 | 1 | [10 empty] | 1 | 1 | 277.5 | 283.9567
279-280 | 1 | [10 empty] | 1 | 1 | 279.5 | 283.9567
285-286 | 1 | [10 empty] | 1 | 1 | 285.5 | 281.8831
286-287 | 1 | 1 | [9 empty] | 2 | 2 | 286.5 | 281.2361
287-288 | 2 | 1 | [9 empty] | 3 | 3 | 287.5 | 280.5035
293-294 | 1 | 1 | [9 empty] | 2 | 2 | 293.5 | 274.3229
294-295 |  | 1 | [9 empty] | 1 | 1 | 294.5 | 272.9983
300-301 | 1 | 1 | [9 empty] | 2 | 2 | 300.5 | 263.3202
301-302 |  | 2 | [9 empty] | 2 | 2 | 301.5 | 261.4234
302-303 | 1 | [10 empty] | 1 | 1 | 302.5 | 259.4469
304-305 |  | 1 | [9 empty] | 1 | 1 | 304.5 | 255.2575
306-307 | 1 | [10 empty] | 1 | 1 | 306.5 | 250.7571
308-309 | 1 | 1 | [9 empty] | 2 | 2 | 308.5 | 245.9512
309-310 | 4 | 4 | [9 empty] | 8 | 8 | 309.5 | 243.4355
310-311 | 1 | [10 empty] | 1 | 1 | 310.5 | 240.8457
311-312 | 1 | 1 | [9 empty] | 2 | 2 | 311.5 | 238.1824
313-314 | 1 | [10 empty] | 1 | 1 | 313.5 | 232.6392
314-315 | 2 | [10 empty] | 2 | 2 | 314.5 | 229.7608
315-316 | 2 | [10 empty] | 2 | 2 | 315.5 | 226.8125
317-318 |  | 1 | [9 empty] | 1 | 1 | 317.5 | 220.7095
319-320 | 1 | 1 | [9 empty] | 2 | 2 | 319.5 | 214.3375
320-321 |  |  | 1 | [8 empty] | 1 | 1 | 320.5 | 211.0531
321-322 |  | 5 | [9 empty] | 5 | 5 | 321.5 | 207.7045
322-323 |  | 1 | [9 empty] | 1 | 1 | 322.5 | 204.2925
323-324 | 2 | [10 empty] | 2 | 2 | 323.5 | 200.8183
324-325 | 2 | [10 empty] | 2 | 2 | 324.5 | 197.283
325-326 | 1 | 2 | [9 empty] | 3 | 3 | 325.5 | 193.6875
329-330 | 2 | 2 | [9 empty] | 4 | 4 | 329.5 | 178.727
330-331 | 1 | 3 | [5 empty] | 2 |  |  |  | 6 | 6 | 330.5 | 174.8479
331-332 | 1 | 3 | [9 empty] | 4 | 4 | 331.5 | 170.9155
332-333 | 2 | 2 | [9 empty] | 4 | 4 | 332.5 | 166.931
333-334 | 2 | [10 empty] | 2 | 2 | 333.5 | 162.8957
334-335 |  | 3 | 1 | [8 empty] | 4 | 4 | 334.5 | 158.8108
335-336 | 2 | 1 | [9 empty] | 3 | 3 | 335.5 | 154.6775
336-337 | 1 | [10 empty] | 1 | 1 | 336.5 | 150.4971
337-338 | 2 | 3 | [9 empty] | 5 | 5 | 337.5 | 146.2708
338-339 |  | 2 | 1 | [8 empty] | 3 | 3 | 338.5 | 142
339-340 |  |  | 1 | [8 empty] | 1 | 1 | 339.5 | 137.6859
340-341 |  | 1 | [9 empty] | 1 | 1 | 340.5 | 133.3299
341-342 |  | 2 | 1 | [8 empty] | 3 | 3 | 341.5 | 128.9333
342-343 | 1 | [10 empty] | 1 | 1 | 342.5 | 124.4974
343-344 | 1 | 2 | 1 | [8 empty] | 4 | 4 | 343.5 | 120.0236
344-345 | 1 | 2 | 1 | [8 empty] | 4 | 4 | 344.5 | 115.5132
345-346 | 1 | 1 | [9 empty] | 2 | 2 | 345.5 | 110.9676
346-347 | 1 | 4 | 3 | 1 | [7 empty] | 9 | 9 | 346.5 | 106.3883
347-348 | 2 | 4 | 7 | [8 empty] | 13 | 13 | 347.5 | 101.7765
348-349 | 1 | 2 | 4 | 2 | [7 empty] | 9 | 9 | 348.5 | 97.1337
349-350 |  | 4 | 2 | 1 | [7 empty] | 7 | 7 | 349.5 | 92.4614
350-351 | 1 | 4 | 4 |  | 1 | [6 empty] | 10 | 10 | 350.5 | 87.7608
351-352 | 2 | 5 | 1 |  |  |  | 1 |  |  |  |  | 9 | 9 | 351.5 | 83.0336
352-353 |  | 3 | 2 |  | 1 | [6 empty] | 6 | 6 | 352.5 | 78.281
353-354 |  | 3 | 3 | 2 | 4 | [6 empty] | 12 | 12 | 353.5 | 73.5046
354-355 |  | 1 | 6 |  | 2 | [6 empty] | 9 | 9 | 354.5 | 68.7058
355-356 |  | 3 | 4 | 2 | 1 | 1 | [5 empty] | 11 | 11 | 355.5 | 63.8861
356-357 |  | 6 | 2 | 1 | 2 | [6 empty] | 11 | 11 | 356.5 | 59.0469
357-358 |  | 3 | 4 | 2 | 2 | 2 | 1 |  |  |  |  | 14 | 14 | 357.5 | 54.1898
358-359 |  | 1 | 3 | 4 | 4 | 2 | [5 empty] | 14 | 14 | 358.5 | 49.3161
359-360 |  | 2 | 6 | 5 | 4 |  |  | 2 |  |  |  | 19 | 19 | 359.5 | 44.4274
Grand Total | 227 | 435 | 428 | 558 | 732 | 684 | 652 | 396 | 170 | 42 | 8 | 4332
| 227 | 435 | 428 | 558 | 732 | 684 | 652 | 396 | 170 | 42 | 8 | 4332 | 722
"weight" speed | 0 | 0 | 0 | 0.35 | 0.45 | 0.55 | 0.65 | 0.75 | 0.85 | 0.95 | 1.05
slack weight | 1090 |  |  | slack area | 228.65 | ratio | 25.16%
|  |  |  | slack speed (intake velocity) | 0.3
Inflow = area * weight speed * count
Direction | 0-0.1 | 0.1-0.2 | 0.2-0.3 | 0.3-0.4 | 0.4-0.5 | 0.5-0.6 | 0.6-0.7 | 0.7-0.8 | 0.8-0.9 | 0.9-1 | 1-1.1 | direction total
0-1 | 0 | 0 | 0 | 152.1719 | 142.2906 | 130.433 | 77.0741 | 29.6439 | 0 | 0 | 0 | 531.6134 |  | southern area |  | 53.3013 | m2
1-2 | 0 | 0 | 0 | 60.5691 | 186.8988 | 171.3239 | 89.9883 | 0 | 29.4193 | 0 | 0 | 538.1994
2-3 | 0 | 0 | 0 | 145.4618 | 187.0223 | 130.6188 | 231.5515 | 133.5874 | 75.6995 | 0 | 0 | 903.9412
3-4 | 0 | 0 | 0 | 69.3062 | 111.385 | 190.5922 | 112.6227 | 167.0776 | 63.1182 | 23.5146 | 0 | 737.6165
4-5 | 0 | 0 | 0 | 69.3379 | 133.7232 | 130.7515 | 218.9098 | 222.8719 | 101.0353 | 18.8203 | 0 | 895.4499
5-6 | 0 | 0 | 0 | 52.0219 | 93.6395 | 179.8473 | 212.5468 | 178.3609 | 88.4373 | 28.2405 | 0 | 833.0942
6-7 | 0 | 0 | 0 | 52.0351 | 107.0437 | 125.3799 | 135.2914 | 200.707 | 101.0969 | 37.6635 | 0 | 759.2176
7-8 | 0 | 0 | 0 | 34.6954 | 37.9171 | 76.3298 | 83.7646 | 44.6084 | 58.9822 | 23.5433 | 0 | 359.8407
8-9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9-10 | 0 | 0 | 0 | 19.0825 | 40.1475 | 73.6038 | 64.4343 | 74.3473 | 37.9171 | 14.126 | 0 | 323.6584
10-11 | 0 | 0 | 0 | 31.2211 | 102.5836 | 109.026 | 206.1583 | 223.0078 | 176.9195 | 47.0794 | 20.8141 | 916.8098
11-12 | 0 | 0 | 0 | 83.2351 | 113.7051 | 237.0714 | 231.8692 | 278.689 | 138.9729 | 84.7214 | 15.6066 | 1183.8707
12-13 | 0 | 0 | 0 | 34.669 | 151.5529 | 196.1273 | 244.6639 | 312.0207 | 319.945 | 94.1015 | 0 | 1353.0803
13-14 | 0 | 0 | 0 | 103.9594 | 256.1856 | 190.5922 | 160.8895 | 167.0776 | 84.1576 | 23.5146 | 77.9695 | 1064.3459
14-15 | 0 | 0 | 0 | 62.3408 | 66.7937 | 228.5828 | 192.9595 | 289.4393 | 227.0985 | 56.4036 | 0 | 1123.6183
15-16 | 0 | 0 | 0 | 145.3658 | 249.1984 | 171.3239 | 247.4679 | 311.498 | 88.2578 | 65.7607 | 0 | 1278.8725
16-17 | 0 | 0 | 0 | 179.8395 | 88.9316 | 217.3884 | 128.4568 | 207.5071 | 134.3855 | 0 | 0 | 956.5089
17-18 | 0 | 0 | 0 | 0 | 179.9309 | 122.1753 | 202.1446 | 33.3205 | 0 | 42.206 | 0 | 579.7774
18-19 | 0 | 0 | 0 | 138.085 | 155.3457 | 189.8669 | 128.2218 | 36.9871 | 41.9187 | 0 | 0 | 690.4252
19-20 | 0 | 0 | 0 | 132.7649 | 121.9269 | 89.4131 | 105.67 | 121.9269 | 92.1226 | 0 | 0 | 663.8245
20-21 | 0 | 0 | 0 | 123.9985 | 79.7133 | 129.9032 | 38.3805 | 0 | 0 | 0 | 0 | 371.9956
21-22 | 0 | 0 | 0 | 223.6013 | 143.7437 | 35.1374 | 0 | 0 | 0 | 0 | 0 | 402.4824
22-23 | 0 | 0 | 0 | 120.2352 | 92.7529 | 0 | 44.6588 | 0 | 0 | 0 | 0 | 257.6468
23-24 | 0 | 0 | 0 | 0 | 99.2312 | 80.8551 | 0 | 0 | 0 | 0 | 0 | 180.0863
24-25 | 0 | 0 | 0 | 27.3984 | 70.4529 | 0 | 0 | 0 | 0 | 0 | 0 | 97.8513
25-26 | 0 | 0 | 0 | 116.247 | 149.4604 | 0 | 0 | 0 | 0 | 0 | 0 | 265.7074
26-27 | 0 | 0 | 0 | 30.7163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.7163
27-28 | 0 | 0 | 0 | 97.0844 | 0 | 50.8537 | 0 | 0 | 0 | 0 | 0 | 147.9382
28-29 | 0 | 0 | 0 | 135.9872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135.9872
29-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30-31 | 0 | 0 | 0 | 186.1795 | 47.8747 | 0 | 0 | 0 | 0 | 0 | 0 | 234.0542
31-32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32-33 | 0 | 0 | 0 | 40.4296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.4296
33-34 | 0 | 0 | 0 | 0 | 54.0106 | 0 | 0 | 0 | 0 | 0 | 0 | 54.0106
34-35 | 0 | 0 | 0 | 0 | 56.0238 | 0 | 0 | 0 | 0 | 0 | 0 | 56.0238
35-36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36-37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37-38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38-39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39-40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40-41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41-42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42-43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43-44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44-45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45-46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46-47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47-48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48-49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
49-50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51-52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
52-53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54-55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55-56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57-58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58-59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59-60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60-61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
63-64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
64-65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
65-66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
66-67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67-68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
68-69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
69-70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
71-72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72-73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
76-77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
77-78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78-79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
81-82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
84-85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
87-88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
89-90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90-91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91-92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
96-97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104-105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109-110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111-112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112-113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
113-114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
114-115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
115-116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
118-119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
120-121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
121-122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
127-128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
129-130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
131-132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
132-133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
133-134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
136-137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
138-139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
139-140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
140-141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
141-142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
142-143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
144-145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
145-146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
146-147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
148-149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149-150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150-151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
151-152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
152-153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153-154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154-155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155-156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156-157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157-158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
158-159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
159-160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160-161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
161-162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
162-163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
163-164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
164-165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
165-166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
166-167 | 0 | 0 | 0 | 37.2359 | 95.7494 | 0 | 0 | 0 | 0 | 0 | 0 | 132.9853
167-168 | 0 | 0 | 0 | 106.8653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.8653
168-169 | 0 | 0 | 0 | 101.9904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.9904
169-170 | 0 | 0 | 0 | 64.7229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.7229
170-171 | 0 | 0 | 0 | 61.4326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.4326
171-172 | 0 | 0 | 0 | 232.494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232.494
172-173 | 0 | 0 | 0 | 54.7967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.7967
173-174 | 0 | 0 | 0 | 0 | 66.1541 | 80.8551 | 0 | 0 | 0 | 0 | 0 | 147.0092
174-175 | 0 | 0 | 0 | 96.1881 | 309.1762 | 37.7882 | 44.6588 | 0 | 0 | 0 | 0 | 487.8113
175-176 | 0 | 0 | 0 | 44.7203 | 172.4925 | 70.2747 | 41.526 | 143.7437 | 0 | 0 | 0 | 472.7571
176-177 | 0 | 0 | 0 | 103.3321 | 106.2845 | 162.379 | 0 | 0 | 0 | 0 | 0 | 371.9956
177-178 | 0 | 0 | 0 | 113.7985 | 73.1562 | 0 | 176.1167 | 0 | 0 | 0 | 0 | 363.0714
178-179 | 0 | 0 | 0 | 34.5213 | 133.1534 | 108.4954 | 64.1109 | 36.9871 | 0 | 0 | 0 | 377.268
179-180 | 0 | 0 | 0 | 108.8471 | 119.9539 | 146.6104 | 144.389 | 33.3205 | 0 | 0 | 0 | 553.121
180-181 | 0 | 0 | 0 | 69.169 | 373.5128 | 260.8661 | 205.5308 | 59.2877 | 67.1928 | 0 | 0 | 1035.5592
181-182 | 0 | 0 | 0 | 72.6829 | 249.1984 | 304.5759 | 449.9416 | 77.8745 | 29.4193 | 0 | 0 | 1183.6926
182-183 | 0 | 0 | 0 | 41.5605 | 267.1748 | 179.6008 | 231.5515 | 111.3228 | 25.2332 | 0 | 0 | 856.4435
183-184 | 0 | 0 | 0 | 103.9594 | 155.9391 | 299.502 | 386.1348 | 185.6417 | 63.1182 | 0 | 0 | 1194.2951
184-185 | 0 | 0 | 0 | 104.0069 | 160.4678 | 228.8152 | 193.1557 | 29.7163 | 50.5176 | 0 | 0 | 766.6795
185-186 | 0 | 0 | 0 | 52.0219 | 153.8363 | 277.9458 | 260.8529 | 55.7378 | 25.2678 | 0 | 0 | 825.6625
186-187 | 0 | 0 | 0 | 52.0351 | 102.5836 | 158.0877 | 225.4856 | 37.168 | 0 | 0 | 0 | 575.3601
187-188 | 0 | 0 | 0 | 22.552 | 57.9909 | 87.2341 | 77.3211 | 52.0431 | 8.426 | 0 | 0 | 305.5672
188-189 | 0 | 0 | 0 | 2.3138e-13 | 2.0355e-13 | 5.5497e-13 | 7.6895e-13 | 5.4801e-13 | 1.183e-13 | 0 | 0 | 2.4252e-12
189-190 | 0 | 0 | 0 | 6.9391 | 40.1475 | 95.4123 | 61.2126 | 52.0431 | 12.639 | 0 | 0 | 268.3936
190-191 | 0 | 0 | 0 | 41.6281 | 124.8844 | 125.3799 | 219.0432 | 104.0703 | 8.4247 | 0 | 0 | 623.4306
191-192 | 0 | 0 | 0 | 57.2241 | 127.0822 | 122.6231 | 280.1753 | 66.8854 | 0 | 0 | 0 | 653.9901
192-193 | 0 | 0 | 0 | 55.4703 | 187.2124 | 141.6475 | 193.1557 | 163.4394 | 50.5176 | 0 | 0 | 791.443
193-194 | 0 | 0 | 0 | 129.9492 | 167.0776 | 217.8196 | 193.0674 | 148.5134 | 21.0394 | 0 | 0 | 877.4666
194-195 | 0 | 0 | 0 | 114.2914 | 213.7398 | 163.2735 | 366.6231 | 133.5874 | 0 | 0 | 0 | 991.5152
195-196 | 0 | 0 | 0 | 169.5934 | 171.3239 | 152.2879 | 179.9766 | 51.9163 | 0 | 0 | 0 | 725.0982
196-197 | 0 | 0 | 0 | 96.8366 | 88.9316 | 173.9107 | 51.3827 | 0 | 0 | 0 | 0 | 411.0617
197-198 | 0 | 0 | 0 | 155.4959 | 159.9386 | 195.4805 | 57.7556 | 66.6411 | 0 | 0 | 0 | 635.3116
198-199 | 0 | 0 | 0 | 189.8669 | 155.3457 | 108.4954 | 32.0555 | 0 | 0 | 0 | 0 | 485.7634
199-200 | 0 | 0 | 0 | 94.8321 | 219.4685 | 89.4131 | 0 | 0 | 0 | 0 | 0 | 403.7137
200-201 | 0 | 0 | 0 | 165.3314 | 212.5689 | 129.9032 | 0 | 0 | 0 | 0 | 0 | 507.8035
201-202 | 0 | 0 | 0 | 134.1608 | 143.7437 | 70.2747 | 0 | 0 | 0 | 0 | 0 | 348.1792
202-203 | 0 | 0 | 0 | 72.1411 | 278.2586 | 37.7882 | 0 | 0 | 0 | 0 | 0 | 388.1879
203-204 | 0 | 0 | 0 | 180.0863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180.0863
204-205 | 0 | 0 | 0 | 136.9918 | 176.1323 | 0 | 0 | 0 | 0 | 0 | 0 | 313.124
205-206 | 0 | 0 | 0 | 58.1235 | 261.5557 | 45.6685 | 0 | 0 | 0 | 0 | 0 | 365.3477
206-207 | 0 | 0 | 0 | 0 | 78.9847 | 0 | 0 | 0 | 0 | 0 | 0 | 78.9847
207-208 | 0 | 0 | 0 | 64.7229 | 83.2152 | 0 | 0 | 0 | 0 | 0 | 0 | 147.9382
208-209 | 0 | 0 | 0 | 101.9904 | 43.7102 | 0 | 0 | 0 | 0 | 0 | 0 | 145.7006
209-210 | 0 | 0 | 0 | 35.6218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.6218
210-211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
211-212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
212-213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213-214 | 0 | 0 | 0 | 84.0165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.0165
214-215 | 0 | 0 | 0 | 43.5741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.5741
215-216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
216-217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
217-218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
218-219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
219-220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
221-222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
222-223 | 0 | 0 | 0 | 55.5838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.5838
223-224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
224-225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
225-226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
228-229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
229-230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
230-231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
231-232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
232-233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
233-234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
234-235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
235-236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
236-237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
237-238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
238-239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
240-241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
241-242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242-243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
243-244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
245-246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
248-249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
249-250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
250-251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
252-253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
253-254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
254-255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256-257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257-258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
258-259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
263-264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
266-267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
267-268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
270-271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
271-272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
277-278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
279-280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
285-286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
286-287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
287-288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
293-294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
294-295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
300-301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
301-302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
302-303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
304-305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
306-307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
308-309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
309-310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
310-311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311-312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313-314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314-315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
315-316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
317-318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
319-320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
320-321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
321-322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
322-323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
323-324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
324-325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
325-326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
329-330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
330-331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 262.2718 | 0 | 0 | 0 | 262.2718
331-332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
332-333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333-334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
334-335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
335-336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
336-337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
337-338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
338-339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
339-340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
340-341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
341-342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
342-343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343-344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
344-345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
345-346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346-347 | 0 | 0 | 0 | 37.2359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.2359
347-348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
348-349 | 0 | 0 | 0 | 67.9936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.9936
349-350 | 0 | 0 | 0 | 32.3615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.3615
350-351 | 0 | 0 | 0 | 0 | 39.4924 | 0 | 0 | 0 | 0 | 0 | 0 | 39.4924
351-352 | 0 | 0 | 0 | 0 | 0 | 0 | 53.9718 | 0 | 0 | 0 | 0 | 53.9718
352-353 | 0 | 0 | 0 | 0 | 35.2265 | 0 | 0 | 0 | 0 | 0 | 0 | 35.2265
353-354 | 0 | 0 | 0 | 51.4532 | 132.3083 | 0 | 0 | 0 | 0 | 0 | 0 | 183.7615
354-355 | 0 | 0 | 0 | 0 | 61.8352 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8352
355-356 | 0 | 0 | 0 | 44.7203 | 28.7487 | 35.1374 | 0 | 0 | 0 | 0 | 0 | 108.6064
356-357 | 0 | 0 | 0 | 20.6664 | 53.1422 | 0 | 0 | 0 | 0 | 0 | 0 | 73.8087
357-358 | 0 | 0 | 0 | 37.9328 | 48.7708 | 59.6087 | 35.2233 | 0 | 0 | 0 | 0 | 181.5357
358-359 | 0 | 0 | 0 | 69.0425 | 88.7689 | 54.2477 | 0 | 0 | 0 | 0 | 0 | 212.0592
359-360 | 0 | 0 | 0 | 77.7479 | 79.9693 | 0 | 0 | 66.6411 | 0 | 0 | 0 | 224.3583
draw excl slacks | 39376.1294 | ok
slacks | 74768.55
total draw | 114144.6794
divisor | 2141.5
Average | 53.3013 | m2 |  |  | 0.45363

## SZ2 - southern intake
Days | DateTime | Velocity at 2.09m above bed (m/s) | Direction at 2.09m above bed (deg)
0 | 2018-11-13 16:00 | 0.70614 | 330.5671 | Bin
0.0069444 | 2018-11-13 16:10 | 0.70614 | 330.5671 | 0.1
0.013889 | 2018-11-13 16:20 | 0.60798 | 10.9033 | 0.2
0.020833 | 2018-11-13 16:30 | 0.69667 | 10.5035 | 0.3
0.027778 | 2018-11-13 16:40 | 0.6299 | 6.3804 | 0.4
0.034722 | 2018-11-13 16:50 | 0.61921 | 5.8395 | 0.5
0.041667 | 2018-11-13 17:00 | 0.79724 | 14.4546 | 0.6
0.048611 | 2018-11-13 17:10 | 0.79724 | 14.4546 | 0.7
0.055556 | 2018-11-13 17:20 | 0.6883 | 8.3538 | 0.8
0.0625 | 2018-11-13 17:30 | 0.61637 | 8.8663 | 0.9
0.069444 | 2018-11-13 17:40 | 0.53824 | 13.21 | 1
0.076389 | 2018-11-13 17:50 | 0.57902 | 0.49477 | 1.1
0.083333 | 2018-11-13 18:00 | 0.53402 | 3.5429 | 1.2
0.090278 | 2018-11-13 18:10 | 0.53402 | 3.5429 | 1.3
0.097222 | 2018-11-13 18:20 | 0.55353 | 9.4623
0.10417 | 2018-11-13 18:30 | 0.61181 | 19.9751
0.11111 | 2018-11-13 18:40 | 0.48716 | 11.1254
0.11806 | 2018-11-13 18:50 | 0.50007 | 8.1625
0.125 | 2018-11-13 19:00 | 0.42371 | 8.5508
0.13194 | 2018-11-13 19:10 | 0.42371 | 8.5508
0.13889 | 2018-11-13 19:20 | 0.35511 | 4.5225 |  | Bin | Frequency | Cumulative %
0.14583 | 2018-11-13 19:30 | 0.28109 | 1.427 |  | 0.1 | 193 | 4.526%
0.15278 | 2018-11-13 19:40 | 0.26974 | 18.3678 |  | 0.2 | 398 | 13.86%
0.15972 | 2018-11-13 19:50 | 0.2093 | 10.1824 |  | 0.3 | 430 | 23.94%
0.16667 | 2018-11-13 20:00 | 0.22681 | 12.9946 |  | 0.4 | 499 | 35.65%
0.17361 | 2018-11-13 20:10 | 0.22681 | 12.9946 |  | 0.5 | 723 | 52.6%
0.18056 | 2018-11-13 20:20 | 0.12323 | 308.0789 |  | 0.6 | 801 | 71.39%
0.1875 | 2018-11-13 20:30 | 0.10296 | 294.0755 |  | 0.7 | 621 | 85.95%
0.19444 | 2018-11-13 20:40 | 0.13859 | 225 |  | 0.8 | 329 | 93.67%
0.20139 | 2018-11-13 20:50 | 0.19801 | 224.1815 |  | 0.9 | 169 | 97.63%
0.20833 | 2018-11-13 21:00 | 0.19972 | 203.6129 |  | 1 | 75 | 99.39%
0.21528 | 2018-11-13 21:10 | 0.19972 | 203.6129 |  | 1.1 | 20 | 99.86%
0.22222 | 2018-11-13 21:20 | 0.37451 | 189.8396 |  | 1.2 | 5 | 99.98%
0.22917 | 2018-11-13 21:30 | 0.33521 | 200.9762 |  | 1.3 | 1 | 100%
0.23611 | 2018-11-13 21:40 | 0.32329 | 203.7106 |  | More | 0 | 100%
0.24306 | 2018-11-13 21:50 | 0.47176 | 193.3587
0.25 | 2018-11-13 22:00 | 0.40481 | 191.9761
0.25694 | 2018-11-13 22:10 | 0.40481 | 191.9761
0.26389 | 2018-11-13 22:20 | 0.4402 | 194.0678
0.27083 | 2018-11-13 22:30 | 0.52602 | 190.6263
0.27778 | 2018-11-13 22:40 | 0.5333 | 188.0845
0.28472 | 2018-11-13 22:50 | 0.4542 | 184.1665
0.29167 | 2018-11-13 23:00 | 0.53727 | 193.2344
0.29861 | 2018-11-13 23:10 | 0.53727 | 193.2344
0.30556 | 2018-11-13 23:20 | 0.61013 | 188.7676
0.3125 | 2018-11-13 23:30 | 0.53446 | 189.5857
0.31944 | 2018-11-13 23:40 | 0.59623 | 194.9686
0.32639 | 2018-11-13 23:50 | 0.56993 | 188.2723
0.33333 | 2018-11-14 | 0.65938 | 190.6624
0.34028 | 2018-11-14 00:10 | 0.65938 | 190.6624
0.34722 | 2018-11-14 00:20 | 0.54005 | 192.6209
0.35417 | 2018-11-14 00:30 | 0.42416 | 189.7732
0.36111 | 2018-11-14 00:40 | 0.45206 | 190.8377
0.36806 | 2018-11-14 00:50 | 0.45426 | 192.2005
0.375 | 2018-11-14 01:00 | 0.38363 | 183.2875
0.38194 | 2018-11-14 01:10 | 0.38363 | 183.2875
0.38889 | 2018-11-14 01:20 | 0.43711 | 181.3109
0.39583 | 2018-11-14 01:30 | 0.36125 | 184.7636
0.40278 | 2018-11-14 01:40 | 0.28724 | 188.6097
0.40972 | 2018-11-14 01:50 | 0.20535 | 171.3175
0.41667 | 2018-11-14 02:00 | 0.16388 | 203.7495
0.42361 | 2018-11-14 02:10 | 0.16388 | 203.7495
0.43056 | 2018-11-14 02:20 | 0.10359 | 186.0959
0.4375 | 2018-11-14 02:30 | 0.1042 | 52.8002
0.44444 | 2018-11-14 02:40 | 0.027803 | 37.6942
0.45139 | 2018-11-14 02:50 | 0.19098 | 25.76
0.45833 | 2018-11-14 03:00 | 0.28288 | 24.2093
0.46528 | 2018-11-14 03:10 | 0.28288 | 24.2093
0.47222 | 2018-11-14 03:20 | 0.46283 | 15.0271
0.47917 | 2018-11-14 03:30 | 0.45951 | 5.996
0.48611 | 2018-11-14 03:40 | 0.43635 | 7.1087
0.49306 | 2018-11-14 03:50 | 0.56833 | 9.2137
0.5 | 2018-11-14 04:00 | 0.57503 | 6.7913
0.50694 | 2018-11-14 04:10 | 0.57503 | 6.7913
0.51389 | 2018-11-14 04:20 | 0.64697 | 7.103
0.52083 | 2018-11-14 04:30 | 0.66837 | 5.7532
0.52778 | 2018-11-14 04:40 | 0.68255 | 4.9588
0.53472 | 2018-11-14 04:50 | 0.66451 | 9.7033
0.54167 | 2018-11-14 05:00 | 0.75611 | 16.7573
0.54861 | 2018-11-14 05:10 | 0.75611 | 16.7573
0.55556 | 2018-11-14 05:20 | 0.68937 | 11.7174
0.5625 | 2018-11-14 05:30 | 0.65144 | 18.1568
0.56944 | 2018-11-14 05:40 | 0.69694 | 10.1651
0.57639 | 2018-11-14 05:50 | 0.54406 | 3.5829
0.58333 | 2018-11-14 06:00 | 0.69287 | 6.7968
0.59028 | 2018-11-14 06:10 | 0.69287 | 6.7968
0.59722 | 2018-11-14 06:20 | 0.50593 | 16.5365
0.60417 | 2018-11-14 06:30 | 0.61329 | 11.9512
0.61111 | 2018-11-14 06:40 | 0.64287 | 7.0587
0.61806 | 2018-11-14 06:50 | 0.6284 | 20.396
0.625 | 2018-11-14 07:00 | 0.51822 | 7.317
0.63194 | 2018-11-14 07:10 | 0.51822 | 7.317
0.63889 | 2018-11-14 07:20 | 0.45015 | 7.7881
0.64583 | 2018-11-14 07:30 | 0.53424 | 11.7727
0.65278 | 2018-11-14 07:40 | 0.40775 | 11.8887
0.65972 | 2018-11-14 07:50 | 0.38613 | 1.484
0.66667 | 2018-11-14 08:00 | 0.36285 | 19.9831
0.67361 | 2018-11-14 08:10 | 0.36285 | 19.9831
0.68056 | 2018-11-14 08:20 | 0.28305 | 14.5272
0.6875 | 2018-11-14 08:30 | 0.30705 | 13.9457
0.69444 | 2018-11-14 08:40 | 0.16834 | 346.9544
0.70139 | 2018-11-14 08:50 | 0.17611 | 344.859
0.70833 | 2018-11-14 09:00 | 0.11493 | 349.4722
0.71528 | 2018-11-14 09:10 | 0.11493 | 349.4722
0.72222 | 2018-11-14 09:20 | 0.037483 | 43.9191
0.72917 | 2018-11-14 09:30 | 0.093963 | 253.3008
0.73611 | 2018-11-14 09:40 | 0.063789 | 256.3994
0.74306 | 2018-11-14 09:50 | 0.0436 | 216.6071
0.75 | 2018-11-14 10:00 | 0.12925 | 213.3212
0.75694 | 2018-11-14 10:10 | 0.12925 | 213.3212
0.76389 | 2018-11-14 10:20 | 0.30608 | 193.9908
0.77083 | 2018-11-14 10:30 | 0.25485 | 211.1951
0.77778 | 2018-11-14 10:40 | 0.36142 | 200.7416
0.78472 | 2018-11-14 10:50 | 0.30516 | 198.1381
0.79167 | 2018-11-14 11:00 | 0.35148 | 200.1363
0.79861 | 2018-11-14 11:10 | 0.35148 | 200.1363
0.80556 | 2018-11-14 11:20 | 0.42716 | 191.8887
0.8125 | 2018-11-14 11:30 | 0.36637 | 196.6543
0.81944 | 2018-11-14 11:40 | 0.43584 | 185.2658
0.82639 | 2018-11-14 11:50 | 0.50498 | 193.5134
0.83333 | 2018-11-14 12:00 | 0.43443 | 190.6116
0.84028 | 2018-11-14 12:10 | 0.43443 | 190.6116
0.84722 | 2018-11-14 12:20 | 0.47791 | 195.2867
0.85417 | 2018-11-14 12:30 | 0.43429 | 182.1113
0.86111 | 2018-11-14 12:40 | 0.55203 | 179.3772
0.86806 | 2018-11-14 12:50 | 0.47659 | 193.7155
0.875 | 2018-11-14 13:00 | 0.4611 | 185.4757
0.88194 | 2018-11-14 13:10 | 0.4611 | 185.4757
0.88889 | 2018-11-14 13:20 | 0.39121 | 193.7521
0.89583 | 2018-11-14 13:30 | 0.40206 | 188.1503
0.90278 | 2018-11-14 13:40 | 0.392 | 180
0.90972 | 2018-11-14 13:50 | 0.37537 | 191.3698
0.91667 | 2018-11-14 14:00 | 0.24636 | 187.9328
0.92361 | 2018-11-14 14:10 | 0.24636 | 187.9328
0.93056 | 2018-11-14 14:20 | 0.19908 | 202.4427
0.9375 | 2018-11-14 14:30 | 0.14723 | 172.5854
0.94444 | 2018-11-14 14:40 | 0.12042 | 184.7636
0.95139 | 2018-11-14 14:50 | 0.056365 | 115.2011
0.95833 | 2018-11-14 15:00 | 0.091006 | 89.3704
0.96528 | 2018-11-14 15:10 | 0.091006 | 89.3704
0.97222 | 2018-11-14 15:20 | 0.15654 | 19.0137
0.97917 | 2018-11-14 15:30 | 0.19123 | 12.0738
0.98611 | 2018-11-14 15:40 | 0.23333 | 13.3811
0.99306 | 2018-11-14 15:50 | 0.28431 | 22.3253
1 | 2018-11-14 16:00 | 0.37574 | 13.0746
1.0069 | 2018-11-14 16:10 | 0.37574 | 13.0746
1.0139 | 2018-11-14 16:20 | 0.43757 | 4.8506
1.0208 | 2018-11-14 16:30 | 0.55797 | 9.6987
1.0278 | 2018-11-14 16:40 | 0.50929 | 7.446
1.0347 | 2018-11-14 16:50 | 0.5402 | 3.8211
1.0417 | 2018-11-14 17:00 | 0.5672 | 11.9043
1.0486 | 2018-11-14 17:10 | 0.5672 | 11.9043
1.0556 | 2018-11-14 17:20 | 0.69324 | 14.8782
1.0625 | 2018-11-14 17:30 | 0.66229 | 11.0554
1.0694 | 2018-11-14 17:40 | 0.71063 | 6.545
1.0764 | 2018-11-14 17:50 | 0.59114 | 8.2672
1.0833 | 2018-11-14 18:00 | 0.61474 | 10.2132
1.0903 | 2018-11-14 18:10 | 0.61474 | 10.2132
1.0972 | 2018-11-14 18:20 | 0.49673 | 6.009
1.1042 | 2018-11-14 18:30 | 0.57836 | 9.1529
1.1111 | 2018-11-14 18:40 | 0.56243 | 9.9313
1.1181 | 2018-11-14 18:50 | 0.58971 | 2.8187
1.125 | 2018-11-14 19:00 | 0.5386 | 16.2815
1.1319 | 2018-11-14 19:10 | 0.5386 | 16.2815
1.1389 | 2018-11-14 19:20 | 0.4056 | 3.1093
1.1458 | 2018-11-14 19:30 | 0.40236 | 2.4215
1.1528 | 2018-11-14 19:40 | 0.40334 | 14.2085
1.1597 | 2018-11-14 19:50 | 0.37838 | 14.6973
1.1667 | 2018-11-14 20:00 | 0.37198 | 7.2588
1.1736 | 2018-11-14 20:10 | 0.37198 | 7.2588
1.1806 | 2018-11-14 20:20 | 0.25116 | 2.0535
1.1875 | 2018-11-14 20:30 | 0.21467 | 4.542
1.1944 | 2018-11-14 20:40 | 0.11304 | 358.4792
1.2014 | 2018-11-14 20:50 | 0.11122 | 3.6085
1.2083 | 2018-11-14 21:00 | 0.10742 | 331.049
1.2153 | 2018-11-14 21:10 | 0.10742 | 331.049
1.2222 | 2018-11-14 21:20 | 0.055803 | 233.7462
1.2292 | 2018-11-14 21:30 | 0.14359 | 223.5891
1.2361 | 2018-11-14 21:40 | 0.12881 | 205.7693
1.2431 | 2018-11-14 21:50 | 0.18398 | 185.9275
1.25 | 2018-11-14 22:00 | 0.26022 | 209.7176
1.2569 | 2018-11-14 22:10 | 0.26022 | 209.7176
1.2639 | 2018-11-14 22:20 | 0.4232 | 201.7763
1.2708 | 2018-11-14 22:30 | 0.37221 | 197.9968
1.2778 | 2018-11-14 22:40 | 0.39705 | 193.5462
1.2847 | 2018-11-14 22:50 | 0.35899 | 194.8492
1.2917 | 2018-11-14 23:00 | 0.40003 | 198.6614
1.2986 | 2018-11-14 23:10 | 0.40003 | 198.6614
1.3056 | 2018-11-14 23:20 | 0.4616 | 194.9394
1.3125 | 2018-11-14 23:30 | 0.42059 | 188.4769
1.3194 | 2018-11-14 23:40 | 0.50977 | 183.1487
1.3264 | 2018-11-14 23:50 | 0.54189 | 195.9599
1.3333 | 2018-11-15 | 0.48504 | 180.7088
1.3403 | 2018-11-15 00:10 | 0.48504 | 180.7088
1.3472 | 2018-11-15 00:20 | 0.49517 | 178.4956
1.3542 | 2018-11-15 00:30 | 0.53433 | 190.1322
1.3611 | 2018-11-15 00:40 | 0.61591 | 188.5906
1.3681 | 2018-11-15 00:50 | 0.51835 | 187.4266
1.375 | 2018-11-15 01:00 | 0.46 | 192.5558
1.3819 | 2018-11-15 01:10 | 0.46 | 192.5558
1.3889 | 2018-11-15 01:20 | 0.43926 | 187.9825
1.3958 | 2018-11-15 01:30 | 0.44909 | 197.628
1.4028 | 2018-11-15 01:40 | 0.36948 | 185.1242
1.4097 | 2018-11-15 01:50 | 0.36719 | 186.254
1.4167 | 2018-11-15 02:00 | 0.37546 | 193.5551
1.4236 | 2018-11-15 02:10 | 0.37546 | 193.5551
1.4306 | 2018-11-15 02:20 | 0.22402 | 179.2327
1.4375 | 2018-11-15 02:30 | 0.29066 | 186.1225
1.4444 | 2018-11-15 02:40 | 0.2413 | 182.8505
1.4514 | 2018-11-15 02:50 | 0.24729 | 177.2186
1.4583 | 2018-11-15 03:00 | 0.11122 | 183.6085
1.4653 | 2018-11-15 03:10 | 0.11122 | 183.6085
1.4722 | 2018-11-15 03:20 | 0.070456 | 96.5198
1.4792 | 2018-11-15 03:30 | 0.14431 | 46.6847
1.4861 | 2018-11-15 03:40 | 0.1964 | 36.9282
1.4931 | 2018-11-15 03:50 | 0.20583 | 28.4327
1.5 | 2018-11-15 04:00 | 0.25747 | 32.1469
1.5069 | 2018-11-15 04:10 | 0.25747 | 32.1469
1.5139 | 2018-11-15 04:20 | 0.31146 | 22.8604
1.5208 | 2018-11-15 04:30 | 0.35477 | 11.2149
1.5278 | 2018-11-15 04:40 | 0.39832 | 11.7331
1.5347 | 2018-11-15 04:50 | 0.49065 | 15.8491
1.5417 | 2018-11-15 05:00 | 0.59872 | 5.463
1.5486 | 2018-11-15 05:10 | 0.59872 | 5.463
1.5556 | 2018-11-15 05:20 | 0.50566 | 4.6507
1.5625 | 2018-11-15 05:30 | 0.63997 | 11.9947
1.5694 | 2018-11-15 05:40 | 0.58022 | 1.5802
1.5764 | 2018-11-15 05:50 | 0.62308 | 10.823
1.5833 | 2018-11-15 06:00 | 0.60373 | 7.9019
1.5903 | 2018-11-15 06:10 | 0.60373 | 7.9019
1.5972 | 2018-11-15 06:20 | 0.70774 | 13.565
1.6042 | 2018-11-15 06:30 | 0.65882 | 4.2653
1.6111 | 2018-11-15 06:40 | 0.66649 | 13.8903
1.6181 | 2018-11-15 06:50 | 0.55246 | 11.1676
1.625 | 2018-11-15 07:00 | 0.53219 | 10.0641
1.6319 | 2018-11-15 07:10 | 0.53219 | 10.0641
1.6389 | 2018-11-15 07:20 | 0.4713 | 12.0014
1.6458 | 2018-11-15 07:30 | 0.50028 | 9.0858
1.6528 | 2018-11-15 07:40 | 0.38724 | 7.4187
1.6597 | 2018-11-15 07:50 | 0.39535 | 6.2442
1.6667 | 2018-11-15 08:00 | 0.40808 | 1.1233
1.6736 | 2018-11-15 08:10 | 0.40808 | 1.1233
1.6806 | 2018-11-15 08:20 | 0.33602 | 0.68206
1.6875 | 2018-11-15 08:30 | 0.35458 | 11.0564
1.6944 | 2018-11-15 08:40 | 0.28302 | 0.60735
1.7014 | 2018-11-15 08:50 | 0.19317 | 2.3736
1.7083 | 2018-11-15 09:00 | 0.29515 | 354.9462
1.7153 | 2018-11-15 09:10 | 0.29515 | 354.9462
1.7222 | 2018-11-15 09:20 | 0.14843 | 345.9637
1.7292 | 2018-11-15 09:30 | 0.15703 | 1.0947
1.7361 | 2018-11-15 09:40 | 0.14727 | 321.3402
1.7431 | 2018-11-15 09:50 | 0.14169 | 337.5979
1.75 | 2018-11-15 10:00 | 0.082462 | 309.0939
1.7569 | 2018-11-15 10:10 | 0.082462 | 309.0939
1.7639 | 2018-11-15 10:20 | 0.093349 | 225.8681
1.7708 | 2018-11-15 10:30 | 0.11206 | 237.019
1.7778 | 2018-11-15 10:40 | 0.19777 | 208.3792
1.7847 | 2018-11-15 10:50 | 0.1449 | 200.1858
1.7917 | 2018-11-15 11:00 | 0.22401 | 217.3815
1.7986 | 2018-11-15 11:10 | 0.22401 | 217.3815
1.8056 | 2018-11-15 11:20 | 0.34918 | 203.9958
1.8125 | 2018-11-15 11:30 | 0.37362 | 190.7986
1.8194 | 2018-11-15 11:40 | 0.33679 | 198.7039
1.8264 | 2018-11-15 11:50 | 0.3891 | 191.7142
1.8333 | 2018-11-15 12:00 | 0.39779 | 186.7856
1.8403 | 2018-11-15 12:10 | 0.39779 | 186.7856
1.8472 | 2018-11-15 12:20 | 0.42528 | 184.4504
1.8542 | 2018-11-15 12:30 | 0.42947 | 182.6692
1.8611 | 2018-11-15 12:40 | 0.53203 | 187.8864
1.8681 | 2018-11-15 12:50 | 0.47548 | 188.7095
1.875 | 2018-11-15 13:00 | 0.47325 | 193.0672
1.8819 | 2018-11-15 13:10 | 0.47325 | 193.0672
1.8889 | 2018-11-15 13:20 | 0.53923 | 185.2137
1.8958 | 2018-11-15 13:30 | 0.55676 | 182.9857
1.9028 | 2018-11-15 13:40 | 0.50459 | 192.8244
1.9097 | 2018-11-15 13:50 | 0.46423 | 198.2008
1.9167 | 2018-11-15 14:00 | 0.37013 | 187.4514
1.9236 | 2018-11-15 14:10 | 0.37013 | 187.4514
1.9306 | 2018-11-15 14:20 | 0.44952 | 191.8099
1.9375 | 2018-11-15 14:30 | 0.4742 | 187.6346
1.9444 | 2018-11-15 14:40 | 0.26815 | 188.7949
1.9514 | 2018-11-15 14:50 | 0.41002 | 189.8299
1.9583 | 2018-11-15 15:00 | 0.29811 | 181.5378
1.9653 | 2018-11-15 15:10 | 0.29811 | 181.5378
1.9722 | 2018-11-15 15:20 | 0.29099 | 189.4947
1.9792 | 2018-11-15 15:30 | 0.20355 | 184.226
1.9861 | 2018-11-15 15:40 | 0.18655 | 172.6083
1.9931 | 2018-11-15 15:50 | 0.12624 | 196.5688
2 | 2018-11-15 16:00 | 0.076059 | 151.7503
2.0069 | 2018-11-15 16:10 | 0.076059 | 151.7503
2.0139 | 2018-11-15 16:20 | 0.09902 | 38.0272
2.0208 | 2018-11-15 16:30 | 0.063 | 0
2.0278 | 2018-11-15 16:40 | 0.24267 | 31.0042
2.0347 | 2018-11-15 16:50 | 0.25252 | 23.8243
2.0417 | 2018-11-15 17:00 | 0.31074 | 20.5345
2.0486 | 2018-11-15 17:10 | 0.31074 | 20.5345
2.0556 | 2018-11-15 17:20 | 0.36068 | 13.3042
2.0625 | 2018-11-15 17:30 | 0.40124 | 16.3573
2.0694 | 2018-11-15 17:40 | 0.393 | 16.406
2.0764 | 2018-11-15 17:50 | 0.40459 | 11.1155
2.0833 | 2018-11-15 18:00 | 0.48464 | 12.0287
2.0903 | 2018-11-15 18:10 | 0.48464 | 12.0287
2.0972 | 2018-11-15 18:20 | 0.4947 | 4.754
2.1042 | 2018-11-15 18:30 | 0.52839 | 7.394
2.1111 | 2018-11-15 18:40 | 0.58068 | 9.9165
2.1181 | 2018-11-15 18:50 | 0.59834 | 3.8332
2.125 | 2018-11-15 19:00 | 0.5741 | 9.0193
2.1319 | 2018-11-15 19:10 | 0.5741 | 9.0193
2.1389 | 2018-11-15 19:20 | 0.54828 | 5.2323
2.1458 | 2018-11-15 19:30 | 0.51288 | 7.0557
2.1528 | 2018-11-15 19:40 | 0.55471 | 8.9189
2.1597 | 2018-11-15 19:50 | 0.57501 | 4.7885
2.1667 | 2018-11-15 20:00 | 0.65266 | 6.0687
2.1736 | 2018-11-15 20:10 | 0.65266 | 6.0687
2.1806 | 2018-11-15 20:20 | 0.37694 | 11.0118
2.1875 | 2018-11-15 20:30 | 0.37298 | 16.8317
2.1944 | 2018-11-15 20:40 | 0.377 | 0
2.2014 | 2018-11-15 20:50 | 0.4122 | 1.8073
2.2083 | 2018-11-15 21:00 | 0.3653 | 7.7087
2.2153 | 2018-11-15 21:10 | 0.3653 | 7.7087
2.2222 | 2018-11-15 21:20 | 0.20261 | 15.7512
2.2292 | 2018-11-15 21:30 | 0.19433 | 351.1194
2.2361 | 2018-11-15 21:40 | 0.17552 | 348.498
2.2431 | 2018-11-15 21:50 | 0.13 | 300.5102
2.25 | 2018-11-15 22:00 | 0.076688 | 12.0426
2.2569 | 2018-11-15 22:10 | 0.076688 | 12.0426
2.2639 | 2018-11-15 22:20 | 0.038601 | 286.5571
2.2708 | 2018-11-15 22:30 | 0.074108 | 266.9059
2.2778 | 2018-11-15 22:40 | 0.14221 | 223.0054
2.2847 | 2018-11-15 22:50 | 0.075286 | 140.3893
2.2917 | 2018-11-15 23:00 | 0.19351 | 184.1489
2.2986 | 2018-11-15 23:10 | 0.19351 | 184.1489
2.3056 | 2018-11-15 23:20 | 0.26703 | 194.0883
2.3125 | 2018-11-15 23:30 | 0.34438 | 198.8032
2.3194 | 2018-11-15 23:40 | 0.35405 | 200.3288
2.3264 | 2018-11-15 23:50 | 0.28534 | 196.9108
2.3333 | 2018-11-16 | 0.36109 | 184.4474
2.3403 | 2018-11-16 00:10 | 0.36109 | 184.4474
2.3472 | 2018-11-16 00:20 | 0.32774 | 176.151
2.3542 | 2018-11-16 00:30 | 0.40035 | 190.2152
2.3611 | 2018-11-16 00:40 | 0.38011 | 184.3756
2.3681 | 2018-11-16 00:50 | 0.37365 | 183.3755
2.375 | 2018-11-16 01:00 | 0.37473 | 185.5128
2.3819 | 2018-11-16 01:10 | 0.37473 | 185.5128
2.3889 | 2018-11-16 01:20 | 0.53789 | 184.799
2.3958 | 2018-11-16 01:30 | 0.40379 | 188.8325
2.4028 | 2018-11-16 01:40 | 0.43757 | 192.0033
2.4097 | 2018-11-16 01:50 | 0.45162 | 194.6209
2.4167 | 2018-11-16 02:00 | 0.46448 | 182.5914
2.4236 | 2018-11-16 02:10 | 0.46448 | 182.5914
2.4306 | 2018-11-16 02:20 | 0.41924 | 200.3801
2.4375 | 2018-11-16 02:30 | 0.3217 | 185.8878
2.4444 | 2018-11-16 02:40 | 0.37574 | 194.9609
2.4514 | 2018-11-16 02:50 | 0.4276 | 189.2861
2.4583 | 2018-11-16 03:00 | 0.28401 | 180.4035
2.4653 | 2018-11-16 03:10 | 0.28401 | 180.4035
2.4722 | 2018-11-16 03:20 | 0.36236 | 200.6856
2.4792 | 2018-11-16 03:30 | 0.24103 | 180.9509
2.4861 | 2018-11-16 03:40 | 0.17632 | 194.1151
2.4931 | 2018-11-16 03:50 | 0.16164 | 188.1802
2.5 | 2018-11-16 04:00 | 0.10382 | 187.1935
2.5069 | 2018-11-16 04:10 | 0.10382 | 187.1935
2.5139 | 2018-11-16 04:20 | 0.071694 | 22.9887
2.5208 | 2018-11-16 04:30 | 0.12903 | 18.9966
2.5278 | 2018-11-16 04:40 | 0.1186 | 19.1989
2.5347 | 2018-11-16 04:50 | 0.24955 | 26.6677
2.5417 | 2018-11-16 05:00 | 0.28448 | 27.646
2.5486 | 2018-11-16 05:10 | 0.28448 | 27.646
2.5556 | 2018-11-16 05:20 | 0.31435 | 14.7436
2.5625 | 2018-11-16 05:30 | 0.3731 | 7.3917
2.5694 | 2018-11-16 05:40 | 0.46349 | 13.8564
2.5764 | 2018-11-16 05:50 | 0.46704 | 15.5241
2.5833 | 2018-11-16 06:00 | 0.54918 | 10.4915
2.5903 | 2018-11-16 06:10 | 0.54918 | 10.4915
2.5972 | 2018-11-16 06:20 | 0.49705 | 6.3529
2.6042 | 2018-11-16 06:30 | 0.54877 | 3.0293
2.6111 | 2018-11-16 06:40 | 0.55018 | 1.4581
2.6181 | 2018-11-16 06:50 | 0.53275 | 7.6586
2.625 | 2018-11-16 07:00 | 0.62052 | 6.1057
2.6319 | 2018-11-16 07:10 | 0.62052 | 6.1057
2.6389 | 2018-11-16 07:20 | 0.58231 | 6.112
2.6458 | 2018-11-16 07:30 | 0.61022 | 4.8884
2.6528 | 2018-11-16 07:40 | 0.67054 | 12.7512
2.6597 | 2018-11-16 07:50 | 0.51616 | 14.817
2.6667 | 2018-11-16 08:00 | 0.52179 | 18.0877
2.6736 | 2018-11-16 08:10 | 0.52179 | 18.0877
2.6806 | 2018-11-16 08:20 | 0.51275 | 5.933
2.6875 | 2018-11-16 08:30 | 0.44449 | 6.0697
2.6944 | 2018-11-16 08:40 | 0.42468 | 10.1721
2.7014 | 2018-11-16 08:50 | 0.3682 | 14.7911
2.7083 | 2018-11-16 09:00 | 0.3798 | 6.9566
2.7153 | 2018-11-16 09:10 | 0.3798 | 6.9566
2.7222 | 2018-11-16 09:20 | 0.28991 | 355.4497
2.7292 | 2018-11-16 09:30 | 0.33086 | 353.9276
2.7361 | 2018-11-16 09:40 | 0.18401 | 359.3773
2.7431 | 2018-11-16 09:50 | 0.22532 | 13.6045
2.75 | 2018-11-16 10:00 | 0.18732 | 347.6703
2.7569 | 2018-11-16 10:10 | 0.18732 | 347.6703
2.7639 | 2018-11-16 10:20 | 0.16451 | 4.5323
2.7708 | 2018-11-16 10:30 | 0.085 | 0
2.7778 | 2018-11-16 10:40 | 0.099298 | 350.7274
2.7847 | 2018-11-16 10:50 | 0.029547 | 156.0375
2.7917 | 2018-11-16 11:00 | 0.056613 | 324.3447
2.7986 | 2018-11-16 11:10 | 0.056613 | 324.3447
2.8056 | 2018-11-16 11:20 | 0.053339 | 173.5412
2.8125 | 2018-11-16 11:30 | 0.15603 | 217.9716
2.8194 | 2018-11-16 11:40 | 0.22674 | 190.4179
2.8264 | 2018-11-16 11:50 | 0.28633 | 191.0745
2.8333 | 2018-11-16 12:00 | 0.33916 | 204.7515
2.8403 | 2018-11-16 12:10 | 0.33916 | 204.7515
2.8472 | 2018-11-16 12:20 | 0.34501 | 198.5925
2.8542 | 2018-11-16 12:30 | 0.28211 | 181.625
2.8611 | 2018-11-16 12:40 | 0.3883 | 193.8573
2.8681 | 2018-11-16 12:50 | 0.4005 | 182.8624
2.875 | 2018-11-16 13:00 | 0.32438 | 191.3792
2.8819 | 2018-11-16 13:10 | 0.32438 | 191.3792
2.8889 | 2018-11-16 13:20 | 0.48425 | 190.5906
2.8958 | 2018-11-16 13:30 | 0.38395 | 184.0325
2.9028 | 2018-11-16 13:40 | 0.47077 | 183.2878
2.9097 | 2018-11-16 13:50 | 0.39736 | 182.452
2.9167 | 2018-11-16 14:00 | 0.44529 | 182.0592
2.9236 | 2018-11-16 14:10 | 0.44529 | 182.0592
2.9306 | 2018-11-16 14:20 | 0.53563 | 185.6787
2.9375 | 2018-11-16 14:30 | 0.47924 | 189.9734
2.9444 | 2018-11-16 14:40 | 0.57032 | 192.8666
2.9514 | 2018-11-16 14:50 | 0.42021 | 189.8658
2.9583 | 2018-11-16 15:00 | 0.4128 | 193.7333
2.9653 | 2018-11-16 15:10 | 0.4128 | 193.7333
2.9722 | 2018-11-16 15:20 | 0.44659 | 190.5802
2.9792 | 2018-11-16 15:30 | 0.3932 | 193.082
2.9861 | 2018-11-16 15:40 | 0.37799 | 190.2099
2.9931 | 2018-11-16 15:50 | 0.36114 | 181.5867
3 | 2018-11-16 16:00 | 0.32697 | 187.7336
3.0069 | 2018-11-16 16:10 | 0.32697 | 187.7336
3.0139 | 2018-11-16 16:20 | 0.26571 | 197.071
3.0208 | 2018-11-16 16:30 | 0.27181 | 171.7507
3.0278 | 2018-11-16 16:40 | 0.22082 | 184.936
3.0347 | 2018-11-16 16:50 | 0.21276 | 175.1469
3.0417 | 2018-11-16 17:00 | 0.16736 | 176.2315
3.0486 | 2018-11-16 17:10 | 0.16736 | 176.2315
3.0556 | 2018-11-16 17:20 | 0.069656 | 129.1737
3.0625 | 2018-11-16 17:30 | 0.11454 | 114.7751
3.0694 | 2018-11-16 17:40 | 0.054489 | 132.7688
3.0764 | 2018-11-16 17:50 | 0.1318 | 11.8215
3.0833 | 2018-11-16 18:00 | 0.15829 | 59.2225
3.0903 | 2018-11-16 18:10 | 0.15829 | 59.2225
3.0972 | 2018-11-16 18:20 | 0.16601 | 31.2005
3.1042 | 2018-11-16 18:30 | 0.30602 | 32.184
3.1111 | 2018-11-16 18:40 | 0.24828 | 19.5296
3.1181 | 2018-11-16 18:50 | 0.30392 | 19.21
3.125 | 2018-11-16 19:00 | 0.27322 | 2.3074
3.1319 | 2018-11-16 19:10 | 0.27322 | 2.3074
3.1389 | 2018-11-16 19:20 | 0.48776 | 10.8722
3.1458 | 2018-11-16 19:30 | 0.52694 | 15.4077
3.1528 | 2018-11-16 19:40 | 0.4831 | 15.7336
3.1597 | 2018-11-16 19:50 | 0.50619 | 13.597
3.1667 | 2018-11-16 20:00 | 0.51935 | 13.0194
3.1736 | 2018-11-16 20:10 | 0.51935 | 13.0194
3.1806 | 2018-11-16 20:20 | 0.53806 | 5.0113
3.1875 | 2018-11-16 20:30 | 0.43786 | 7.6119
3.1944 | 2018-11-16 20:40 | 0.34353 | 3.1706
3.2014 | 2018-11-16 20:50 | 0.43603 | 5.5275
3.2083 | 2018-11-16 21:00 | 0.45481 | 8.3439
3.2153 | 2018-11-16 21:10 | 0.45481 | 8.3439
3.2222 | 2018-11-16 21:20 | 0.49172 | 7.9488
3.2292 | 2018-11-16 21:30 | 0.51951 | 9.7524
3.2361 | 2018-11-16 21:40 | 0.3963 | 7.394
3.2431 | 2018-11-16 21:50 | 0.44925 | 1.9134
3.25 | 2018-11-16 22:00 | 0.41464 | 19.44
3.2569 | 2018-11-16 22:10 | 0.41464 | 19.44
3.2639 | 2018-11-16 22:20 | 0.32547 | 7.0595
3.2708 | 2018-11-16 22:30 | 0.21444 | 15.138
3.2778 | 2018-11-16 22:40 | 0.16811 | 34.8245
3.2847 | 2018-11-16 22:50 | 0.153 | 0.37448
3.2917 | 2018-11-16 23:00 | 0.20025 | 2.8624
3.2986 | 2018-11-16 23:10 | 0.20025 | 2.8624
3.3056 | 2018-11-16 23:20 | 0.065765 | 331.8763
3.3125 | 2018-11-16 23:30 | 0.10242 | 9.5543
3.3194 | 2018-11-16 23:40 | 0.021401 | 232.5947
3.3264 | 2018-11-16 23:50 | 0.088023 | 201.3179
3.3333 | 2018-11-17 | 0.067535 | 152.6761
3.3403 | 2018-11-17 00:10 | 0.067535 | 152.6761
3.3472 | 2018-11-17 00:20 | 0.14525 | 172.4836
3.3542 | 2018-11-17 00:30 | 0.17175 | 197.2744
3.3611 | 2018-11-17 00:40 | 0.22138 | 199.2534
3.3681 | 2018-11-17 00:50 | 0.25164 | 200.9558
3.375 | 2018-11-17 01:00 | 0.25564 | 209.2723
3.3819 | 2018-11-17 01:10 | 0.25564 | 209.2723
3.3889 | 2018-11-17 01:20 | 0.37879 | 190.0343
3.3958 | 2018-11-17 01:30 | 0.26661 | 183.8713
3.4028 | 2018-11-17 01:40 | 0.35264 | 174.4672
3.4097 | 2018-11-17 01:50 | 0.36839 | 182.6449
3.4167 | 2018-11-17 02:00 | 0.3139 | 192.8852
3.4236 | 2018-11-17 02:10 | 0.3139 | 192.8852
3.4306 | 2018-11-17 02:20 | 0.32213 | 186.5955
3.4375 | 2018-11-17 02:30 | 0.41402 | 184.0166
3.4444 | 2018-11-17 02:40 | 0.46547 | 194.8125
3.4514 | 2018-11-17 02:50 | 0.43599 | 189.5055
3.4583 | 2018-11-17 03:00 | 0.411 | 180
3.4653 | 2018-11-17 03:10 | 0.411 | 180
3.4722 | 2018-11-17 03:20 | 0.42773 | 191.5989
3.4792 | 2018-11-17 03:30 | 0.48316 | 193.4035
3.4861 | 2018-11-17 03:40 | 0.47579 | 191.6406
3.4931 | 2018-11-17 03:50 | 0.47983 | 186.2215
3.5 | 2018-11-17 04:00 | 0.413 | 180
3.5069 | 2018-11-17 04:10 | 0.413 | 180
3.5139 | 2018-11-17 04:20 | 0.43896 | 192.2315
3.5208 | 2018-11-17 04:30 | 0.329 | 179.8259
3.5278 | 2018-11-17 04:40 | 0.28378 | 191.5871
3.5347 | 2018-11-17 04:50 | 0.27899 | 195.3812
3.5417 | 2018-11-17 05:00 | 0.22843 | 183.5137
3.5486 | 2018-11-17 05:10 | 0.22843 | 183.5137
3.5556 | 2018-11-17 05:20 | 0.15108 | 170.4753
3.5625 | 2018-11-17 05:30 | 0.10595 | 197.5798
3.5694 | 2018-11-17 05:40 | 0.11402 | 178.9949
3.5764 | 2018-11-17 05:50 | 0.060075 | 87.1376
3.5833 | 2018-11-17 06:00 | 0.082492 | 6.2635
3.5903 | 2018-11-17 06:10 | 0.082492 | 6.2635
3.5972 | 2018-11-17 06:20 | 0.16763 | 19.5159
3.6042 | 2018-11-17 06:30 | 0.22901 | 9.2978
3.6111 | 2018-11-17 06:40 | 0.3502 | 30.7393
3.6181 | 2018-11-17 06:50 | 0.37537 | 18.0005
3.625 | 2018-11-17 07:00 | 0.24131 | 17.609
3.6319 | 2018-11-17 07:10 | 0.24131 | 17.609
3.6389 | 2018-11-17 07:20 | 0.38011 | 6.0406
3.6458 | 2018-11-17 07:30 | 0.43836 | 10.5153
3.6528 | 2018-11-17 07:40 | 0.52589 | 18.745
3.6597 | 2018-11-17 07:50 | 0.5003 | 11.0629
3.6667 | 2018-11-17 08:00 | 0.48581 | 13.693
3.6736 | 2018-11-17 08:10 | 0.48581 | 13.693
3.6806 | 2018-11-17 08:20 | 0.52809 | 6.1964
3.6875 | 2018-11-17 08:30 | 0.56325 | 11.4695
3.6944 | 2018-11-17 08:40 | 0.50136 | 7.5644
3.7014 | 2018-11-17 08:50 | 0.47376 | 8.1301
3.7083 | 2018-11-17 09:00 | 0.57719 | 1.4892
3.7153 | 2018-11-17 09:10 | 0.57719 | 1.4892
3.7222 | 2018-11-17 09:20 | 0.56185 | 12.75
3.7292 | 2018-11-17 09:30 | 0.378 | 0
3.7361 | 2018-11-17 09:40 | 0.44152 | 8.2035
3.7431 | 2018-11-17 09:50 | 0.47006 | 5.371
3.75 | 2018-11-17 10:00 | 0.40231 | 10.1647
3.7569 | 2018-11-17 10:10 | 0.40231 | 10.1647
3.7639 | 2018-11-17 10:20 | 0.3965 | 2.8913
3.7708 | 2018-11-17 10:30 | 0.34027 | 11.0127
3.7778 | 2018-11-17 10:40 | 0.38185 | 10.8685
3.7847 | 2018-11-17 10:50 | 0.37646 | 6.5587
3.7917 | 2018-11-17 11:00 | 0.29947 | 10.9722
3.7986 | 2018-11-17 11:10 | 0.29947 | 10.9722
3.8056 | 2018-11-17 11:20 | 0.33305 | 7.7652
3.8125 | 2018-11-17 11:30 | 0.18014 | 357.7729
3.8194 | 2018-11-17 11:40 | 0.1695 | 355.6013
3.8264 | 2018-11-17 11:50 | 0.12588 | 38.8731
3.8333 | 2018-11-17 12:00 | 0.10187 | 13.627
3.8403 | 2018-11-17 12:10 | 0.10187 | 13.627
3.8472 | 2018-11-17 12:20 | 0.053339 | 329.5889
3.8542 | 2018-11-17 12:30 | 0.053339 | 6.4588
3.8611 | 2018-11-17 12:40 | 0.015 | 180
3.8681 | 2018-11-17 12:50 | 0.053759 | 161.565
3.875 | 2018-11-17 13:00 | 0.049041 | 140.7928
3.8819 | 2018-11-17 13:10 | 0.049041 | 140.7928
3.8889 | 2018-11-17 13:20 | 0.22287 | 204.3801
3.8958 | 2018-11-17 13:30 | 0.17716 | 210.9083
3.9028 | 2018-11-17 13:40 | 0.26502 | 189.9955
3.9097 | 2018-11-17 13:50 | 0.29155 | 185.9061
3.9167 | 2018-11-17 14:00 | 0.35483 | 185.8231
3.9236 | 2018-11-17 14:10 | 0.35483 | 185.8231
3.9306 | 2018-11-17 14:20 | 0.37836 | 194.073
3.9375 | 2018-11-17 14:30 | 0.44033 | 182.2126
3.9444 | 2018-11-17 14:40 | 0.40121 | 181.8568
3.9514 | 2018-11-17 14:50 | 0.42423 | 181.8912
3.9583 | 2018-11-17 15:00 | 0.42938 | 182.4026
3.9653 | 2018-11-17 15:10 | 0.42938 | 182.4026
3.9722 | 2018-11-17 15:20 | 0.4892 | 178.3601
3.9792 | 2018-11-17 15:30 | 0.51851 | 185.6446
3.9861 | 2018-11-17 15:40 | 0.62344 | 188.858
3.9931 | 2018-11-17 15:50 | 0.45446 | 187.0781
4 | 2018-11-17 16:00 | 0.47873 | 189.6197
4.0069 | 2018-11-17 16:10 | 0.47873 | 189.6197
4.0139 | 2018-11-17 16:20 | 0.48726 | 184.1191
4.0208 | 2018-11-17 16:30 | 0.42163 | 183.1271
4.0278 | 2018-11-17 16:40 | 0.45812 | 184.0054
4.0347 | 2018-11-17 16:50 | 0.41401 | 193.8349
4.0417 | 2018-11-17 17:00 | 0.43342 | 193.7477
4.0486 | 2018-11-17 17:10 | 0.43342 | 193.7477
4.0556 | 2018-11-17 17:20 | 0.42929 | 193.7449
4.0625 | 2018-11-17 17:30 | 0.33791 | 168.3908
4.0694 | 2018-11-17 17:40 | 0.379 | 180
4.0764 | 2018-11-17 17:50 | 0.36502 | 188.5075
4.0833 | 2018-11-17 18:00 | 0.32339 | 185.3228
4.0903 | 2018-11-17 18:10 | 0.32339 | 185.3228
4.0972 | 2018-11-17 18:20 | 0.12398 | 167.4211
4.1042 | 2018-11-17 18:30 | 0.1261 | 182.2724
4.1111 | 2018-11-17 18:40 | 0.14129 | 183.6522
4.1181 | 2018-11-17 18:50 | 0.19321 | 177.3301
4.125 | 2018-11-17 19:00 | 0.12357 | 156.1317
4.1319 | 2018-11-17 19:10 | 0.12357 | 156.1317
4.1389 | 2018-11-17 19:20 | 0.07267 | 34.3461
4.1458 | 2018-11-17 19:30 | 0.067357 | 18.166
4.1528 | 2018-11-17 19:40 | 0.091548 | 21.8014
4.1597 | 2018-11-17 19:50 | 0.15788 | 42.176
4.1667 | 2018-11-17 20:00 | 0.26 | 14.25
4.1736 | 2018-11-17 20:10 | 0.26 | 14.25
4.1806 | 2018-11-17 20:20 | 0.35023 | 21.4369
4.1875 | 2018-11-17 20:30 | 0.40029 | 15.3555
4.1944 | 2018-11-17 20:40 | 0.37357 | 12.9946
4.2014 | 2018-11-17 20:50 | 0.42231 | 16.9332
4.2083 | 2018-11-17 21:00 | 0.39951 | 11.8443
4.2153 | 2018-11-17 21:10 | 0.39951 | 11.8443
4.2222 | 2018-11-17 21:20 | 0.41253 | 8.5033
4.2292 | 2018-11-17 21:30 | 0.43172 | 3.3197
4.2361 | 2018-11-17 21:40 | 0.49032 | 8.4441
4.2431 | 2018-11-17 21:50 | 0.43106 | 9.6153
4.25 | 2018-11-17 22:00 | 0.5242 | 5.2538
4.2569 | 2018-11-17 22:10 | 0.5242 | 5.2538
4.2639 | 2018-11-17 22:20 | 0.40702 | 0.56309
4.2708 | 2018-11-17 22:30 | 0.39374 | 5.392
4.2778 | 2018-11-17 22:40 | 0.37305 | 13.3285
4.2847 | 2018-11-17 22:50 | 0.40077 | 6.7349
4.2917 | 2018-11-17 23:00 | 0.399 | 0.1436
4.2986 | 2018-11-17 23:10 | 0.399 | 0.1436
4.3056 | 2018-11-17 23:20 | 0.31416 | 1.8241
4.3125 | 2018-11-17 23:30 | 0.2792 | 7.2014
4.3194 | 2018-11-17 23:40 | 0.2784 | 356.9115
4.3264 | 2018-11-17 23:50 | 0.23402 | 359.2655
4.3333 | 2018-11-18 | 0.23208 | 1.4815
4.3403 | 2018-11-18 00:10 | 0.23208 | 1.4815
4.3472 | 2018-11-18 00:20 | 0.21623 | 8.2425
4.3542 | 2018-11-18 00:30 | 0.117 | 0.4897
4.3611 | 2018-11-18 00:40 | 0.15494 | 43.1692
4.3681 | 2018-11-18 00:50 | 0.14235 | 355.9717
4.375 | 2018-11-18 01:00 | 0.067978 | 333.8119
4.3819 | 2018-11-18 01:10 | 0.067978 | 333.8119
4.3889 | 2018-11-18 01:20 | 0.048384 | 161.9395
4.3958 | 2018-11-18 01:30 | 0.05794 | 111.2505
4.4028 | 2018-11-18 01:40 | 0.21645 | 173.3675
4.4097 | 2018-11-18 01:50 | 0.27325 | 169.8827
4.4167 | 2018-11-18 02:00 | 0.34149 | 194.2397
4.4236 | 2018-11-18 02:10 | 0.34149 | 194.2397
4.4306 | 2018-11-18 02:20 | 0.33491 | 171.2408
4.4375 | 2018-11-18 02:30 | 0.35415 | 193.0553
4.4444 | 2018-11-18 02:40 | 0.43434 | 185.9469
4.4514 | 2018-11-18 02:50 | 0.4298 | 186.5463
4.4583 | 2018-11-18 03:00 | 0.44406 | 180.9032
4.4653 | 2018-11-18 03:10 | 0.44406 | 180.9032
4.4722 | 2018-11-18 03:20 | 0.49898 | 188.8771
4.4792 | 2018-11-18 03:30 | 0.44463 | 184.9028
4.4861 | 2018-11-18 03:40 | 0.51014 | 181.3479
4.4931 | 2018-11-18 03:50 | 0.46092 | 187.4796
4.5 | 2018-11-18 04:00 | 0.55713 | 186.079
4.5069 | 2018-11-18 04:10 | 0.55713 | 186.079
4.5139 | 2018-11-18 04:20 | 0.49623 | 174.5651
4.5208 | 2018-11-18 04:30 | 0.51673 | 186.8912
4.5278 | 2018-11-18 04:40 | 0.48989 | 185.0356
4.5347 | 2018-11-18 04:50 | 0.43859 | 187.3357
4.5417 | 2018-11-18 05:00 | 0.42343 | 190.7527
4.5486 | 2018-11-18 05:10 | 0.42343 | 190.7527
4.5556 | 2018-11-18 05:20 | 0.60208 | 179.0483
4.5625 | 2018-11-18 05:30 | 0.39685 | 176.2435
4.5694 | 2018-11-18 05:40 | 0.39341 | 189.5102
4.5764 | 2018-11-18 05:50 | 0.36954 | 176.8976
4.5833 | 2018-11-18 06:00 | 0.30101 | 179.6193
4.5903 | 2018-11-18 06:10 | 0.30101 | 179.6193
4.5972 | 2018-11-18 06:20 | 0.29971 | 170.9777
4.6042 | 2018-11-18 06:30 | 0.28745 | 176.8091
4.6111 | 2018-11-18 06:40 | 0.22332 | 176.9198
4.6181 | 2018-11-18 06:50 | 0.21242 | 171.3359
4.625 | 2018-11-18 07:00 | 0.19745 | 159.5458
4.6319 | 2018-11-18 07:10 | 0.19745 | 159.5458
4.6389 | 2018-11-18 07:20 | 0.16254 | 145.5278
4.6458 | 2018-11-18 07:30 | 0.10234 | 146.1547
4.6528 | 2018-11-18 07:40 | 0.08864 | 66.0375
4.6597 | 2018-11-18 07:50 | 0.1508 | 36.6419
4.6667 | 2018-11-18 08:00 | 0.15893 | 33.1901
4.6736 | 2018-11-18 08:10 | 0.15893 | 33.1901
4.6806 | 2018-11-18 08:20 | 0.30528 | 30.5131
4.6875 | 2018-11-18 08:30 | 0.37977 | 22.4458
4.6944 | 2018-11-18 08:40 | 0.41848 | 17.0927
4.7014 | 2018-11-18 08:50 | 0.41812 | 11.3099
4.7083 | 2018-11-18 09:00 | 0.44727 | 6.9343
4.7153 | 2018-11-18 09:10 | 0.44727 | 6.9343
4.7222 | 2018-11-18 09:20 | 0.41105 | 5.7245
4.7292 | 2018-11-18 09:30 | 0.38823 | 7.3996
4.7361 | 2018-11-18 09:40 | 0.5041 | 10.2845
4.7431 | 2018-11-18 09:50 | 0.46304 | 6.5725
4.75 | 2018-11-18 10:00 | 0.48961 | 7.8653
4.7569 | 2018-11-18 10:10 | 0.48961 | 7.8653
4.7639 | 2018-11-18 10:20 | 0.50701 | 0.33902
4.7708 | 2018-11-18 10:30 | 0.57419 | 3.6946
4.7778 | 2018-11-18 10:40 | 0.52768 | 12.5877
4.7847 | 2018-11-18 10:50 | 0.54009 | 7.8751
4.7917 | 2018-11-18 11:00 | 0.52012 | 11.8716
4.7986 | 2018-11-18 11:10 | 0.52012 | 11.8716
4.8056 | 2018-11-18 11:20 | 0.4044 | 10.9765
4.8125 | 2018-11-18 11:30 | 0.4658 | 6.2859
4.8194 | 2018-11-18 11:40 | 0.39813 | 10.8583
4.8264 | 2018-11-18 11:50 | 0.34658 | 3.3082
4.8333 | 2018-11-18 12:00 | 0.35703 | 18.7902
4.8403 | 2018-11-18 12:10 | 0.35703 | 18.7902
4.8472 | 2018-11-18 12:20 | 0.3223 | 2.4896
4.8542 | 2018-11-18 12:30 | 0.27918 | 2.0527
4.8611 | 2018-11-18 12:40 | 0.17818 | 2.5734
4.8681 | 2018-11-18 12:50 | 0.11922 | 8.1981
4.875 | 2018-11-18 13:00 | 0.135 | 0
4.8819 | 2018-11-18 13:10 | 0.135 | 0
4.8889 | 2018-11-18 13:20 | 0.10715 | 22.4965
4.8958 | 2018-11-18 13:30 | 0.05021 | 315.8069
4.9028 | 2018-11-18 13:40 | 0.042544 | 293.5523
4.9097 | 2018-11-18 13:50 | 0.073817 | 215.6279
4.9167 | 2018-11-18 14:00 | 0.072367 | 191.1547
4.9236 | 2018-11-18 14:10 | 0.072367 | 191.1547
4.9306 | 2018-11-18 14:20 | 0.25804 | 206.4658
4.9375 | 2018-11-18 14:30 | 0.27241 | 196.6388
4.9444 | 2018-11-18 14:40 | 0.31527 | 177.6367
4.9514 | 2018-11-18 14:50 | 0.3672 | 181.8728
4.9583 | 2018-11-18 15:00 | 0.33269 | 195.8744
4.9653 | 2018-11-18 15:10 | 0.33269 | 195.8744
4.9722 | 2018-11-18 15:20 | 0.45603 | 185.4106
4.9792 | 2018-11-18 15:30 | 0.53545 | 189.5679
4.9861 | 2018-11-18 15:40 | 0.51749 | 187.5508
4.9931 | 2018-11-18 15:50 | 0.5071 | 178.8701
5 | 2018-11-18 16:00 | 0.63186 | 182.9937
5.0069 | 2018-11-18 16:10 | 0.63186 | 182.9937
5.0139 | 2018-11-18 16:20 | 0.58669 | 187.2462
5.0208 | 2018-11-18 16:30 | 0.60896 | 185.6544
5.0278 | 2018-11-18 16:40 | 0.46966 | 188.0783
5.0347 | 2018-11-18 16:50 | 0.53662 | 185.6681
5.0417 | 2018-11-18 17:00 | 0.56647 | 187.2003
5.0486 | 2018-11-18 17:10 | 0.56647 | 187.2003
5.0556 | 2018-11-18 17:20 | 0.46517 | 175.9319
5.0625 | 2018-11-18 17:30 | 0.52434 | 182.0766
5.0694 | 2018-11-18 17:40 | 0.58094 | 190.6136
5.0764 | 2018-11-18 17:50 | 0.54259 | 193.3191
5.0833 | 2018-11-18 18:00 | 0.5333 | 188.0845
5.0903 | 2018-11-18 18:10 | 0.5333 | 188.0845
5.0972 | 2018-11-18 18:20 | 0.4554 | 182.3912
5.1042 | 2018-11-18 18:30 | 0.39796 | 188.0894
5.1111 | 2018-11-18 18:40 | 0.33928 | 191.045
5.1181 | 2018-11-18 18:50 | 0.36393 | 175.9032
5.125 | 2018-11-18 19:00 | 0.40098 | 175.9958
5.1319 | 2018-11-18 19:10 | 0.40098 | 175.9958
5.1389 | 2018-11-18 19:20 | 0.26905 | 178.9352
5.1458 | 2018-11-18 19:30 | 0.26666 | 189.4977
5.1528 | 2018-11-18 19:40 | 0.23109 | 172.2907
5.1597 | 2018-11-18 19:50 | 0.070711 | 151.2602
5.1667 | 2018-11-18 20:00 | 0.1729 | 138.7517
5.1736 | 2018-11-18 20:10 | 0.1729 | 138.7517
5.1806 | 2018-11-18 20:20 | 0.057009 | 91.0051
5.1875 | 2018-11-18 20:30 | 0.086023 | 35.5377
5.1944 | 2018-11-18 20:40 | 0.111 | 0
5.2014 | 2018-11-18 20:50 | 0.15925 | 25.2777
5.2083 | 2018-11-18 21:00 | 0.17094 | 49.5078
5.2153 | 2018-11-18 21:10 | 0.17094 | 49.5078
5.2222 | 2018-11-18 21:20 | 0.287 | 12.6804
5.2292 | 2018-11-18 21:30 | 0.32888 | 18.435
5.2361 | 2018-11-18 21:40 | 0.34787 | 9.5977
5.2431 | 2018-11-18 21:50 | 0.36891 | 14.6013
5.25 | 2018-11-18 22:00 | 0.37252 | 18.6295
5.2569 | 2018-11-18 22:10 | 0.37252 | 18.6295
5.2639 | 2018-11-18 22:20 | 0.39806 | 20.4381
5.2708 | 2018-11-18 22:30 | 0.41136 | 14.6443
5.2778 | 2018-11-18 22:40 | 0.32419 | 1.9445
5.2847 | 2018-11-18 22:50 | 0.48628 | 13.9219
5.2917 | 2018-11-18 23:00 | 0.34201 | 13.183
5.2986 | 2018-11-18 23:10 | 0.34201 | 13.183
5.3056 | 2018-11-18 23:20 | 0.38107 | 11.8112
5.3125 | 2018-11-18 23:30 | 0.37934 | 2.4174
5.3194 | 2018-11-18 23:40 | 0.39174 | 7.9233
5.3264 | 2018-11-18 23:50 | 0.30537 | 13.4446
5.3333 | 2018-11-19 | 0.28798 | 12.6367
5.3403 | 2018-11-19 00:10 | 0.28798 | 12.6367
5.3472 | 2018-11-19 00:20 | 0.3507 | 10.3487
5.3542 | 2018-11-19 00:30 | 0.32666 | 9.693
5.3611 | 2018-11-19 00:40 | 0.29045 | 11.1165
5.3681 | 2018-11-19 00:50 | 0.29039 | 357.0391
5.375 | 2018-11-19 01:00 | 0.22008 | 12.3311
5.3819 | 2018-11-19 01:10 | 0.22008 | 12.3311
5.3889 | 2018-11-19 01:20 | 0.25689 | 16.742
5.3958 | 2018-11-19 01:30 | 0.19191 | 8.0879
5.4028 | 2018-11-19 01:40 | 0.056754 | 104.2811
5.4097 | 2018-11-19 01:50 | 0.059775 | 342.4744
5.4167 | 2018-11-19 02:00 | 0.10723 | 176.257
5.4236 | 2018-11-19 02:10 | 0.10723 | 176.257
5.4306 | 2018-11-19 02:20 | 0.16844 | 187.5047
5.4375 | 2018-11-19 02:30 | 0.15081 | 191.0864
5.4444 | 2018-11-19 02:40 | 0.25653 | 191.9232
5.4514 | 2018-11-19 02:50 | 0.29642 | 185.6144
5.4583 | 2018-11-19 03:00 | 0.33917 | 171.0098
5.4653 | 2018-11-19 03:10 | 0.33917 | 171.0098
5.4722 | 2018-11-19 03:20 | 0.3762 | 184.5739
5.4792 | 2018-11-19 03:30 | 0.47579 | 188.9476
5.4861 | 2018-11-19 03:40 | 0.49827 | 186.5688
5.4931 | 2018-11-19 03:50 | 0.52322 | 181.6428
5.5 | 2018-11-19 04:00 | 0.54899 | 183.4461
5.5069 | 2018-11-19 04:10 | 0.54899 | 183.4461
5.5139 | 2018-11-19 04:20 | 0.57159 | 182.6071
5.5208 | 2018-11-19 04:30 | 0.5097 | 188.5752
5.5278 | 2018-11-19 04:40 | 0.55981 | 184.6107
5.5347 | 2018-11-19 04:50 | 0.59673 | 185.4813
5.5417 | 2018-11-19 05:00 | 0.62728 | 183.6561
5.5486 | 2018-11-19 05:10 | 0.62728 | 183.6561
5.5556 | 2018-11-19 05:20 | 0.58242 | 185.2211
5.5625 | 2018-11-19 05:30 | 0.60532 | 189.509
5.5694 | 2018-11-19 05:40 | 0.53051 | 187.4733
5.5764 | 2018-11-19 05:50 | 0.61402 | 192.7009
5.5833 | 2018-11-19 06:00 | 0.61622 | 186.7098
5.5903 | 2018-11-19 06:10 | 0.61622 | 186.7098
5.5972 | 2018-11-19 06:20 | 0.54005 | 187.0197
5.6042 | 2018-11-19 06:30 | 0.5283 | 186.412
5.6111 | 2018-11-19 06:40 | 0.42347 | 182.707
5.6181 | 2018-11-19 06:50 | 0.49211 | 183.845
5.625 | 2018-11-19 07:00 | 0.40895 | 186.8817
5.6319 | 2018-11-19 07:10 | 0.40895 | 186.8817
5.6389 | 2018-11-19 07:20 | 0.39479 | 176.3694
5.6458 | 2018-11-19 07:30 | 0.36739 | 182.6521
5.6528 | 2018-11-19 07:40 | 0.29938 | 177.128
5.6597 | 2018-11-19 07:50 | 0.25251 | 183.6329
5.6667 | 2018-11-19 08:00 | 0.23455 | 183.9116
5.6736 | 2018-11-19 08:10 | 0.23455 | 183.9116
5.6806 | 2018-11-19 08:20 | 0.073824 | 151.6992
5.6875 | 2018-11-19 08:30 | 0.12182 | 127.9987
5.6944 | 2018-11-19 08:40 | 0.075392 | 68.1986
5.7014 | 2018-11-19 08:50 | 0.14066 | 57.7787
5.7083 | 2018-11-19 09:00 | 0.22931 | 17.2497
5.7153 | 2018-11-19 09:10 | 0.22931 | 17.2497
5.7222 | 2018-11-19 09:20 | 0.3356 | 24.6559
5.7292 | 2018-11-19 09:30 | 0.40638 | 19.1037
5.7361 | 2018-11-19 09:40 | 0.34667 | 5.6284
5.7431 | 2018-11-19 09:50 | 0.35328 | 4.8714
5.75 | 2018-11-19 10:00 | 0.44754 | 11.2095
5.7569 | 2018-11-19 10:10 | 0.44754 | 11.2095
5.7639 | 2018-11-19 10:20 | 0.4878 | 13.1531
5.7708 | 2018-11-19 10:30 | 0.54161 | 14.652
5.7778 | 2018-11-19 10:40 | 0.42859 | 9.2645
5.7847 | 2018-11-19 10:50 | 0.56953 | 11.0337
5.7917 | 2018-11-19 11:00 | 0.57253 | 10.466
5.7986 | 2018-11-19 11:10 | 0.57253 | 10.466
5.8056 | 2018-11-19 11:20 | 0.67464 | 17.3338
5.8125 | 2018-11-19 11:30 | 0.56144 | 7.9858
5.8194 | 2018-11-19 11:40 | 0.45216 | 1.5208
5.8264 | 2018-11-19 11:50 | 0.45801 | 359.6247
5.8333 | 2018-11-19 12:00 | 0.49901 | 359.6555
5.8403 | 2018-11-19 12:10 | 0.49901 | 359.6555
5.8472 | 2018-11-19 12:20 | 0.44651 | 14.1296
5.8542 | 2018-11-19 12:30 | 0.33712 | 1.5298
5.8611 | 2018-11-19 12:40 | 0.2983 | 7.125
5.8681 | 2018-11-19 12:50 | 0.33987 | 11.5414
5.875 | 2018-11-19 13:00 | 0.39004 | 8.2547
5.8819 | 2018-11-19 13:10 | 0.39004 | 8.2547
5.8889 | 2018-11-19 13:20 | 0.33304 | 0.86023
5.8958 | 2018-11-19 13:30 | 0.19191 | 351.9121
5.9028 | 2018-11-19 13:40 | 0.24502 | 347.2683
5.9097 | 2018-11-19 13:50 | 0.19958 | 350.7737
5.9167 | 2018-11-19 14:00 | 0.17801 | 332.5713
5.9236 | 2018-11-19 14:10 | 0.17801 | 332.5713
5.9306 | 2018-11-19 14:20 | 0.10279 | 287.5536
5.9375 | 2018-11-19 14:30 | 0.007 | 180
5.9444 | 2018-11-19 14:40 | 0.09827 | 238.7363
5.9514 | 2018-11-19 14:50 | 0.18724 | 203.2789
5.9583 | 2018-11-19 15:00 | 0.2292 | 194.4
5.9653 | 2018-11-19 15:10 | 0.2292 | 194.4
5.9722 | 2018-11-19 15:20 | 0.41842 | 190.0476
5.9792 | 2018-11-19 15:30 | 0.38862 | 183.2453
5.9861 | 2018-11-19 15:40 | 0.47994 | 183.5838
5.9931 | 2018-11-19 15:50 | 0.43865 | 184.9697
6 | 2018-11-19 16:00 | 0.48956 | 184.5693
6.0069 | 2018-11-19 16:10 | 0.48956 | 184.5693
6.0139 | 2018-11-19 16:20 | 0.6007 | 191.3286
6.0208 | 2018-11-19 16:30 | 0.54654 | 175.6978
6.0278 | 2018-11-19 16:40 | 0.53901 | 176.49
6.0347 | 2018-11-19 16:50 | 0.57056 | 185.4308
6.0417 | 2018-11-19 17:00 | 0.67423 | 189.9932
6.0486 | 2018-11-19 17:10 | 0.67423 | 189.9932
6.0556 | 2018-11-19 17:20 | 0.69809 | 180.9029
6.0625 | 2018-11-19 17:30 | 0.72862 | 182.3598
6.0694 | 2018-11-19 17:40 | 0.74282 | 182.7006
6.0764 | 2018-11-19 17:50 | 0.73715 | 181.166
6.0833 | 2018-11-19 18:00 | 0.67607 | 183.2221
6.0903 | 2018-11-19 18:10 | 0.67607 | 183.2221
6.0972 | 2018-11-19 18:20 | 0.72574 | 184.98
6.1042 | 2018-11-19 18:30 | 0.70603 | 179.4319
6.1111 | 2018-11-19 18:40 | 0.6124 | 177.9412
6.1181 | 2018-11-19 18:50 | 0.5853 | 183.8206
6.125 | 2018-11-19 19:00 | 0.66173 | 186.8565
6.1319 | 2018-11-19 19:10 | 0.66173 | 186.8565
6.1389 | 2018-11-19 19:20 | 0.63828 | 181.7058
6.1458 | 2018-11-19 19:30 | 0.6258 | 187.8064
6.1528 | 2018-11-19 19:40 | 0.50657 | 185.7781
6.1597 | 2018-11-19 19:50 | 0.619 | 180.1851
6.1667 | 2018-11-19 20:00 | 0.48513 | 186.5098
6.1736 | 2018-11-19 20:10 | 0.48513 | 186.5098
6.1806 | 2018-11-19 20:20 | 0.40941 | 166.4389
6.1875 | 2018-11-19 20:30 | 0.41502 | 180.5522
6.1944 | 2018-11-19 20:40 | 0.36598 | 168.0146
6.2014 | 2018-11-19 20:50 | 0.28934 | 177.2266
6.2083 | 2018-11-19 21:00 | 0.10551 | 194.8265
6.2153 | 2018-11-19 21:10 | 0.10551 | 194.8265
6.2222 | 2018-11-19 21:20 | 0.12107 | 178.1066
6.2292 | 2018-11-19 21:30 | 0.059093 | 113.9625
6.2361 | 2018-11-19 21:40 | 0.1461 | 72.0611
6.2431 | 2018-11-19 21:50 | 0.10466 | 44.2258
6.25 | 2018-11-19 22:00 | 0.22993 | 25.2277
6.2569 | 2018-11-19 22:10 | 0.22993 | 25.2277
6.2639 | 2018-11-19 22:20 | 0.22528 | 6.1155
6.2708 | 2018-11-19 22:30 | 0.26816 | 21.2063
6.2778 | 2018-11-19 22:40 | 0.36487 | 8.3522
6.2847 | 2018-11-19 22:50 | 0.37697 | 9.3124
6.2917 | 2018-11-19 23:00 | 0.35413 | 7.6267
6.2986 | 2018-11-19 23:10 | 0.35413 | 7.6267
6.3056 | 2018-11-19 23:20 | 0.29838 | 357.1184
6.3125 | 2018-11-19 23:30 | 0.47295 | 3.6368
6.3194 | 2018-11-19 23:40 | 0.45842 | 13.3693
6.3264 | 2018-11-19 23:50 | 0.48665 | 4.7148
6.3333 | 2018-11-20 | 0.48705 | 3.7671
6.3403 | 2018-11-20 00:10 | 0.48705 | 3.7671
6.3472 | 2018-11-20 00:20 | 0.45644 | 2.5114
6.3542 | 2018-11-20 00:30 | 0.42347 | 2.707
6.3611 | 2018-11-20 00:40 | 0.37593 | 13.8514
6.3681 | 2018-11-20 00:50 | 0.36902 | 0.62107
6.375 | 2018-11-20 01:00 | 0.33315 | 358.2799
6.3819 | 2018-11-20 01:10 | 0.33315 | 358.2799
6.3889 | 2018-11-20 01:20 | 0.35681 | 8.3799
6.3958 | 2018-11-20 01:30 | 0.37127 | 19.0206
6.4028 | 2018-11-20 01:40 | 0.33889 | 11.5752
6.4097 | 2018-11-20 01:50 | 0.26215 | 1.9674
6.4167 | 2018-11-20 02:00 | 0.20863 | 9.1011
6.4236 | 2018-11-20 02:10 | 0.20863 | 9.1011
6.4306 | 2018-11-20 02:20 | 0.046615 | 22.7144
6.4375 | 2018-11-20 02:30 | 0.079762 | 277.9269
6.4444 | 2018-11-20 02:40 | 0.092195 | 167.4712
6.4514 | 2018-11-20 02:50 | 0.12629 | 200.8746
6.4583 | 2018-11-20 03:00 | 0.17674 | 190.1019
6.4653 | 2018-11-20 03:10 | 0.17674 | 190.1019
6.4722 | 2018-11-20 03:20 | 0.33846 | 195.5966
6.4792 | 2018-11-20 03:30 | 0.33915 | 178.3103
6.4861 | 2018-11-20 03:40 | 0.46918 | 178.4122
6.4931 | 2018-11-20 03:50 | 0.50103 | 185.153
6.5 | 2018-11-20 04:00 | 0.59322 | 178.4545
6.5069 | 2018-11-20 04:10 | 0.59322 | 178.4545
6.5139 | 2018-11-20 04:20 | 0.67324 | 181.5321
6.5208 | 2018-11-20 04:30 | 0.62454 | 187.6371
6.5278 | 2018-11-20 04:40 | 0.70456 | 182.2776
6.5347 | 2018-11-20 04:50 | 0.74575 | 183.9214
6.5417 | 2018-11-20 05:00 | 0.66913 | 188.9415
6.5486 | 2018-11-20 05:10 | 0.66913 | 188.9415
6.5556 | 2018-11-20 05:20 | 0.82374 | 182.4352
6.5625 | 2018-11-20 05:30 | 0.77679 | 182.5825
6.5694 | 2018-11-20 05:40 | 0.74067 | 188.7756
6.5764 | 2018-11-20 05:50 | 0.75726 | 181.5134
6.5833 | 2018-11-20 06:00 | 0.73186 | 187.8533
6.5903 | 2018-11-20 06:10 | 0.73186 | 187.8533
6.5972 | 2018-11-20 06:20 | 0.83532 | 181.5778
6.6042 | 2018-11-20 06:30 | 0.7756 | 187.4824
6.6111 | 2018-11-20 06:40 | 0.62235 | 181.9337
6.6181 | 2018-11-20 06:50 | 0.77936 | 183.3837
6.625 | 2018-11-20 07:00 | 0.70688 | 186.009
6.6319 | 2018-11-20 07:10 | 0.70688 | 186.009
6.6389 | 2018-11-20 07:20 | 0.65501 | 179.7376
6.6458 | 2018-11-20 07:30 | 0.57011 | 184.9306
6.6528 | 2018-11-20 07:40 | 0.6023 | 181.8077
6.6597 | 2018-11-20 07:50 | 0.48659 | 186.9644
6.6667 | 2018-11-20 08:00 | 0.46499 | 185.306
6.6736 | 2018-11-20 08:10 | 0.46499 | 185.306
6.6806 | 2018-11-20 08:20 | 0.494 | 180.232
6.6875 | 2018-11-20 08:30 | 0.37944 | 172.2756
6.6944 | 2018-11-20 08:40 | 0.26829 | 168.6063
6.7014 | 2018-11-20 08:50 | 0.3561 | 175.4902
6.7083 | 2018-11-20 09:00 | 0.24163 | 142.229
6.7153 | 2018-11-20 09:10 | 0.24163 | 142.229
6.7222 | 2018-11-20 09:20 | 0.10993 | 148.7681
6.7292 | 2018-11-20 09:30 | 0.057245 | 160.6155
6.7361 | 2018-11-20 09:40 | 0.11819 | 66.0375
6.7431 | 2018-11-20 09:50 | 0.13201 | 49.9166
6.75 | 2018-11-20 10:00 | 0.26799 | 45.1512
6.7569 | 2018-11-20 10:10 | 0.26799 | 45.1512
6.7639 | 2018-11-20 10:20 | 0.21205 | 12.5288
6.7708 | 2018-11-20 10:30 | 0.32321 | 15.7993
6.7778 | 2018-11-20 10:40 | 0.33697 | 15.3148
6.7847 | 2018-11-20 10:50 | 0.31829 | 16.613
6.7917 | 2018-11-20 11:00 | 0.43815 | 8.7959
6.7986 | 2018-11-20 11:10 | 0.43815 | 8.7959
6.8056 | 2018-11-20 11:20 | 0.44864 | 3.0665
6.8125 | 2018-11-20 11:30 | 0.55036 | 2.0826
6.8194 | 2018-11-20 11:40 | 0.621 | 10.2966
6.8264 | 2018-11-20 11:50 | 0.5909 | 11.5191
6.8333 | 2018-11-20 12:00 | 0.59785 | 7.3033
6.8403 | 2018-11-20 12:10 | 0.59785 | 7.3033
6.8472 | 2018-11-20 12:20 | 0.56232 | 5.2037
6.8542 | 2018-11-20 12:30 | 0.59306 | 11.5752
6.8611 | 2018-11-20 12:40 | 0.65791 | 7.6867
6.8681 | 2018-11-20 12:50 | 0.55665 | 20.6163
6.875 | 2018-11-20 13:00 | 0.58201 | 10.0935
6.8819 | 2018-11-20 13:10 | 0.58201 | 10.0935
6.8889 | 2018-11-20 13:20 | 0.30017 | 353.1118
6.8958 | 2018-11-20 13:30 | 0.42186 | 6.6702
6.9028 | 2018-11-20 13:40 | 0.37643 | 16.9908
6.9097 | 2018-11-20 13:50 | 0.29498 | 355.3331
6.9167 | 2018-11-20 14:00 | 0.27899 | 350.3013
6.9236 | 2018-11-20 14:10 | 0.27899 | 350.3013
6.9306 | 2018-11-20 14:20 | 0.257 | 0.22294
6.9375 | 2018-11-20 14:30 | 0.18559 | 347.2368
6.9444 | 2018-11-20 14:40 | 0.16672 | 349.6337
6.9514 | 2018-11-20 14:50 | 0.032016 | 308.6598
6.9583 | 2018-11-20 15:00 | 0.020616 | 112.8337
6.9653 | 2018-11-20 15:10 | 0.020616 | 112.8337
6.9722 | 2018-11-20 15:20 | 0.069893 | 199.2127
6.9792 | 2018-11-20 15:30 | 0.13169 | 170.8238
6.9861 | 2018-11-20 15:40 | 0.26341 | 153.6295
6.9931 | 2018-11-20 15:50 | 0.30101 | 179.429
7 | 2018-11-20 16:00 | 0.34829 | 184.9412
7.0069 | 2018-11-20 16:10 | 0.34829 | 184.9412
7.0139 | 2018-11-20 16:20 | 0.42434 | 182.296
7.0208 | 2018-11-20 16:30 | 0.54477 | 183.0515
7.0278 | 2018-11-20 16:40 | 0.63208 | 179.0935
7.0347 | 2018-11-20 16:50 | 0.59501 | 173.3408
7.0417 | 2018-11-20 17:00 | 0.67022 | 178.5465
7.0486 | 2018-11-20 17:10 | 0.67022 | 178.5465
7.0556 | 2018-11-20 17:20 | 0.6517 | 187.583
7.0625 | 2018-11-20 17:30 | 0.64538 | 185.8696
7.0694 | 2018-11-20 17:40 | 0.60496 | 183.2219
7.0764 | 2018-11-20 17:50 | 0.64851 | 185.0424
7.0833 | 2018-11-20 18:00 | 0.78614 | 175.769
7.0903 | 2018-11-20 18:10 | 0.78614 | 175.769
7.0972 | 2018-11-20 18:20 | 0.71029 | 175.3971
7.1042 | 2018-11-20 18:30 | 0.80306 | 180.7135
7.1111 | 2018-11-20 18:40 | 0.81122 | 184.2416
7.1181 | 2018-11-20 18:50 | 0.79708 | 180.7907
7.125 | 2018-11-20 19:00 | 0.78753 | 183.5673
7.1319 | 2018-11-20 19:10 | 0.78753 | 183.5673
7.1389 | 2018-11-20 19:20 | 0.71463 | 182.406
7.1458 | 2018-11-20 19:30 | 0.77747 | 181.9902
7.1528 | 2018-11-20 19:40 | 0.66105 | 184.5117
7.1597 | 2018-11-20 19:50 | 0.62389 | 185.5187
7.1667 | 2018-11-20 20:00 | 0.62428 | 183.6737
7.1736 | 2018-11-20 20:10 | 0.62428 | 183.6737
7.1806 | 2018-11-20 20:20 | 0.52008 | 179.0084
7.1875 | 2018-11-20 20:30 | 0.50515 | 176.1407
7.1944 | 2018-11-20 20:40 | 0.37819 | 178.1817
7.2014 | 2018-11-20 20:50 | 0.44171 | 183.2446
7.2083 | 2018-11-20 21:00 | 0.36683 | 167.4034
7.2153 | 2018-11-20 21:10 | 0.36683 | 167.4034
7.2222 | 2018-11-20 21:20 | 0.31214 | 166.0973
7.2292 | 2018-11-20 21:30 | 0.25584 | 161.0693
7.2361 | 2018-11-20 21:40 | 0.2045 | 155.4401
7.2431 | 2018-11-20 21:50 | 0.19019 | 159.3734
7.25 | 2018-11-20 22:00 | 0.069857 | 76.7595
7.2569 | 2018-11-20 22:10 | 0.069857 | 76.7595
7.2639 | 2018-11-20 22:20 | 0.1408 | 42.9854
7.2708 | 2018-11-20 22:30 | 0.29498 | 30.564
7.2778 | 2018-11-20 22:40 | 0.36716 | 19.0765
7.2847 | 2018-11-20 22:50 | 0.40883 | 20.474
7.2917 | 2018-11-20 23:00 | 0.44543 | 10.4774
7.2986 | 2018-11-20 23:10 | 0.44543 | 10.4774
7.3056 | 2018-11-20 23:20 | 0.46951 | 11.5493
7.3125 | 2018-11-20 23:30 | 0.57166 | 8.7538
7.3194 | 2018-11-20 23:40 | 0.85636 | 7.5151
7.3264 | 2018-11-20 23:50 | 0.87136 | 8.8461
7.3333 | 2018-11-21 | 0.79535 | 19.0045
7.3403 | 2018-11-21 00:10 | 0.79535 | 19.0045
7.3472 | 2018-11-21 00:20 | 0.7225 | 5.6396
7.3542 | 2018-11-21 00:30 | 0.72411 | 3.1667
7.3611 | 2018-11-21 00:40 | 0.64168 | 8.8751
7.3681 | 2018-11-21 00:50 | 0.71673 | 13.474
7.375 | 2018-11-21 01:00 | 0.56056 | 12.1519
7.3819 | 2018-11-21 01:10 | 0.56056 | 12.1519
7.3889 | 2018-11-21 01:20 | 0.54034 | 4.0327
7.3958 | 2018-11-21 01:30 | 0.51117 | 358.5427
7.4028 | 2018-11-21 01:40 | 0.36731 | 2.3405
7.4097 | 2018-11-21 01:50 | 0.39899 | 13.479
7.4167 | 2018-11-21 02:00 | 0.4321 | 10.3997
7.4236 | 2018-11-21 02:10 | 0.4321 | 10.3997
7.4306 | 2018-11-21 02:20 | 0.31073 | 10.008
7.4375 | 2018-11-21 02:30 | 0.36566 | 3.4493
7.4444 | 2018-11-21 02:40 | 0.26489 | 351.5334
7.4514 | 2018-11-21 02:50 | 0.31031 | 15.5142
7.4583 | 2018-11-21 03:00 | 0.27561 | 347.4261
7.4653 | 2018-11-21 03:10 | 0.27561 | 347.4261
7.4722 | 2018-11-21 03:20 | 0.099358 | 319.8991
7.4792 | 2018-11-21 03:30 | 0.075313 | 169.2869
7.4861 | 2018-11-21 03:40 | 0.066573 | 237.2648
7.4931 | 2018-11-21 03:50 | 0.096208 | 200.6954
7.5 | 2018-11-21 04:00 | 0.19278 | 205.5017
7.5069 | 2018-11-21 04:10 | 0.19278 | 205.5017
7.5139 | 2018-11-21 04:20 | 0.34106 | 190.8157
7.5208 | 2018-11-21 04:30 | 0.42701 | 180.4025
7.5278 | 2018-11-21 04:40 | 0.4414 | 185.9818
7.5347 | 2018-11-21 04:50 | 0.36479 | 176.2277
7.5417 | 2018-11-21 05:00 | 0.47731 | 187.7057
7.5486 | 2018-11-21 05:10 | 0.47731 | 187.7057
7.5556 | 2018-11-21 05:20 | 0.48872 | 184.8123
7.5625 | 2018-11-21 05:30 | 0.58825 | 181.6561
7.5694 | 2018-11-21 05:40 | 0.59815 | 183.5465
7.5764 | 2018-11-21 05:50 | 0.6022 | 186.771
7.5833 | 2018-11-21 06:00 | 0.57419 | 183.6946
7.5903 | 2018-11-21 06:10 | 0.57419 | 183.6946
7.5972 | 2018-11-21 06:20 | 0.62735 | 181.9183
7.6042 | 2018-11-21 06:30 | 0.58212 | 187.6012
7.6111 | 2018-11-21 06:40 | 0.45007 | 181.0185
7.6181 | 2018-11-21 06:50 | 0.49704 | 180.6917
7.625 | 2018-11-21 07:00 | 0.52827 | 181.8441
7.6319 | 2018-11-21 07:10 | 0.52827 | 181.8441
7.6389 | 2018-11-21 07:20 | 0.43466 | 185.0154
7.6458 | 2018-11-21 07:30 | 0.50529 | 181.928
7.6528 | 2018-11-21 07:40 | 0.52545 | 184.2565
7.6597 | 2018-11-21 07:50 | 0.4012 | 173.991
7.6667 | 2018-11-21 08:00 | 0.37026 | 171.3009
7.6736 | 2018-11-21 08:10 | 0.37026 | 171.3009
7.6806 | 2018-11-21 08:20 | 0.40289 | 174.4451
7.6875 | 2018-11-21 08:30 | 0.36999 | 184.1849
7.6944 | 2018-11-21 08:40 | 0.288 | 184.7802
7.7014 | 2018-11-21 08:50 | 0.29889 | 175.5866
7.7083 | 2018-11-21 09:00 | 0.29026 | 174.6626
7.7153 | 2018-11-21 09:10 | 0.29026 | 174.6626
7.7222 | 2018-11-21 09:20 | 0.14494 | 140.5993
7.7292 | 2018-11-21 09:30 | 0.19313 | 121.8796
7.7361 | 2018-11-21 09:40 | 0.15763 | 54.2933
7.7431 | 2018-11-21 09:50 | 0.16261 | 39.7605
7.75 | 2018-11-21 10:00 | 0.3042 | 20.9969
7.7569 | 2018-11-21 10:10 | 0.3042 | 20.9969
7.7639 | 2018-11-21 10:20 | 0.4361 | 20.6791
7.7708 | 2018-11-21 10:30 | 0.46932 | 13.6809
7.7778 | 2018-11-21 10:40 | 0.44152 | 8.2035
7.7847 | 2018-11-21 10:50 | 0.49952 | 4.4779
7.7917 | 2018-11-21 11:00 | 0.68999 | 9.2575
7.7986 | 2018-11-21 11:10 | 0.68999 | 9.2575
7.8056 | 2018-11-21 11:20 | 0.82438 | 8.651
7.8125 | 2018-11-21 11:30 | 0.92365 | 5.0933
7.8194 | 2018-11-21 11:40 | 0.74128 | 9.5513
7.8264 | 2018-11-21 11:50 | 0.73978 | 8.3163
7.8333 | 2018-11-21 12:00 | 0.85113 | 6.8829
7.8403 | 2018-11-21 12:10 | 0.85113 | 6.8829
7.8472 | 2018-11-21 12:20 | 0.95078 | 8.2238
7.8542 | 2018-11-21 12:30 | 0.80019 | 6.53
7.8611 | 2018-11-21 12:40 | 0.76431 | 10.7072
7.8681 | 2018-11-21 12:50 | 0.72789 | 10.3682
7.875 | 2018-11-21 13:00 | 0.68457 | 2.3441
7.8819 | 2018-11-21 13:10 | 0.68457 | 2.3441
7.8889 | 2018-11-21 13:20 | 0.64817 | 11.1192
7.8958 | 2018-11-21 13:30 | 0.56086 | 3.1685
7.9028 | 2018-11-21 13:40 | 0.4766 | 2.8864
7.9097 | 2018-11-21 13:50 | 0.44482 | 356.5201
7.9167 | 2018-11-21 14:00 | 0.48807 | 0.93919
7.9236 | 2018-11-21 14:10 | 0.48807 | 0.93919
7.9306 | 2018-11-21 14:20 | 0.41474 | 5.257
7.9375 | 2018-11-21 14:30 | 0.37526 | 2.138
7.9444 | 2018-11-21 14:40 | 0.32078 | 16.8532
7.9514 | 2018-11-21 14:50 | 0.25778 | 4.4498
7.9583 | 2018-11-21 15:00 | 0.214 | 347.5873
7.9653 | 2018-11-21 15:10 | 0.214 | 347.5873
7.9722 | 2018-11-21 15:20 | 0.27509 | 358.5419
7.9792 | 2018-11-21 15:30 | 0.24367 | 355.7636
7.9861 | 2018-11-21 15:40 | 0.14086 | 317.5895
7.9931 | 2018-11-21 15:50 | 0.1006 | 322.6745
8 | 2018-11-21 16:00 | 0.084865 | 314.0452
8.0069 | 2018-11-21 16:10 | 0.084865 | 314.0452
8.0139 | 2018-11-21 16:20 | 0.22241 | 219.3438
8.0208 | 2018-11-21 16:30 | 0.2658 | 200.4804
8.0278 | 2018-11-21 16:40 | 0.35187 | 190.4796
8.0347 | 2018-11-21 16:50 | 0.49774 | 198.5078
8.0417 | 2018-11-21 17:00 | 0.54776 | 197.6411
8.0486 | 2018-11-21 17:10 | 0.54776 | 197.6411
8.0556 | 2018-11-21 17:20 | 0.57345 | 185.303
8.0625 | 2018-11-21 17:30 | 0.63103 | 197.1428
8.0694 | 2018-11-21 17:40 | 0.62112 | 181.107
8.0764 | 2018-11-21 17:50 | 0.61653 | 190.0887
8.0833 | 2018-11-21 18:00 | 0.5463 | 181.8882
8.0903 | 2018-11-21 18:10 | 0.5463 | 181.8882
8.0972 | 2018-11-21 18:20 | 0.51019 | 186.4146
8.1042 | 2018-11-21 18:30 | 0.54244 | 192.7809
8.1111 | 2018-11-21 18:40 | 0.59624 | 186.839
8.1181 | 2018-11-21 18:50 | 0.71748 | 188.819
8.125 | 2018-11-21 19:00 | 0.61672 | 184.2776
8.1319 | 2018-11-21 19:10 | 0.61672 | 184.2776
8.1389 | 2018-11-21 19:20 | 0.67728 | 192.9693
8.1458 | 2018-11-21 19:30 | 0.70939 | 187.696
8.1528 | 2018-11-21 19:40 | 0.61347 | 185.1437
8.1597 | 2018-11-21 19:50 | 0.66881 | 192.8726
8.1667 | 2018-11-21 20:00 | 0.65534 | 194.3119
8.1736 | 2018-11-21 20:10 | 0.65534 | 194.3119
8.1806 | 2018-11-21 20:20 | 0.54737 | 187.2419
8.1875 | 2018-11-21 20:30 | 0.459 | 180
8.1944 | 2018-11-21 20:40 | 0.48626 | 181.8856
8.2014 | 2018-11-21 20:50 | 0.30303 | 195.5039
8.2083 | 2018-11-21 21:00 | 0.33326 | 184.9921
8.2153 | 2018-11-21 21:10 | 0.33326 | 184.9921
8.2222 | 2018-11-21 21:20 | 0.26005 | 195.1585
8.2292 | 2018-11-21 21:30 | 0.20815 | 182.2026
8.2361 | 2018-11-21 21:40 | 0.15 | 179.618
8.2431 | 2018-11-21 21:50 | 0.19194 | 140.9206
8.25 | 2018-11-21 22:00 | 0.1259 | 43.7127
8.2569 | 2018-11-21 22:10 | 0.1259 | 43.7127
8.2639 | 2018-11-21 22:20 | 0.32026 | 25.5249
8.2708 | 2018-11-21 22:30 | 0.33954 | 20.5165
8.2778 | 2018-11-21 22:40 | 0.45711 | 23.8734
8.2847 | 2018-11-21 22:50 | 0.47117 | 12.5024
8.2917 | 2018-11-21 23:00 | 0.51377 | 9.9757
8.2986 | 2018-11-21 23:10 | 0.51377 | 9.9757
8.3056 | 2018-11-21 23:20 | 0.60449 | 17.0261
8.3125 | 2018-11-21 23:30 | 0.67091 | 11.2597
8.3194 | 2018-11-21 23:40 | 0.63576 | 8.9586
8.3264 | 2018-11-21 23:50 | 0.84839 | 14.0526
8.3333 | 2018-11-22 | 0.73138 | 15.1383
8.3403 | 2018-11-22 00:10 | 0.73138 | 15.1383
8.3472 | 2018-11-22 00:20 | 0.88709 | 4.7851
8.3542 | 2018-11-22 00:30 | 0.75367 | 8.6999
8.3611 | 2018-11-22 00:40 | 0.77991 | 9.5952
8.3681 | 2018-11-22 00:50 | 0.8545 | 10.9286
8.375 | 2018-11-22 01:00 | 0.81687 | 19.0782
8.3819 | 2018-11-22 01:10 | 0.81687 | 19.0782
8.3889 | 2018-11-22 01:20 | 0.82682 | 7.3657
8.3958 | 2018-11-22 01:30 | 0.71932 | 5.5045
8.4028 | 2018-11-22 01:40 | 0.56543 | 2.2299
8.4097 | 2018-11-22 01:50 | 0.45835 | 7.9003
8.4167 | 2018-11-22 02:00 | 0.58938 | 6.1362
8.4236 | 2018-11-22 02:10 | 0.58938 | 6.1362
8.4306 | 2018-11-22 02:20 | 0.33853 | 3.2174
8.4375 | 2018-11-22 02:30 | 0.56899 | 9.6113
8.4444 | 2018-11-22 02:40 | 0.42046 | 4.775
8.4514 | 2018-11-22 02:50 | 0.41332 | 4.5794
8.4583 | 2018-11-22 03:00 | 0.31772 | 11.8051
8.4653 | 2018-11-22 03:10 | 0.31772 | 11.8051
8.4722 | 2018-11-22 03:20 | 0.24459 | 3.9855
8.4792 | 2018-11-22 03:30 | 0.18232 | 350.8477
8.4861 | 2018-11-22 03:40 | 0.1593 | 321.1155
8.4931 | 2018-11-22 03:50 | 0.044688 | 310.4622
8.5 | 2018-11-22 04:00 | 0.10866 | 263.6598
8.5069 | 2018-11-22 04:10 | 0.10866 | 263.6598
8.5139 | 2018-11-22 04:20 | 0.21694 | 207.7462
8.5208 | 2018-11-22 04:30 | 0.16243 | 217.9987
8.5278 | 2018-11-22 04:40 | 0.36727 | 203.4239
8.5347 | 2018-11-22 04:50 | 0.42821 | 197.6733
8.5417 | 2018-11-22 05:00 | 0.49652 | 197.7051
8.5486 | 2018-11-22 05:10 | 0.49652 | 197.7051
8.5556 | 2018-11-22 05:20 | 0.59885 | 184.5014
8.5625 | 2018-11-22 05:30 | 0.67567 | 185.0946
8.5694 | 2018-11-22 05:40 | 0.60501 | 183.3164
8.5764 | 2018-11-22 05:50 | 0.66036 | 187.308
8.5833 | 2018-11-22 06:00 | 0.63061 | 184.0921
8.5903 | 2018-11-22 06:10 | 0.63061 | 184.0921
8.5972 | 2018-11-22 06:20 | 0.69006 | 180.7473
8.6042 | 2018-11-22 06:30 | 0.6535 | 189.7794
8.6111 | 2018-11-22 06:40 | 0.664 | 179.9137
8.6181 | 2018-11-22 06:50 | 0.62548 | 190.5015
8.625 | 2018-11-22 07:00 | 0.68039 | 187.8562
8.6319 | 2018-11-22 07:10 | 0.68039 | 187.8562
8.6389 | 2018-11-22 07:20 | 0.64983 | 188.3171
8.6458 | 2018-11-22 07:30 | 0.66994 | 187.6342
8.6528 | 2018-11-22 07:40 | 0.69334 | 185.6284
8.6597 | 2018-11-22 07:50 | 0.69296 | 188.1301
8.6667 | 2018-11-22 08:00 | 0.66419 | 189.0085
8.6736 | 2018-11-22 08:10 | 0.66419 | 189.0085
8.6806 | 2018-11-22 08:20 | 0.58839 | 189.6864
8.6875 | 2018-11-22 08:30 | 0.49809 | 176.2012
8.6944 | 2018-11-22 08:40 | 0.51994 | 190.64
8.7014 | 2018-11-22 08:50 | 0.39789 | 199.5279
8.7083 | 2018-11-22 09:00 | 0.44561 | 190.6039
8.7153 | 2018-11-22 09:10 | 0.44561 | 190.6039
8.7222 | 2018-11-22 09:20 | 0.39513 | 174.0441
8.7292 | 2018-11-22 09:30 | 0.29793 | 199.408
8.7361 | 2018-11-22 09:40 | 0.23022 | 182.4895
8.7431 | 2018-11-22 09:50 | 0.13485 | 144.6599
8.75 | 2018-11-22 10:00 | 0.074967 | 136.0809
8.7569 | 2018-11-22 10:10 | 0.074967 | 136.0809
8.7639 | 2018-11-22 10:20 | 0.1999 | 51.2954
8.7708 | 2018-11-22 10:30 | 0.36763 | 27.1924
8.7778 | 2018-11-22 10:40 | 0.35996 | 14.8084
8.7847 | 2018-11-22 10:50 | 0.52606 | 27.8803
8.7917 | 2018-11-22 11:00 | 0.52917 | 23.028
8.7986 | 2018-11-22 11:10 | 0.52917 | 23.028
8.8056 | 2018-11-22 11:20 | 0.62835 | 18.7521
8.8125 | 2018-11-22 11:30 | 0.5892 | 12.1491
8.8194 | 2018-11-22 11:40 | 0.52542 | 9.6416
8.8264 | 2018-11-22 11:50 | 0.75017 | 14.2771
8.8333 | 2018-11-22 12:00 | 0.83522 | 10.2067
8.8403 | 2018-11-22 12:10 | 0.83522 | 10.2067
8.8472 | 2018-11-22 12:20 | 0.91724 | 10.1093
8.8542 | 2018-11-22 12:30 | 0.90377 | 12.0062
8.8611 | 2018-11-22 12:40 | 0.9604 | 7.1176
8.8681 | 2018-11-22 12:50 | 0.96154 | 8.4925
8.875 | 2018-11-22 13:00 | 0.81198 | 10.6457
8.8819 | 2018-11-22 13:10 | 0.81198 | 10.6457
8.8889 | 2018-11-22 13:20 | 0.76758 | 17.5143
8.8958 | 2018-11-22 13:30 | 0.79768 | 6.8399
8.9028 | 2018-11-22 13:40 | 0.69381 | 8.0367
8.9097 | 2018-11-22 13:50 | 0.72759 | 11.4953
8.9167 | 2018-11-22 14:00 | 0.5836 | 5.4078
8.9236 | 2018-11-22 14:10 | 0.5836 | 5.4078
8.9306 | 2018-11-22 14:20 | 0.56823 | 1.6135
8.9375 | 2018-11-22 14:30 | 0.51749 | 7.5507
8.9444 | 2018-11-22 14:40 | 0.57833 | 15.2377
8.9514 | 2018-11-22 14:50 | 0.47347 | 2.5421
8.9583 | 2018-11-22 15:00 | 0.50148 | 6.7566
8.9653 | 2018-11-22 15:10 | 0.50148 | 6.7566
8.9722 | 2018-11-22 15:20 | 0.25158 | 3.8747
8.9792 | 2018-11-22 15:30 | 0.31616 | 355.1009
8.9861 | 2018-11-22 15:40 | 0.35843 | 5.1221
8.9931 | 2018-11-22 15:50 | 0.26128 | 15.3128
9 | 2018-11-22 16:00 | 0.13228 | 343.7571
9.0069 | 2018-11-22 16:10 | 0.13228 | 343.7571
9.0139 | 2018-11-22 16:20 | 0.1044 | 286.6992
9.0208 | 2018-11-22 16:30 | 0.067007 | 270.8551
9.0278 | 2018-11-22 16:40 | 0.20366 | 231.7796
9.0347 | 2018-11-22 16:50 | 0.24491 | 213.171
9.0417 | 2018-11-22 17:00 | 0.3702 | 196.4769
9.0486 | 2018-11-22 17:10 | 0.3702 | 196.4769
9.0556 | 2018-11-22 17:20 | 0.52378 | 189.2285
9.0625 | 2018-11-22 17:30 | 0.63774 | 186.2112
9.0694 | 2018-11-22 17:40 | 0.62382 | 188.4808
9.0764 | 2018-11-22 17:50 | 0.61266 | 185.3384
9.0833 | 2018-11-22 18:00 | 0.69778 | 187.9908
9.0903 | 2018-11-22 18:10 | 0.69778 | 187.9908
9.0972 | 2018-11-22 18:20 | 0.64537 | 186.6735
9.1042 | 2018-11-22 18:30 | 0.5681 | 197.0953
9.1111 | 2018-11-22 18:40 | 0.61911 | 183.4262
9.1181 | 2018-11-22 18:50 | 0.70923 | 189.7412
9.125 | 2018-11-22 19:00 | 0.75693 | 185.8386
9.1319 | 2018-11-22 19:10 | 0.75693 | 185.8386
9.1389 | 2018-11-22 19:20 | 0.66776 | 193.2454
9.1458 | 2018-11-22 19:30 | 0.70627 | 189.7824
9.1528 | 2018-11-22 19:40 | 0.83274 | 190.7972
9.1597 | 2018-11-22 19:50 | 0.72763 | 191.8968
9.1667 | 2018-11-22 20:00 | 0.76581 | 190.0773
9.1736 | 2018-11-22 20:10 | 0.76581 | 190.0773
9.1806 | 2018-11-22 20:20 | 0.64107 | 187.89
9.1875 | 2018-11-22 20:30 | 0.68391 | 188.1538
9.1944 | 2018-11-22 20:40 | 0.66055 | 190.7316
9.2014 | 2018-11-22 20:50 | 0.6092 | 196.2038
9.2083 | 2018-11-22 21:00 | 0.5917 | 190.9111
9.2153 | 2018-11-22 21:10 | 0.5917 | 190.9111
9.2222 | 2018-11-22 21:20 | 0.40978 | 192.544
9.2292 | 2018-11-22 21:30 | 0.45221 | 195.3885
9.2361 | 2018-11-22 21:40 | 0.40227 | 184.5626
9.2431 | 2018-11-22 21:50 | 0.40708 | 187.0552
9.25 | 2018-11-22 22:00 | 0.26596 | 167.8451
9.2569 | 2018-11-22 22:10 | 0.26596 | 167.8451
9.2639 | 2018-11-22 22:20 | 0.28601 | 180.4007
9.2708 | 2018-11-22 22:30 | 0.087641 | 196.574
9.2778 | 2018-11-22 22:40 | 0.050912 | 45
9.2847 | 2018-11-22 22:50 | 0.21095 | 31.4296
9.2917 | 2018-11-22 23:00 | 0.27549 | 17.3168
9.2986 | 2018-11-22 23:10 | 0.27549 | 17.3168
9.3056 | 2018-11-22 23:20 | 0.44876 | 16.1734
9.3125 | 2018-11-22 23:30 | 0.47848 | 23.1357
9.3194 | 2018-11-22 23:40 | 0.58475 | 21.7832
9.3264 | 2018-11-22 23:50 | 0.61492 | 10.3049
9.3333 | 2018-11-23 | 0.72527 | 15.7609
9.3403 | 2018-11-23 00:10 | 0.72527 | 15.7609
9.3472 | 2018-11-23 00:20 | 0.6983 | 12.4042
9.3542 | 2018-11-23 00:30 | 0.85572 | 12.0059
9.3611 | 2018-11-23 00:40 | 0.83898 | 10.0911
9.3681 | 2018-11-23 00:50 | 0.81179 | 13.6083
9.375 | 2018-11-23 01:00 | 0.84618 | 7.4694
9.3819 | 2018-11-23 01:10 | 0.84618 | 7.4694
9.3889 | 2018-11-23 01:20 | 0.84339 | 14.9095
9.3958 | 2018-11-23 01:30 | 0.79367 | 8.4772
9.4028 | 2018-11-23 01:40 | 0.88649 | 12.641
9.4097 | 2018-11-23 01:50 | 0.76841 | 6.8013
9.4167 | 2018-11-23 02:00 | 0.71038 | 11.9427
9.4236 | 2018-11-23 02:10 | 0.71038 | 11.9427
9.4306 | 2018-11-23 02:20 | 0.76808 | 9.7444
9.4375 | 2018-11-23 02:30 | 0.66513 | 6.3878
9.4444 | 2018-11-23 02:40 | 0.61804 | 12.2372
9.4514 | 2018-11-23 02:50 | 0.51316 | 1.4516
9.4583 | 2018-11-23 03:00 | 0.45245 | 8.9002
9.4653 | 2018-11-23 03:10 | 0.45245 | 8.9002
9.4722 | 2018-11-23 03:20 | 0.404 | 0
9.4792 | 2018-11-23 03:30 | 0.36949 | 11.5532
9.4861 | 2018-11-23 03:40 | 0.33104 | 359.1346
9.4931 | 2018-11-23 03:50 | 0.23602 | 0.7283
9.5 | 2018-11-23 04:00 | 0.2191 | 347.613
9.5069 | 2018-11-23 04:10 | 0.2191 | 347.613
9.5139 | 2018-11-23 04:20 | 0.12304 | 7.4716
9.5208 | 2018-11-23 04:30 | 0.16219 | 311.7509
9.5278 | 2018-11-23 04:40 | 0.1096 | 238.05
9.5347 | 2018-11-23 04:50 | 0.1212 | 205.9308
9.5417 | 2018-11-23 05:00 | 0.28412 | 219.5732
9.5486 | 2018-11-23 05:10 | 0.28412 | 219.5732
9.5556 | 2018-11-23 05:20 | 0.39189 | 205.0611
9.5625 | 2018-11-23 05:30 | 0.33039 | 192.9426
9.5694 | 2018-11-23 05:40 | 0.52968 | 196.4506
9.5764 | 2018-11-23 05:50 | 0.58733 | 188.4198
9.5833 | 2018-11-23 06:00 | 0.6614 | 194.2674
9.5903 | 2018-11-23 06:10 | 0.6614 | 194.2674
9.5972 | 2018-11-23 06:20 | 0.67304 | 187.6846
9.6042 | 2018-11-23 06:30 | 0.65681 | 191.7719
9.6111 | 2018-11-23 06:40 | 0.61716 | 188.1039
9.6181 | 2018-11-23 06:50 | 0.62954 | 182.367
9.625 | 2018-11-23 07:00 | 0.69264 | 186.6325
9.6319 | 2018-11-23 07:10 | 0.69264 | 186.6325
9.6389 | 2018-11-23 07:20 | 0.75972 | 194.9509
9.6458 | 2018-11-23 07:30 | 0.69189 | 182.8996
9.6528 | 2018-11-23 07:40 | 0.68699 | 185.3454
9.6597 | 2018-11-23 07:50 | 0.68061 | 185.9033
9.6667 | 2018-11-23 08:00 | 0.73687 | 185.0607
9.6736 | 2018-11-23 08:10 | 0.73687 | 185.0607
9.6806 | 2018-11-23 08:20 | 0.66315 | 181.2097
9.6875 | 2018-11-23 08:30 | 0.64486 | 187.0368
9.6944 | 2018-11-23 08:40 | 0.61679 | 191.2188
9.7014 | 2018-11-23 08:50 | 0.59718 | 191.103
9.7083 | 2018-11-23 09:00 | 0.56854 | 195.8208
9.7153 | 2018-11-23 09:10 | 0.56854 | 195.8208
9.7222 | 2018-11-23 09:20 | 0.55806 | 188.4495
9.7292 | 2018-11-23 09:30 | 0.50202 | 180.4565
9.7361 | 2018-11-23 09:40 | 0.41724 | 181.9229
9.7431 | 2018-11-23 09:50 | 0.43711 | 181.3109
9.75 | 2018-11-23 10:00 | 0.31327 | 177.6217
9.7569 | 2018-11-23 10:10 | 0.31327 | 177.6217
9.7639 | 2018-11-23 10:20 | 0.26123 | 177.5867
9.7708 | 2018-11-23 10:30 | 0.22518 | 177.7094
9.7778 | 2018-11-23 10:40 | 0.13872 | 158.4287
9.7847 | 2018-11-23 10:50 | 0.050567 | 24.5377
9.7917 | 2018-11-23 11:00 | 0.13427 | 34.992
9.7986 | 2018-11-23 11:10 | 0.13427 | 34.992
9.8056 | 2018-11-23 11:20 | 0.41527 | 34.7999
9.8125 | 2018-11-23 11:30 | 0.46107 | 13.6746
9.8194 | 2018-11-23 11:40 | 0.56323 | 17.8881
9.8264 | 2018-11-23 11:50 | 0.49851 | 12.8654
9.8333 | 2018-11-23 12:00 | 0.64711 | 13.5853
9.8403 | 2018-11-23 12:10 | 0.64711 | 13.5853
9.8472 | 2018-11-23 12:20 | 0.71269 | 11.2469
9.8542 | 2018-11-23 12:30 | 0.79001 | 8.6635
9.8611 | 2018-11-23 12:40 | 0.79646 | 12.6927
9.8681 | 2018-11-23 12:50 | 0.87154 | 11.181
9.875 | 2018-11-23 13:00 | 0.89024 | 15.7067
9.8819 | 2018-11-23 13:10 | 0.89024 | 15.7067
9.8889 | 2018-11-23 13:20 | 0.87351 | 11.49
9.8958 | 2018-11-23 13:30 | 0.91976 | 17.3317
9.9028 | 2018-11-23 13:40 | 0.89264 | 10.391
9.9097 | 2018-11-23 13:50 | 0.79327 | 4.3378
9.9167 | 2018-11-23 14:00 | 0.7277 | 12.2982
9.9236 | 2018-11-23 14:10 | 0.7277 | 12.2982
9.9306 | 2018-11-23 14:20 | 0.69474 | 12.9761
9.9375 | 2018-11-23 14:30 | 0.71552 | 4.8102
9.9444 | 2018-11-23 14:40 | 0.69753 | 13.9366
9.9514 | 2018-11-23 14:50 | 0.64738 | 11.2232
9.9583 | 2018-11-23 15:00 | 0.59306 | 11.5752
9.9653 | 2018-11-23 15:10 | 0.59306 | 11.5752
9.9722 | 2018-11-23 15:20 | 0.52966 | 5.7429
9.9792 | 2018-11-23 15:30 | 0.5553 | 7.1378
9.9861 | 2018-11-23 15:40 | 0.47642 | 2.406
9.9931 | 2018-11-23 15:50 | 0.40443 | 4.8225
10 | 2018-11-23 16:00 | 0.42647 | 2.688
10.0069 | 2018-11-23 16:10 | 0.42647 | 2.688
10.0139 | 2018-11-23 16:20 | 0.30487 | 355.6734
10.0208 | 2018-11-23 16:30 | 0.28411 | 358.3865
10.0278 | 2018-11-23 16:40 | 0.18797 | 20.556
10.0347 | 2018-11-23 16:50 | 0.14757 | 354.9462
10.0417 | 2018-11-23 17:00 | 0.086023 | 287.5924
10.0486 | 2018-11-23 17:10 | 0.086023 | 287.5924
10.0556 | 2018-11-23 17:20 | 0.095 | 233.1301
10.0625 | 2018-11-23 17:30 | 0.20163 | 223.1913
10.0694 | 2018-11-23 17:40 | 0.37152 | 204.1504
10.0764 | 2018-11-23 17:50 | 0.39205 | 195.3833
10.0833 | 2018-11-23 18:00 | 0.43031 | 190.5788
10.0903 | 2018-11-23 18:10 | 0.43031 | 190.5788
10.0972 | 2018-11-23 18:20 | 0.61166 | 187.7989
10.1042 | 2018-11-23 18:30 | 0.59536 | 185.1073
10.1111 | 2018-11-23 18:40 | 0.58461 | 189.2529
10.1181 | 2018-11-23 18:50 | 0.66052 | 191.1738
10.125 | 2018-11-23 19:00 | 0.68504 | 191.6216
10.1319 | 2018-11-23 19:10 | 0.68504 | 191.6216
10.1389 | 2018-11-23 19:20 | 0.671 | 190.3889
10.1458 | 2018-11-23 19:30 | 0.6997 | 186.6476
10.1528 | 2018-11-23 19:40 | 0.76 | 188.322
10.1597 | 2018-11-23 19:50 | 0.74769 | 189.7017
10.1667 | 2018-11-23 20:00 | 0.75759 | 183.7084
10.1736 | 2018-11-23 20:10 | 0.75759 | 183.7084
10.1806 | 2018-11-23 20:20 | 0.76003 | 192.8477
10.1875 | 2018-11-23 20:30 | 0.82446 | 189.5651
10.1944 | 2018-11-23 20:40 | 0.67871 | 188.6435
10.2014 | 2018-11-23 20:50 | 0.79551 | 190.5754
10.2083 | 2018-11-23 21:00 | 0.71306 | 195.537
10.2153 | 2018-11-23 21:10 | 0.71306 | 195.537
10.2222 | 2018-11-23 21:20 | 0.58181 | 188.1022
10.2292 | 2018-11-23 21:30 | 0.61266 | 185.3384
10.2361 | 2018-11-23 21:40 | 0.61212 | 183.4654
10.2431 | 2018-11-23 21:50 | 0.66996 | 188.8437
10.25 | 2018-11-23 22:00 | 0.59788 | 186.5307
10.2569 | 2018-11-23 22:10 | 0.59788 | 186.5307
10.2639 | 2018-11-23 22:20 | 0.51348 | 184.3559
10.2708 | 2018-11-23 22:30 | 0.31094 | 194.5278
10.2778 | 2018-11-23 22:40 | 0.35441 | 177.2506
10.2847 | 2018-11-23 22:50 | 0.29896 | 184.6045
10.2917 | 2018-11-23 23:00 | 0.19938 | 193.3392
10.2986 | 2018-11-23 23:10 | 0.19938 | 193.3392
10.3056 | 2018-11-23 23:20 | 0.042048 | 115.3462
10.3125 | 2018-11-23 23:30 | 0.17265 | 27.604
10.3194 | 2018-11-23 23:40 | 0.24432 | 41.8478
10.3264 | 2018-11-23 23:50 | 0.32832 | 21.2505
10.3333 | 2018-11-24 | 0.41869 | 18.0888
10.3403 | 2018-11-24 00:10 | 0.41869 | 18.0888
10.3472 | 2018-11-24 00:20 | 0.62251 | 17.096
10.3542 | 2018-11-24 00:30 | 0.61992 | 16.3009
10.3611 | 2018-11-24 00:40 | 0.67661 | 12.7217
10.3681 | 2018-11-24 00:50 | 0.77387 | 19.1608
10.375 | 2018-11-24 01:00 | 0.76371 | 8.6606
10.3819 | 2018-11-24 01:10 | 0.76371 | 8.6606
10.3889 | 2018-11-24 01:20 | 0.77266 | 4.7513
10.3958 | 2018-11-24 01:30 | 0.93573 | 12.655
10.4028 | 2018-11-24 01:40 | 0.83544 | 16.2657
10.4097 | 2018-11-24 01:50 | 0.8437 | 18.3061
10.4167 | 2018-11-24 02:00 | 0.83215 | 12.6334
10.4236 | 2018-11-24 02:10 | 0.83215 | 12.6334
10.4306 | 2018-11-24 02:20 | 0.85981 | 12.63
10.4375 | 2018-11-24 02:30 | 0.75082 | 7.7308
10.4444 | 2018-11-24 02:40 | 0.68263 | 10.1247
10.4514 | 2018-11-24 02:50 | 0.63096 | 12.0757
10.4583 | 2018-11-24 03:00 | 0.67501 | 8.2621
10.4653 | 2018-11-24 03:10 | 0.67501 | 8.2621
10.4722 | 2018-11-24 03:20 | 0.63092 | 19.1529
10.4792 | 2018-11-24 03:30 | 0.53954 | 10.7893
10.4861 | 2018-11-24 03:40 | 0.47376 | 8.1301
10.4931 | 2018-11-24 03:50 | 0.46391 | 18.474
10.5 | 2018-11-24 04:00 | 0.39577 | 16.7408
10.5069 | 2018-11-24 04:10 | 0.39577 | 16.7408
10.5139 | 2018-11-24 04:20 | 0.34059 | 356.6335
10.5208 | 2018-11-24 04:30 | 0.2634 | 346.3858
10.5278 | 2018-11-24 04:40 | 0.29203 | 359.2152
10.5347 | 2018-11-24 04:50 | 0.22905 | 339.8246
10.5417 | 2018-11-24 05:00 | 0.12479 | 353.5584
10.5486 | 2018-11-24 05:10 | 0.12479 | 353.5584
10.5556 | 2018-11-24 05:20 | 0.073355 | 242.387
10.5625 | 2018-11-24 05:30 | 0.12161 | 233.6955
10.5694 | 2018-11-24 05:40 | 0.18322 | 216.1193
10.5764 | 2018-11-24 05:50 | 0.39189 | 195.845
10.5833 | 2018-11-24 06:00 | 0.44055 | 195.2665
10.5903 | 2018-11-24 06:10 | 0.44055 | 195.2665
10.5972 | 2018-11-24 06:20 | 0.5608 | 193.1937
10.6042 | 2018-11-24 06:30 | 0.58176 | 186.5142
10.6111 | 2018-11-24 06:40 | 0.57064 | 182.712
10.6181 | 2018-11-24 06:50 | 0.66547 | 191.9685
10.625 | 2018-11-24 07:00 | 0.68112 | 181.0936
10.6319 | 2018-11-24 07:10 | 0.68112 | 181.0936
10.6389 | 2018-11-24 07:20 | 0.69445 | 189.9506
10.6458 | 2018-11-24 07:30 | 0.70703 | 191.8344
10.6528 | 2018-11-24 07:40 | 0.8201 | 180.9083
10.6597 | 2018-11-24 07:50 | 0.76134 | 186.789
10.6667 | 2018-11-24 08:00 | 0.74055 | 190.9761
10.6736 | 2018-11-24 08:10 | 0.74055 | 190.9761
10.6806 | 2018-11-24 08:20 | 0.8092 | 193.1432
10.6875 | 2018-11-24 08:30 | 0.73658 | 194.2249
10.6944 | 2018-11-24 08:40 | 0.82433 | 185.1504
10.7014 | 2018-11-24 08:50 | 0.70667 | 192.0891
10.7083 | 2018-11-24 09:00 | 0.72322 | 183.3292
10.7153 | 2018-11-24 09:10 | 0.72322 | 183.3292
10.7222 | 2018-11-24 09:20 | 0.67351 | 183.8311
10.7292 | 2018-11-24 09:30 | 0.68979 | 182.7421
10.7361 | 2018-11-24 09:40 | 0.64601 | 180.3548
10.7431 | 2018-11-24 09:50 | 0.61675 | 187.8279
10.75 | 2018-11-24 10:00 | 0.61817 | 183.5243
10.7569 | 2018-11-24 10:10 | 0.61817 | 183.5243
10.7639 | 2018-11-24 10:20 | 0.48817 | 181.526
10.7708 | 2018-11-24 10:30 | 0.51254 | 174.2894
10.7778 | 2018-11-24 10:40 | 0.4452 | 187.8753
10.7847 | 2018-11-24 10:50 | 0.40011 | 174.1184
10.7917 | 2018-11-24 11:00 | 0.38603 | 192.4161
10.7986 | 2018-11-24 11:10 | 0.38603 | 192.4161
10.8056 | 2018-11-24 11:20 | 0.20335 | 176.617
10.8125 | 2018-11-24 11:30 | 0.14629 | 164.5388
10.8194 | 2018-11-24 11:40 | 0.039395 | 113.9625
10.8264 | 2018-11-24 11:50 | 0.18418 | 12.2251
10.8333 | 2018-11-24 12:00 | 0.23726 | 35.5658
10.8403 | 2018-11-24 12:10 | 0.23726 | 35.5658
10.8472 | 2018-11-24 12:20 | 0.44989 | 16.6626
10.8542 | 2018-11-24 12:30 | 0.50305 | 20.2361
10.8611 | 2018-11-24 12:40 | 0.44658 | 17.4612
10.8681 | 2018-11-24 12:50 | 0.5838 | 16.4172
10.875 | 2018-11-24 13:00 | 0.56141 | 19.5646
10.8819 | 2018-11-24 13:10 | 0.56141 | 19.5646
10.8889 | 2018-11-24 13:20 | 0.77177 | 11.9651
10.8958 | 2018-11-24 13:30 | 0.88317 | 10.6356
10.9028 | 2018-11-24 13:40 | 0.79898 | 4.9542
10.9097 | 2018-11-24 13:50 | 0.81409 | 11.0477
10.9167 | 2018-11-24 14:00 | 0.90511 | 6.6618
10.9236 | 2018-11-24 14:10 | 0.90511 | 6.6618
10.9306 | 2018-11-24 14:20 | 0.75326 | 5.3322
10.9375 | 2018-11-24 14:30 | 0.73292 | 4.1469
10.9444 | 2018-11-24 14:40 | 0.74023 | 10.4295
10.9514 | 2018-11-24 14:50 | 0.81006 | 5.7387
10.9583 | 2018-11-24 15:00 | 0.75793 | 8.8036
10.9653 | 2018-11-24 15:10 | 0.75793 | 8.8036
10.9722 | 2018-11-24 15:20 | 0.64674 | 7.6415
10.9792 | 2018-11-24 15:30 | 0.66752 | 4.9846
10.9861 | 2018-11-24 15:40 | 0.63745 | 3.8679
10.9931 | 2018-11-24 15:50 | 0.52055 | 2.6425
11 | 2018-11-24 16:00 | 0.55292 | 4.7722
11.0069 | 2018-11-24 16:10 | 0.55292 | 4.7722
11.0139 | 2018-11-24 16:20 | 0.43436 | 9.0069
11.0208 | 2018-11-24 16:30 | 0.44211 | 12.2758
11.0278 | 2018-11-24 16:40 | 0.3339 | 9.8291
11.0347 | 2018-11-24 16:50 | 0.33981 | 9.6564
11.0417 | 2018-11-24 17:00 | 0.29614 | 1.7416
11.0486 | 2018-11-24 17:10 | 0.29614 | 1.7416
11.0556 | 2018-11-24 17:20 | 0.22091 | 352.4568
11.0625 | 2018-11-24 17:30 | 0.12929 | 347.0386
11.0694 | 2018-11-24 17:40 | 0.15108 | 271.8965
11.0764 | 2018-11-24 17:50 | 0.10224 | 183.9259
11.0833 | 2018-11-24 18:00 | 0.23759 | 241.6012
11.0903 | 2018-11-24 18:10 | 0.23759 | 241.6012
11.0972 | 2018-11-24 18:20 | 0.36994 | 190.2771
11.1042 | 2018-11-24 18:30 | 0.45562 | 190.4961
11.1111 | 2018-11-24 18:40 | 0.58749 | 193.1847
11.1181 | 2018-11-24 18:50 | 0.57898 | 195.8367
11.125 | 2018-11-24 19:00 | 0.7065 | 187.1552
11.1319 | 2018-11-24 19:10 | 0.7065 | 187.1552
11.1389 | 2018-11-24 19:20 | 0.54051 | 185.5207
11.1458 | 2018-11-24 19:30 | 0.56151 | 182.4497
11.1528 | 2018-11-24 19:40 | 0.5991 | 189.9969
11.1597 | 2018-11-24 19:50 | 0.74884 | 189.2988
11.1667 | 2018-11-24 20:00 | 0.84091 | 189.6527
11.1736 | 2018-11-24 20:10 | 0.84091 | 189.6527
11.1806 | 2018-11-24 20:20 | 0.7503 | 187.4281
11.1875 | 2018-11-24 20:30 | 0.76722 | 187.8661
11.1944 | 2018-11-24 20:40 | 0.83052 | 192.4465
11.2014 | 2018-11-24 20:50 | 0.69794 | 188.6525
11.2083 | 2018-11-24 21:00 | 0.81351 | 188.7676
11.2153 | 2018-11-24 21:10 | 0.81351 | 188.7676
11.2222 | 2018-11-24 21:20 | 0.77794 | 189.6197
11.2292 | 2018-11-24 21:30 | 0.69349 | 182.1486
11.2361 | 2018-11-24 21:40 | 0.78404 | 188.2128
11.2431 | 2018-11-24 21:50 | 0.76054 | 189.9949
11.25 | 2018-11-24 22:00 | 0.62592 | 183.1138
11.2569 | 2018-11-24 22:10 | 0.62592 | 183.1138
11.2639 | 2018-11-24 22:20 | 0.59103 | 184.7556
11.2708 | 2018-11-24 22:30 | 0.65384 | 184.2979
11.2778 | 2018-11-24 22:40 | 0.5853 | 183.8206
11.2847 | 2018-11-24 22:50 | 0.4758 | 187.2445
11.2917 | 2018-11-24 23:00 | 0.52241 | 188.2542
11.2986 | 2018-11-24 23:10 | 0.52241 | 188.2542
11.3056 | 2018-11-24 23:20 | 0.31509 | 171.9728
11.3125 | 2018-11-24 23:30 | 0.2408 | 163.597
11.3194 | 2018-11-24 23:40 | 0.18986 | 174.5597
11.3264 | 2018-11-24 23:50 | 0.17936 | 170.6952
11.3333 | 2018-11-25 | 0.011662 | 120.9638
11.3403 | 2018-11-25 00:10 | 0.011662 | 120.9638
11.3472 | 2018-11-25 00:20 | 0.32003 | 6.4588
11.3542 | 2018-11-25 00:30 | 0.3083 | 11.6015
11.3611 | 2018-11-25 00:40 | 0.53269 | 12.0272
11.3681 | 2018-11-25 00:50 | 0.56269 | 10.6509
11.375 | 2018-11-25 01:00 | 0.55979 | 13.639
11.3819 | 2018-11-25 01:10 | 0.55979 | 13.639
11.3889 | 2018-11-25 01:20 | 0.62517 | 16.6378
11.3958 | 2018-11-25 01:30 | 0.68049 | 6.5819
11.4028 | 2018-11-25 01:40 | 0.77073 | 15.9658
11.4097 | 2018-11-25 01:50 | 0.72182 | 13.4587
11.4167 | 2018-11-25 02:00 | 0.76835 | 14.1628
11.4236 | 2018-11-25 02:10 | 0.76835 | 14.1628
11.4306 | 2018-11-25 02:20 | 0.94979 | 11.4164
11.4375 | 2018-11-25 02:30 | 0.77681 | 15.378
11.4444 | 2018-11-25 02:40 | 0.86334 | 10.8153
11.4514 | 2018-11-25 02:50 | 0.68056 | 14.1179
11.4583 | 2018-11-25 03:00 | 0.79053 | 13.087
11.4653 | 2018-11-25 03:10 | 0.79053 | 13.087
11.4722 | 2018-11-25 03:20 | 0.72306 | 10.0355
11.4792 | 2018-11-25 03:30 | 0.76015 | 8.3966
11.4861 | 2018-11-25 03:40 | 0.62671 | 8.9964
11.4931 | 2018-11-25 03:50 | 0.73306 | 9.5009
11.5 | 2018-11-25 04:00 | 0.65765 | 8.7462
11.5069 | 2018-11-25 04:10 | 0.65765 | 8.7462
11.5139 | 2018-11-25 04:20 | 0.4753 | 2.0497
11.5208 | 2018-11-25 04:30 | 0.4111 | 1.2545
11.5278 | 2018-11-25 04:40 | 0.46766 | 14.8683
11.5347 | 2018-11-25 04:50 | 0.32812 | 358.4283
11.5417 | 2018-11-25 05:00 | 0.32001 | 0.53713
11.5486 | 2018-11-25 05:10 | 0.32001 | 0.53713
11.5556 | 2018-11-25 05:20 | 0.24913 | 358.1598
11.5625 | 2018-11-25 05:30 | 0.17 | 359.663
11.5694 | 2018-11-25 05:40 | 0.1586 | 338.9366
11.5764 | 2018-11-25 05:50 | 0.082225 | 346.6398
11.5833 | 2018-11-25 06:00 | 0.12385 | 321.5569
11.5903 | 2018-11-25 06:10 | 0.12385 | 321.5569
11.5972 | 2018-11-25 06:20 | 0.13473 | 185.9645
11.6042 | 2018-11-25 06:30 | 0.39242 | 193.8592
11.6111 | 2018-11-25 06:40 | 0.41868 | 196.2274
11.6181 | 2018-11-25 06:50 | 0.48974 | 196.7329
11.625 | 2018-11-25 07:00 | 0.48892 | 199.102
11.6319 | 2018-11-25 07:10 | 0.48892 | 199.102
11.6389 | 2018-11-25 07:20 | 0.64393 | 186.3304
11.6458 | 2018-11-25 07:30 | 0.53131 | 190.7389
11.6528 | 2018-11-25 07:40 | 0.606 | 192.7749
11.6597 | 2018-11-25 07:50 | 0.58665 | 184.3013
11.6667 | 2018-11-25 08:00 | 0.67371 | 184.0856
11.6736 | 2018-11-25 08:10 | 0.67371 | 184.0856
11.6806 | 2018-11-25 08:20 | 0.67328 | 194.0982
11.6875 | 2018-11-25 08:30 | 0.74085 | 190.2633
11.6944 | 2018-11-25 08:40 | 0.8439 | 185.5079
11.7014 | 2018-11-25 08:50 | 0.83403 | 184.8835
11.7083 | 2018-11-25 09:00 | 0.76562 | 189.0932
11.7153 | 2018-11-25 09:10 | 0.76562 | 189.0932
11.7222 | 2018-11-25 09:20 | 0.78843 | 188.387
11.7292 | 2018-11-25 09:30 | 0.79427 | 188.7626
11.7361 | 2018-11-25 09:40 | 0.70407 | 184.3987
11.7431 | 2018-11-25 09:50 | 0.70563 | 188.9684
11.75 | 2018-11-25 10:00 | 0.6323 | 190.8479
11.7569 | 2018-11-25 10:10 | 0.6323 | 190.8479
11.7639 | 2018-11-25 10:20 | 0.68311 | 181.0066
11.7708 | 2018-11-25 10:30 | 0.62908 | 180.9108
11.7778 | 2018-11-25 10:40 | 0.45366 | 190.5421
11.7847 | 2018-11-25 10:50 | 0.44589 | 185.2759
11.7917 | 2018-11-25 11:00 | 0.49445 | 182.4342
11.7986 | 2018-11-25 11:10 | 0.49445 | 182.4342
11.8056 | 2018-11-25 11:20 | 0.42302 | 180.5418
11.8125 | 2018-11-25 11:30 | 0.43219 | 187.9801
11.8194 | 2018-11-25 11:40 | 0.36383 | 193.3487
11.8264 | 2018-11-25 11:50 | 0.28418 | 177.9834
11.8333 | 2018-11-25 12:00 | 0.10671 | 169.7432
11.8403 | 2018-11-25 12:10 | 0.10671 | 169.7432
11.8472 | 2018-11-25 12:20 | 0.11131 | 81.2147
11.8542 | 2018-11-25 12:30 | 0.28206 | 29.2914
11.8611 | 2018-11-25 12:40 | 0.33204 | 11.8176
11.8681 | 2018-11-25 12:50 | 0.37117 | 15.3093
11.875 | 2018-11-25 13:00 | 0.4702 | 12.5288
11.8819 | 2018-11-25 13:10 | 0.4702 | 12.5288
11.8889 | 2018-11-25 13:20 | 0.58065 | 14.5628
11.8958 | 2018-11-25 13:30 | 0.63601 | 11.6103
11.9028 | 2018-11-25 13:40 | 0.72912 | 15.6755
11.9097 | 2018-11-25 13:50 | 0.69453 | 7.8618
11.9167 | 2018-11-25 14:00 | 0.78584 | 11.1526
11.9236 | 2018-11-25 14:10 | 0.78584 | 11.1526
11.9306 | 2018-11-25 14:20 | 0.774 | 9.2189
11.9375 | 2018-11-25 14:30 | 0.91705 | 11.0649
11.9444 | 2018-11-25 14:40 | 0.85553 | 10.5744
11.9514 | 2018-11-25 14:50 | 0.8149 | 12.689
11.9583 | 2018-11-25 15:00 | 0.72918 | 6.1406
11.9653 | 2018-11-25 15:10 | 0.72918 | 6.1406
11.9722 | 2018-11-25 15:20 | 0.77612 | 6.5848
11.9792 | 2018-11-25 15:30 | 0.83312 | 13.8194
11.9861 | 2018-11-25 15:40 | 0.58943 | 10.2614
11.9931 | 2018-11-25 15:50 | 0.65752 | 12.4721
12 | 2018-11-25 16:00 | 0.6173 | 3.7153
12.0069 | 2018-11-25 16:10 | 0.6173 | 3.7153
12.0139 | 2018-11-25 16:20 | 0.50794 | 11.3542
12.0208 | 2018-11-25 16:30 | 0.47872 | 11.5681
12.0278 | 2018-11-25 16:40 | 0.63756 | 12.6848
12.0347 | 2018-11-25 16:50 | 0.54108 | 16.4254
12.0417 | 2018-11-25 17:00 | 0.43106 | 13.0046
12.0486 | 2018-11-25 17:10 | 0.43106 | 13.0046
12.0556 | 2018-11-25 17:20 | 0.38803 | 0.73831
12.0625 | 2018-11-25 17:30 | 0.25717 | 12.5771
12.0694 | 2018-11-25 17:40 | 0.164 | 0
12.0764 | 2018-11-25 17:50 | 0.25316 | 352.51
12.0833 | 2018-11-25 18:00 | 0.151 | 337.0007
12.0903 | 2018-11-25 18:10 | 0.151 | 337.0007
12.0972 | 2018-11-25 18:20 | 0.087132 | 279.2461
12.1042 | 2018-11-25 18:30 | 0.14509 | 214.895
12.1111 | 2018-11-25 18:40 | 0.17129 | 205.9667
12.1181 | 2018-11-25 18:50 | 0.40536 | 208.272
12.125 | 2018-11-25 19:00 | 0.43028 | 205.6122
12.1319 | 2018-11-25 19:10 | 0.43028 | 205.6122
12.1389 | 2018-11-25 19:20 | 0.54886 | 186.8013
12.1458 | 2018-11-25 19:30 | 0.6079 | 183.1119
12.1528 | 2018-11-25 19:40 | 0.59613 | 187.5184
12.1597 | 2018-11-25 19:50 | 0.60874 | 182.8248
12.1667 | 2018-11-25 20:00 | 0.59335 | 183.8655
12.1736 | 2018-11-25 20:10 | 0.59335 | 183.8655
12.1806 | 2018-11-25 20:20 | 0.77808 | 183.0205
12.1875 | 2018-11-25 20:30 | 0.81036 | 187.7301
12.1944 | 2018-11-25 20:40 | 0.76037 | 193.6159
12.2014 | 2018-11-25 20:50 | 0.75 | 189.8265
12.2083 | 2018-11-25 21:00 | 0.81914 | 188.5654
12.2153 | 2018-11-25 21:10 | 0.81914 | 188.5654
12.2222 | 2018-11-25 21:20 | 0.77932 | 192.4491
12.2292 | 2018-11-25 21:30 | 0.69757 | 188.9897
12.2361 | 2018-11-25 21:40 | 0.79875 | 194.8714
12.2431 | 2018-11-25 21:50 | 0.68111 | 185.4762
12.25 | 2018-11-25 22:00 | 0.77845 | 189.8374
12.2569 | 2018-11-25 22:10 | 0.77845 | 189.8374
12.2639 | 2018-11-25 22:20 | 0.74781 | 193.2186
12.2708 | 2018-11-25 22:30 | 0.72318 | 178.7323
12.2778 | 2018-11-25 22:40 | 0.75002 | 180.382
12.2847 | 2018-11-25 22:50 | 0.63803 | 180.5388
12.2917 | 2018-11-25 23:00 | 0.61953 | 186.1155
12.2986 | 2018-11-25 23:10 | 0.61953 | 186.1155
12.3056 | 2018-11-25 23:20 | 0.52893 | 188.5897
12.3125 | 2018-11-25 23:30 | 0.63267 | 191.4875
12.3194 | 2018-11-25 23:40 | 0.51371 | 176.9872
12.3264 | 2018-11-25 23:50 | 0.47704 | 179.2793
12.3333 | 2018-11-26 | 0.35315 | 188.7955
12.3403 | 2018-11-26 00:10 | 0.35315 | 188.7955
12.3472 | 2018-11-26 00:20 | 0.27313 | 193.1204
12.3542 | 2018-11-26 00:30 | 0.2814 | 176.9444
12.3611 | 2018-11-26 00:40 | 0.06364 | 188.1301
12.3681 | 2018-11-26 00:50 | 0.052773 | 152.9494
12.375 | 2018-11-26 01:00 | 0.11512 | 7.9893
12.3819 | 2018-11-26 01:10 | 0.11512 | 7.9893
12.3889 | 2018-11-26 01:20 | 0.38658 | 10.5832
12.3958 | 2018-11-26 01:30 | 0.4767 | 22.3148
12.4028 | 2018-11-26 01:40 | 0.56602 | 20.2599
12.4097 | 2018-11-26 01:50 | 0.54038 | 15.7852
12.4167 | 2018-11-26 02:00 | 0.52362 | 9.1205
12.4236 | 2018-11-26 02:10 | 0.52362 | 9.1205
12.4306 | 2018-11-26 02:20 | 0.74195 | 10.7193
12.4375 | 2018-11-26 02:30 | 0.69313 | 7.6274
12.4444 | 2018-11-26 02:40 | 0.73132 | 8.6509
12.4514 | 2018-11-26 02:50 | 0.84234 | 10.9497
12.4583 | 2018-11-26 03:00 | 0.81502 | 16.6117
12.4653 | 2018-11-26 03:10 | 0.81502 | 16.6117
12.4722 | 2018-11-26 03:20 | 0.83575 | 15.3333
12.4792 | 2018-11-26 03:30 | 0.78112 | 8.7629
12.4861 | 2018-11-26 03:40 | 0.71262 | 6.5266
12.4931 | 2018-11-26 03:50 | 0.72915 | 10.0307
12.5 | 2018-11-26 04:00 | 0.69702 | 4.3609
12.5069 | 2018-11-26 04:10 | 0.69702 | 4.3609
12.5139 | 2018-11-26 04:20 | 0.67209 | 11.3267
12.5208 | 2018-11-26 04:30 | 0.6119 | 9.216
12.5278 | 2018-11-26 04:40 | 0.57789 | 3.1743
12.5347 | 2018-11-26 04:50 | 0.63524 | 9.2399
12.5417 | 2018-11-26 05:00 | 0.49033 | 7.6178
12.5486 | 2018-11-26 05:10 | 0.49033 | 7.6178
12.5556 | 2018-11-26 05:20 | 0.37711 | 358.6324
12.5625 | 2018-11-26 05:30 | 0.41335 | 2.3571
12.5694 | 2018-11-26 05:40 | 0.27735 | 8.9189
12.5764 | 2018-11-26 05:50 | 0.26792 | 6.8598
12.5833 | 2018-11-26 06:00 | 0.36549 | 2.9798
12.5903 | 2018-11-26 06:10 | 0.36549 | 2.9798
12.5972 | 2018-11-26 06:20 | 0.20124 | 343.5462
12.6042 | 2018-11-26 06:30 | 0.16164 | 351.8198
12.6111 | 2018-11-26 06:40 | 0.095718 | 302.1957
12.6181 | 2018-11-26 06:50 | 0.10373 | 213.9965
12.625 | 2018-11-26 07:00 | 0.15967 | 207.207
12.6319 | 2018-11-26 07:10 | 0.15967 | 207.207
12.6389 | 2018-11-26 07:20 | 0.39089 | 201.7742
12.6458 | 2018-11-26 07:30 | 0.46064 | 194.9715
12.6528 | 2018-11-26 07:40 | 0.53093 | 205.5515
12.6597 | 2018-11-26 07:50 | 0.60814 | 184.8106
12.6667 | 2018-11-26 08:00 | 0.6396 | 194.5794
12.6736 | 2018-11-26 08:10 | 0.6396 | 194.5794
12.6806 | 2018-11-26 08:20 | 0.60034 | 188.3326
12.6875 | 2018-11-26 08:30 | 0.59719 | 181.4393
12.6944 | 2018-11-26 08:40 | 0.63007 | 175.3572
12.7014 | 2018-11-26 08:50 | 0.73799 | 191.1729
12.7083 | 2018-11-26 09:00 | 0.79975 | 186.2453
12.7153 | 2018-11-26 09:10 | 0.79975 | 186.2453
12.7222 | 2018-11-26 09:20 | 0.69271 | 191.829
12.7292 | 2018-11-26 09:30 | 0.69245 | 189.4759
12.7361 | 2018-11-26 09:40 | 0.80081 | 184.7993
12.7431 | 2018-11-26 09:50 | 0.75232 | 189.9506
12.75 | 2018-11-26 10:00 | 0.80262 | 183.6431
12.7569 | 2018-11-26 10:10 | 0.80262 | 183.6431
12.7639 | 2018-11-26 10:20 | 0.63708 | 186.4892
12.7708 | 2018-11-26 10:30 | 0.65705 | 194.5438
12.7778 | 2018-11-26 10:40 | 0.66556 | 188.6414
12.7847 | 2018-11-26 10:50 | 0.57418 | 184.9957
12.7917 | 2018-11-26 11:00 | 0.64614 | 190.1621
12.7986 | 2018-11-26 11:10 | 0.64614 | 190.1621
12.8056 | 2018-11-26 11:20 | 0.60316 | 184.8504
12.8125 | 2018-11-26 11:30 | 0.6164 | 191.5105
12.8194 | 2018-11-26 11:40 | 0.50839 | 190.4258
12.8264 | 2018-11-26 11:50 | 0.50581 | 191.8653
12.8333 | 2018-11-26 12:00 | 0.54231 | 185.2901
12.8403 | 2018-11-26 12:10 | 0.54231 | 185.2901
12.8472 | 2018-11-26 12:20 | 0.37464 | 192.3297
12.8542 | 2018-11-26 12:30 | 0.25943 | 176.6854
12.8611 | 2018-11-26 12:40 | 0.1666 | 172.0645
12.8681 | 2018-11-26 12:50 | 0.21446 | 186.6942
12.875 | 2018-11-26 13:00 | 0.041231 | 67.1663
12.8819 | 2018-11-26 13:10 | 0.041231 | 67.1663
12.8889 | 2018-11-26 13:20 | 0.24131 | 17.609
12.8958 | 2018-11-26 13:30 | 0.33903 | 19.2901
12.9028 | 2018-11-26 13:40 | 0.51282 | 16.7741
12.9097 | 2018-11-26 13:50 | 0.37741 | 14.7358
12.9167 | 2018-11-26 14:00 | 0.52739 | 9.6052
12.9236 | 2018-11-26 14:10 | 0.52739 | 9.6052
12.9306 | 2018-11-26 14:20 | 0.6892 | 12.8264
12.9375 | 2018-11-26 14:30 | 0.60089 | 9.8699
12.9444 | 2018-11-26 14:40 | 0.62053 | 5.1777
12.9514 | 2018-11-26 14:50 | 0.6975 | 8.4089
12.9583 | 2018-11-26 15:00 | 0.82581 | 6.187
12.9653 | 2018-11-26 15:10 | 0.82581 | 6.187
12.9722 | 2018-11-26 15:20 | 0.98343 | 10.4872
12.9792 | 2018-11-26 15:30 | 0.74384 | 7.1823
12.9861 | 2018-11-26 15:40 | 0.84355 | 9.0715
12.9931 | 2018-11-26 15:50 | 0.80204 | 7.5946
13 | 2018-11-26 16:00 | 0.73457 | 2.2626
13.0069 | 2018-11-26 16:10 | 0.73457 | 2.2626
13.0139 | 2018-11-26 16:20 | 0.74803 | 9.8527
13.0208 | 2018-11-26 16:30 | 0.74432 | 8.5764
13.0278 | 2018-11-26 16:40 | 0.57678 | 11.0956
13.0347 | 2018-11-26 16:50 | 0.586 | 14.6291
13.0417 | 2018-11-26 17:00 | 0.49408 | 358.9563
13.0486 | 2018-11-26 17:10 | 0.49408 | 358.9563
13.0556 | 2018-11-26 17:20 | 0.45906 | 8.5184
13.0625 | 2018-11-26 17:30 | 0.46556 | 8.0257
13.0694 | 2018-11-26 17:40 | 0.43256 | 353.7622
13.0764 | 2018-11-26 17:50 | 0.44219 | 1.6847
13.0833 | 2018-11-26 18:00 | 0.30109 | 8.2108
13.0903 | 2018-11-26 18:10 | 0.30109 | 8.2108
13.0972 | 2018-11-26 18:20 | 0.28557 | 350.9335
13.1042 | 2018-11-26 18:30 | 0.18732 | 12.3298
13.1111 | 2018-11-26 18:40 | 0.21986 | 349.2523
13.1181 | 2018-11-26 18:50 | 0.16357 | 348.0031
13.125 | 2018-11-26 19:00 | 0.096675 | 309.1226
13.1319 | 2018-11-26 19:10 | 0.096675 | 309.1226
13.1389 | 2018-11-26 19:20 | 0.14101 | 228.7376
13.1458 | 2018-11-26 19:30 | 0.29051 | 209.0354
13.1528 | 2018-11-26 19:40 | 0.36653 | 197.7923
13.1597 | 2018-11-26 19:50 | 0.403 | 202.6199
13.1667 | 2018-11-26 20:00 | 0.44783 | 195.2776
13.1736 | 2018-11-26 20:10 | 0.44783 | 195.2776
13.1806 | 2018-11-26 20:20 | 0.61466 | 190.6884
13.1875 | 2018-11-26 20:30 | 0.66639 | 183.6997
13.1944 | 2018-11-26 20:40 | 0.60949 | 185.1774
13.2014 | 2018-11-26 20:50 | 0.56801 | 180.4035
13.2083 | 2018-11-26 21:00 | 0.68855 | 186.5883
13.2153 | 2018-11-26 21:10 | 0.68855 | 186.5883
13.2222 | 2018-11-26 21:20 | 0.65989 | 187.6635
13.2292 | 2018-11-26 21:30 | 0.65838 | 187.3301
13.2361 | 2018-11-26 21:40 | 0.68936 | 184.7429
13.2431 | 2018-11-26 21:50 | 0.62953 | 191.4527
13.25 | 2018-11-26 22:00 | 0.65309 | 187.8323
13.2569 | 2018-11-26 22:10 | 0.65309 | 187.8323
13.2639 | 2018-11-26 22:20 | 0.59171 | 187.9658
13.2708 | 2018-11-26 22:30 | 0.68209 | 191.244
13.2778 | 2018-11-26 22:40 | 0.6309 | 186.3703
13.2847 | 2018-11-26 22:50 | 0.67678 | 195.864
13.2917 | 2018-11-26 23:00 | 0.64465 | 182.5784
13.2986 | 2018-11-26 23:10 | 0.64465 | 182.5784
13.3056 | 2018-11-26 23:20 | 0.65535 | 192.4245
13.3125 | 2018-11-26 23:30 | 0.64959 | 174.8774
13.3194 | 2018-11-26 23:40 | 0.53361 | 193.4373
13.3264 | 2018-11-26 23:50 | 0.58222 | 173.0947
13.3333 | 2018-11-27 | 0.52324 | 181.7523
13.3403 | 2018-11-27 00:10 | 0.52324 | 181.7523
13.3472 | 2018-11-27 00:20 | 0.44255 | 182.8495
13.3542 | 2018-11-27 00:30 | 0.37718 | 188.5383
13.3611 | 2018-11-27 00:40 | 0.33639 | 186.8292
13.3681 | 2018-11-27 00:50 | 0.26343 | 183.2643
13.375 | 2018-11-27 01:00 | 0.23025 | 185.983
13.3819 | 2018-11-27 01:10 | 0.23025 | 185.983
13.3889 | 2018-11-27 01:20 | 0.080623 | 203.3852
13.3958 | 2018-11-27 01:30 | 0.078103 | 76.6755
13.4028 | 2018-11-27 01:40 | 0.1841 | 14.7911
13.4097 | 2018-11-27 01:50 | 0.30099 | 27.0758
13.4167 | 2018-11-27 02:00 | 0.46555 | 22.2128
13.4236 | 2018-11-27 02:10 | 0.46555 | 22.2128
13.4306 | 2018-11-27 02:20 | 0.56948 | 14.2315
13.4375 | 2018-11-27 02:30 | 0.56606 | 18.1149
13.4444 | 2018-11-27 02:40 | 0.64999 | 10.5493
13.4514 | 2018-11-27 02:50 | 0.73576 | 10.2561
13.4583 | 2018-11-27 03:00 | 0.6712 | 6.4156
13.4653 | 2018-11-27 03:10 | 0.6712 | 6.4156
13.4722 | 2018-11-27 03:20 | 0.78987 | 2.6849
13.4792 | 2018-11-27 03:30 | 0.77671 | 8.5891
13.4861 | 2018-11-27 03:40 | 0.79473 | 12.7947
13.4931 | 2018-11-27 03:50 | 0.87912 | 12.2814
13.5 | 2018-11-27 04:00 | 0.83638 | 12.3579
13.5069 | 2018-11-27 04:10 | 0.83638 | 12.3579
13.5139 | 2018-11-27 04:20 | 0.7441 | 6.0171
13.5208 | 2018-11-27 04:30 | 0.73981 | 9.8061
13.5278 | 2018-11-27 04:40 | 0.61665 | 6.2376
13.5347 | 2018-11-27 04:50 | 0.81809 | 13.6456
13.5417 | 2018-11-27 05:00 | 0.69582 | 8.5959
13.5486 | 2018-11-27 05:10 | 0.69582 | 8.5959
13.5556 | 2018-11-27 05:20 | 0.65592 | 8.3278
13.5625 | 2018-11-27 05:30 | 0.63348 | 11.8421
13.5694 | 2018-11-27 05:40 | 0.41035 | 2.3743
13.5764 | 2018-11-27 05:50 | 0.50137 | 6.6431
13.5833 | 2018-11-27 06:00 | 0.55161 | 6.5581
13.5903 | 2018-11-27 06:10 | 0.55161 | 6.5581
13.5972 | 2018-11-27 06:20 | 0.33065 | 5.7278
13.6042 | 2018-11-27 06:30 | 0.41962 | 7.5315
13.6111 | 2018-11-27 06:40 | 0.39096 | 10.0165
13.6181 | 2018-11-27 06:50 | 0.32257 | 13.9932
13.625 | 2018-11-27 07:00 | 0.27 | 0
13.6319 | 2018-11-27 07:10 | 0.27 | 0
13.6389 | 2018-11-27 07:20 | 0.11151 | 330.4463
13.6458 | 2018-11-27 07:30 | 0.018358 | 330.6422
13.6528 | 2018-11-27 07:40 | 0.044045 | 230.5275
13.6597 | 2018-11-27 07:50 | 0.17368 | 234.8458
13.6667 | 2018-11-27 08:00 | 0.20144 | 198.5249
13.6736 | 2018-11-27 08:10 | 0.20144 | 198.5249
13.6806 | 2018-11-27 08:20 | 0.40637 | 200.7541
13.6875 | 2018-11-27 08:30 | 0.43231 | 202.2936
13.6944 | 2018-11-27 08:40 | 0.50478 | 199.44
13.7014 | 2018-11-27 08:50 | 0.5578 | 187.52
13.7083 | 2018-11-27 09:00 | 0.65674 | 186.1186
13.7153 | 2018-11-27 09:10 | 0.65674 | 186.1186
13.7222 | 2018-11-27 09:20 | 0.61278 | 187.8789
13.7292 | 2018-11-27 09:30 | 0.4952 | 191.0603
13.7361 | 2018-11-27 09:40 | 0.6109 | 191.3283
13.7431 | 2018-11-27 09:50 | 0.64595 | 193.1542
13.75 | 2018-11-27 10:00 | 0.66343 | 188.582
13.7569 | 2018-11-27 10:10 | 0.66343 | 188.582
13.7639 | 2018-11-27 10:20 | 0.65531 | 186.5719
13.7708 | 2018-11-27 10:30 | 0.7193 | 190.1695
13.7778 | 2018-11-27 10:40 | 0.67883 | 186.0885
13.7847 | 2018-11-27 10:50 | 0.60422 | 194.8642
13.7917 | 2018-11-27 11:00 | 0.68031 | 185.6519
13.7986 | 2018-11-27 11:10 | 0.68031 | 185.6519
13.8056 | 2018-11-27 11:20 | 0.62153 | 191.9789
13.8125 | 2018-11-27 11:30 | 0.60416 | 181.3278
13.8194 | 2018-11-27 11:40 | 0.60246 | 188.3991
13.8264 | 2018-11-27 11:50 | 0.585 | 180
13.8333 | 2018-11-27 12:00 | 0.5023 | 193.7043
13.8403 | 2018-11-27 12:10 | 0.5023 | 193.7043
13.8472 | 2018-11-27 12:20 | 0.42933 | 194.8455
13.8542 | 2018-11-27 12:30 | 0.43278 | 183.4442
13.8611 | 2018-11-27 12:40 | 0.34085 | 187.4169
13.8681 | 2018-11-27 12:50 | 0.32138 | 186.9702
13.875 | 2018-11-27 13:00 | 0.30384 | 190.2374
13.8819 | 2018-11-27 13:10 | 0.30384 | 190.2374
13.8889 | 2018-11-27 13:20 | 0.24948 | 138.9005
13.8958 | 2018-11-27 13:30 | 0.062 | 90
13.9028 | 2018-11-27 13:40 | 0.059397 | 45
13.9097 | 2018-11-27 13:50 | 0.10847 | 40.8878
13.9167 | 2018-11-27 14:00 | 0.2242 | 24.5074
13.9236 | 2018-11-27 14:10 | 0.2242 | 24.5074
13.9306 | 2018-11-27 14:20 | 0.45195 | 17.5128
13.9375 | 2018-11-27 14:30 | 0.42541 | 13.8729
13.9444 | 2018-11-27 14:40 | 0.56953 | 11.0337
13.9514 | 2018-11-27 14:50 | 0.67491 | 19.294
13.9583 | 2018-11-27 15:00 | 0.88192 | 14.7138
13.9653 | 2018-11-27 15:10 | 0.88192 | 14.7138
13.9722 | 2018-11-27 15:20 | 0.76806 | 8.3094
13.9792 | 2018-11-27 15:30 | 0.85718 | 9.2645
13.9861 | 2018-11-27 15:40 | 0.78204 | 7.125
13.9931 | 2018-11-27 15:50 | 0.9134 | 10.5349
14 | 2018-11-27 16:00 | 0.84542 | 5.1576
14.0069 | 2018-11-27 16:10 | 0.84542 | 5.1576
14.0139 | 2018-11-27 16:20 | 0.83764 | 11.7795
14.0208 | 2018-11-27 16:30 | 0.86182 | 14.8586
14.0278 | 2018-11-27 16:40 | 0.71898 | 11.7163
14.0347 | 2018-11-27 16:50 | 0.85252 | 14.3297
14.0417 | 2018-11-27 17:00 | 0.78688 | 7.0076
14.0486 | 2018-11-27 17:10 | 0.78688 | 7.0076
14.0556 | 2018-11-27 17:20 | 0.70999 | 6.7947
14.0625 | 2018-11-27 17:30 | 0.73314 | 12.0456
14.0694 | 2018-11-27 17:40 | 0.7894 | 3.4133
14.0764 | 2018-11-27 17:50 | 0.46629 | 12.6354
14.0833 | 2018-11-27 18:00 | 0.51976 | 10.5316
14.0903 | 2018-11-27 18:10 | 0.51976 | 10.5316
14.0972 | 2018-11-27 18:20 | 0.76778 | 8.1618
14.1042 | 2018-11-27 18:30 | 0.46687 | 7.3838
14.1111 | 2018-11-27 18:40 | 0.63132 | 16.282
14.1181 | 2018-11-27 18:50 | 0.58833 | 7.7169
14.125 | 2018-11-27 19:00 | 0.49862 | 354.1293
14.1319 | 2018-11-27 19:10 | 0.49862 | 354.1293
14.1389 | 2018-11-27 19:20 | 0.34846 | 8.0836
14.1458 | 2018-11-27 19:30 | 0.27505 | 5.0058
14.1528 | 2018-11-27 19:40 | 0.24713 | 349.5085
14.1597 | 2018-11-27 19:50 | 0.19812 | 349.8245
14.1667 | 2018-11-27 20:00 | 0.13322 | 352.2348
14.1736 | 2018-11-27 20:10 | 0.13322 | 352.2348
14.1806 | 2018-11-27 20:20 | 0.098473 | 325.3416
14.1875 | 2018-11-27 20:30 | 0.031401 | 232.7652
14.1944 | 2018-11-27 20:40 | 0.16863 | 236.1215
14.2014 | 2018-11-27 20:50 | 0.084119 | 198.0042
14.2083 | 2018-11-27 21:00 | 0.24127 | 187.8614
14.2153 | 2018-11-27 21:10 | 0.24127 | 187.8614
14.2222 | 2018-11-27 21:20 | 0.308 | 186.5251
14.2292 | 2018-11-27 21:30 | 0.45292 | 189.2751
14.2361 | 2018-11-27 21:40 | 0.39283 | 197.3279
14.2431 | 2018-11-27 21:50 | 0.50688 | 196.5044
14.25 | 2018-11-27 22:00 | 0.52365 | 182.846
14.2569 | 2018-11-27 22:10 | 0.52365 | 182.846
14.2639 | 2018-11-27 22:20 | 0.60395 | 186.5602
14.2708 | 2018-11-27 22:30 | 0.58111 | 186.8193
14.2778 | 2018-11-27 22:40 | 0.52983 | 184.7636
14.2847 | 2018-11-27 22:50 | 0.50231 | 192.1824
14.2917 | 2018-11-27 23:00 | 0.596 | 180.0961
14.2986 | 2018-11-27 23:10 | 0.596 | 180.0961
14.3056 | 2018-11-27 23:20 | 0.51218 | 186.3896
14.3125 | 2018-11-27 23:30 | 0.50667 | 182.9415
14.3194 | 2018-11-27 23:40 | 0.57522 | 181.5939
14.3264 | 2018-11-27 23:50 | 0.51563 | 184.5606
14.3333 | 2018-11-28 | 0.54169 | 190.8536
14.3403 | 2018-11-28 00:10 | 0.54169 | 190.8536
14.3472 | 2018-11-28 00:20 | 0.46211 | 176.0292
14.3542 | 2018-11-28 00:30 | 0.4162 | 188.1496
14.3611 | 2018-11-28 00:40 | 0.40524 | 181.9798
14.3681 | 2018-11-28 00:50 | 0.41202 | 179.4437
14.375 | 2018-11-28 01:00 | 0.30929 | 171.6341
14.3819 | 2018-11-28 01:10 | 0.30929 | 171.6341
14.3889 | 2018-11-28 01:20 | 0.30986 | 172.2099
14.3958 | 2018-11-28 01:30 | 0.14243 | 175.5704
14.4028 | 2018-11-28 01:40 | 0.20674 | 155.4184
14.4097 | 2018-11-28 01:50 | 0.072622 | 141.7098
14.4167 | 2018-11-28 02:00 | 0.18258 | 101.3715
14.4236 | 2018-11-28 02:10 | 0.18258 | 101.3715
14.4306 | 2018-11-28 02:20 | 0.22496 | 32.8424
14.4375 | 2018-11-28 02:30 | 0.34047 | 28.221
14.4444 | 2018-11-28 02:40 | 0.37779 | 9.1382
14.4514 | 2018-11-28 02:50 | 0.53674 | 14.3469
14.4583 | 2018-11-28 03:00 | 0.45097 | 10.0889
14.4653 | 2018-11-28 03:10 | 0.45097 | 10.0889
14.4722 | 2018-11-28 03:20 | 0.86775 | 4.5608
14.4792 | 2018-11-28 03:30 | 0.99757 | 15.3458
14.4861 | 2018-11-28 03:40 | 0.88813 | 12.2209
14.4931 | 2018-11-28 03:50 | 0.98416 | 11.9037
14.5 | 2018-11-28 04:00 | 0.82577 | 7.8652
14.5069 | 2018-11-28 04:10 | 0.82577 | 7.8652
14.5139 | 2018-11-28 04:20 | 0.76853 | 7.4764
14.5208 | 2018-11-28 04:30 | 0.92212 | 6.0383
14.5278 | 2018-11-28 04:40 | 1.0133 | 8.5699
14.5347 | 2018-11-28 04:50 | 1.0102 | 10.8984
14.5417 | 2018-11-28 05:00 | 1.0308 | 13.8071
14.5486 | 2018-11-28 05:10 | 1.0308 | 13.8071
14.5556 | 2018-11-28 05:20 | 0.91982 | 4.4895
14.5625 | 2018-11-28 05:30 | 0.87475 | 5.9713
14.5694 | 2018-11-28 05:40 | 0.78514 | 16.9579
14.5764 | 2018-11-28 05:50 | 0.83477 | 10.4215
14.5833 | 2018-11-28 06:00 | 0.79014 | 10.0584
14.5903 | 2018-11-28 06:10 | 0.79014 | 10.0584
14.5972 | 2018-11-28 06:20 | 0.68588 | 9.737
14.6042 | 2018-11-28 06:30 | 0.73623 | 11.6762
14.6111 | 2018-11-28 06:40 | 0.6554 | 13.2305
14.6181 | 2018-11-28 06:50 | 0.63267 | 4.1695
14.625 | 2018-11-28 07:00 | 0.50879 | 15.6206
14.6319 | 2018-11-28 07:10 | 0.50879 | 15.6206
14.6389 | 2018-11-28 07:20 | 0.57938 | 357.9228
14.6458 | 2018-11-28 07:30 | 0.4942 | 358.3767
14.6528 | 2018-11-28 07:40 | 0.50961 | 357.1881
14.6597 | 2018-11-28 07:50 | 0.28278 | 4.2588
14.6667 | 2018-11-28 08:00 | 0.236 | 359.7572
14.6736 | 2018-11-28 08:10 | 0.236 | 359.7572
14.6806 | 2018-11-28 08:20 | 0.15116 | 357.3458
14.6875 | 2018-11-28 08:30 | 0.19888 | 13.9664
14.6944 | 2018-11-28 08:40 | 0.14699 | 353.3585
14.7014 | 2018-11-28 08:50 | 0.05831 | 329.0363
14.7083 | 2018-11-28 09:00 | 0.1056 | 245.3764
14.7153 | 2018-11-28 09:10 | 0.1056 | 245.3764
14.7222 | 2018-11-28 09:20 | 0.16 | 216.8699
14.7292 | 2018-11-28 09:30 | 0.19088 | 215.1887
14.7361 | 2018-11-28 09:40 | 0.22567 | 218.3426
14.7431 | 2018-11-28 09:50 | 0.33131 | 203.8571
14.75 | 2018-11-28 10:00 | 0.3731 | 187.3917
14.7569 | 2018-11-28 10:10 | 0.3731 | 187.3917
14.7639 | 2018-11-28 10:20 | 0.43859 | 187.3357
14.7708 | 2018-11-28 10:30 | 0.47642 | 186.8714
14.7778 | 2018-11-28 10:40 | 0.41633 | 173.9334
14.7847 | 2018-11-28 10:50 | 0.42557 | 187.4256
14.7917 | 2018-11-28 11:00 | 0.43871 | 183.2668
14.7986 | 2018-11-28 11:10 | 0.43871 | 183.2668
14.8056 | 2018-11-28 11:20 | 0.55467 | 184.4462
14.8125 | 2018-11-28 11:30 | 0.50284 | 191.3546
14.8194 | 2018-11-28 11:40 | 0.52221 | 185.2739
14.8264 | 2018-11-28 11:50 | 0.57609 | 180.9946
14.8333 | 2018-11-28 12:00 | 0.4821 | 185.3558
14.8403 | 2018-11-28 12:10 | 0.4821 | 185.3558
14.8472 | 2018-11-28 12:20 | 0.53528 | 189.4623
14.8542 | 2018-11-28 12:30 | 0.46182 | 185.0933
14.8611 | 2018-11-28 12:40 | 0.47636 | 184.3341
14.8681 | 2018-11-28 12:50 | 0.46006 | 186.6152
14.875 | 2018-11-28 13:00 | 0.41201 | 180.4172
14.8819 | 2018-11-28 13:10 | 0.41201 | 180.4172
14.8889 | 2018-11-28 13:20 | 0.26737 | 183.0015
14.8958 | 2018-11-28 13:30 | 0.36325 | 192.238
14.9028 | 2018-11-28 13:40 | 0.18612 | 171.3475
14.9097 | 2018-11-28 13:50 | 0.26692 | 191.0152
14.9167 | 2018-11-28 14:00 | 0.10607 | 171.8699
14.9236 | 2018-11-28 14:10 | 0.10607 | 171.8699
14.9306 | 2018-11-28 14:20 | 0.064885 | 65.4099
14.9375 | 2018-11-28 14:30 | 0.15951 | 30.1013
14.9444 | 2018-11-28 14:40 | 0.2597 | 32.0989
14.9514 | 2018-11-28 14:50 | 0.29848 | 28.6258
14.9583 | 2018-11-28 15:00 | 0.41755 | 4.946
14.9653 | 2018-11-28 15:10 | 0.41755 | 4.946
14.9722 | 2018-11-28 15:20 | 0.50065 | 8.6156
14.9792 | 2018-11-28 15:30 | 0.69234 | 12.852
14.9861 | 2018-11-28 15:40 | 0.74003 | 13.3602
14.9931 | 2018-11-28 15:50 | 0.76941 | 9.8786
15 | 2018-11-28 16:00 | 0.80342 | 9.6734
15.0069 | 2018-11-28 16:10 | 0.80342 | 9.6734
15.0139 | 2018-11-28 16:20 | 0.90726 | 10.8641
15.0208 | 2018-11-28 16:30 | 0.85133 | 4.2439
15.0278 | 2018-11-28 16:40 | 1.0966 | 13.3392
15.0347 | 2018-11-28 16:50 | 0.84507 | 11.1903
15.0417 | 2018-11-28 17:00 | 0.98524 | 9.405
15.0486 | 2018-11-28 17:10 | 0.98524 | 9.405
15.0556 | 2018-11-28 17:20 | 0.89213 | 11.247
15.0625 | 2018-11-28 17:30 | 1.0586 | 8.4746
15.0694 | 2018-11-28 17:40 | 1.0128 | 11.9091
15.0764 | 2018-11-28 17:50 | 1.0707 | 10.7117
15.0833 | 2018-11-28 18:00 | 0.86095 | 11.3882
15.0903 | 2018-11-28 18:10 | 0.86095 | 11.3882
15.0972 | 2018-11-28 18:20 | 0.97365 | 5.5993
15.1042 | 2018-11-28 18:30 | 0.85983 | 9.9115
15.1111 | 2018-11-28 18:40 | 0.89296 | 6.0426
15.1181 | 2018-11-28 18:50 | 0.76753 | 6.8843
15.125 | 2018-11-28 19:00 | 0.61683 | 2.9737
15.1319 | 2018-11-28 19:10 | 0.61683 | 2.9737
15.1389 | 2018-11-28 19:20 | 0.4753 | 18.778
15.1458 | 2018-11-28 19:30 | 0.56443 | 2.2338
15.1528 | 2018-11-28 19:40 | 0.61166 | 7.7989
15.1597 | 2018-11-28 19:50 | 0.4272 | 355.7042
15.1667 | 2018-11-28 20:00 | 0.43941 | 6.009
15.1736 | 2018-11-28 20:10 | 0.43941 | 6.009
15.1806 | 2018-11-28 20:20 | 0.36616 | 7.5326
15.1875 | 2018-11-28 20:30 | 0.3261 | 15.6558
15.1944 | 2018-11-28 20:40 | 0.32504 | 359.1186
15.2014 | 2018-11-28 20:50 | 0.16038 | 356.0671
15.2083 | 2018-11-28 21:00 | 0.17605 | 1.302
15.2153 | 2018-11-28 21:10 | 0.17605 | 1.302
15.2222 | 2018-11-28 21:20 | 0.009 | 270
15.2292 | 2018-11-28 21:30 | 0.12279 | 229.9554
15.2361 | 2018-11-28 21:40 | 0.22847 | 209.9315
15.2431 | 2018-11-28 21:50 | 0.18385 | 202.3801
15.25 | 2018-11-28 22:00 | 0.23149 | 198.9046
15.2569 | 2018-11-28 22:10 | 0.23149 | 198.9046
15.2639 | 2018-11-28 22:20 | 0.41189 | 201.2073
15.2708 | 2018-11-28 22:30 | 0.41376 | 201.1071
15.2778 | 2018-11-28 22:40 | 0.48622 | 199.963
15.2847 | 2018-11-28 22:50 | 0.4686 | 187.1098
15.2917 | 2018-11-28 23:00 | 0.43106 | 187.8669
15.2986 | 2018-11-28 23:10 | 0.43106 | 187.8669
15.3056 | 2018-11-28 23:20 | 0.40498 | 174.3316
15.3125 | 2018-11-28 23:30 | 0.44417 | 192.8786
15.3194 | 2018-11-28 23:40 | 0.54265 | 198.7021
15.3264 | 2018-11-28 23:50 | 0.47205 | 191.2385
15.3333 | 2018-11-29 | 0.5187 | 197.387
15.3403 | 2018-11-29 00:10 | 0.5187 | 197.387
15.3472 | 2018-11-29 00:20 | 0.4788 | 194.7618
15.3542 | 2018-11-29 00:30 | 0.4565 | 196.8074
15.3611 | 2018-11-29 00:40 | 0.53803 | 179.361
15.3681 | 2018-11-29 00:50 | 0.39564 | 195.09
15.375 | 2018-11-29 01:00 | 0.5241 | 183.7195
15.3819 | 2018-11-29 01:10 | 0.5241 | 183.7195
15.3889 | 2018-11-29 01:20 | 0.36502 | 188.5075
15.3958 | 2018-11-29 01:30 | 0.37889 | 183.9348
15.4028 | 2018-11-29 01:40 | 0.421 | 179.8639
15.4097 | 2018-11-29 01:50 | 0.39001 | 179.7062
15.4167 | 2018-11-29 02:00 | 0.21949 | 188.6469
15.4236 | 2018-11-29 02:10 | 0.21949 | 188.6469
15.4306 | 2018-11-29 02:20 | 0.078339 | 194.0362
15.4375 | 2018-11-29 02:30 | 0.065765 | 118.1237
15.4444 | 2018-11-29 02:40 | 0.084929 | 102.2361
15.4514 | 2018-11-29 02:50 | 0.042059 | 71.9958
15.4583 | 2018-11-29 03:00 | 0.1719 | 24.0302
15.4653 | 2018-11-29 03:10 | 0.1719 | 24.0302
15.4722 | 2018-11-29 03:20 | 0.37792 | 22.5616
15.4792 | 2018-11-29 03:30 | 0.36569 | 28.9481
15.4861 | 2018-11-29 03:40 | 0.47586 | 13.861
15.4931 | 2018-11-29 03:50 | 0.49116 | 25.3129
15.5 | 2018-11-29 04:00 | 0.47129 | 10.7615
15.5069 | 2018-11-29 04:10 | 0.47129 | 10.7615
15.5139 | 2018-11-29 04:20 | 0.69872 | 5.9146
15.5208 | 2018-11-29 04:30 | 0.78175 | 10.7637
15.5278 | 2018-11-29 04:40 | 0.67889 | 12.419
15.5347 | 2018-11-29 04:50 | 0.74181 | 12.9309
15.5417 | 2018-11-29 05:00 | 0.93522 | 14.1105
15.5486 | 2018-11-29 05:10 | 0.93522 | 14.1105
15.5556 | 2018-11-29 05:20 | 0.72846 | 8.208
15.5625 | 2018-11-29 05:30 | 0.80732 | 12.2286
15.5694 | 2018-11-29 05:40 | 0.91448 | 6.2779
15.5764 | 2018-11-29 05:50 | 0.84047 | 1.9092
15.5833 | 2018-11-29 06:00 | 0.64688 | 5.4109
15.5903 | 2018-11-29 06:10 | 0.64688 | 5.4109
15.5972 | 2018-11-29 06:20 | 0.79753 | 14.8203
15.6042 | 2018-11-29 06:30 | 0.54499 | 9.8253
15.6111 | 2018-11-29 06:40 | 0.75689 | 8.28
15.6181 | 2018-11-29 06:50 | 0.77711 | 6.5763
15.625 | 2018-11-29 07:00 | 0.74756 | 6.9919
15.6319 | 2018-11-29 07:10 | 0.74756 | 6.9919
15.6389 | 2018-11-29 07:20 | 0.68765 | 2.5004
15.6458 | 2018-11-29 07:30 | 0.61801 | 7.999
15.6528 | 2018-11-29 07:40 | 0.51246 | 11.0249
15.6597 | 2018-11-29 07:50 | 0.48843 | 9.308
15.6667 | 2018-11-29 08:00 | 0.58245 | 2.2631
15.6736 | 2018-11-29 08:10 | 0.58245 | 2.2631
15.6806 | 2018-11-29 08:20 | 0.40741 | 15.8102
15.6875 | 2018-11-29 08:30 | 0.4036 | 350.4443
15.6944 | 2018-11-29 08:40 | 0.30101 | 0.57104
15.7014 | 2018-11-29 08:50 | 0.211 | 7.8997
15.7083 | 2018-11-29 09:00 | 0.19006 | 32.1013
15.7153 | 2018-11-29 09:10 | 0.19006 | 32.1013
15.7222 | 2018-11-29 09:20 | 0.15008 | 330.0184
15.7292 | 2018-11-29 09:30 | 0.20038 | 320.6703
15.7361 | 2018-11-29 09:40 | 0.051788 | 10.008
15.7431 | 2018-11-29 09:50 | 0.084149 | 176.5936
15.75 | 2018-11-29 10:00 | 0.074545 | 263.0656
15.7569 | 2018-11-29 10:10 | 0.074545 | 263.0656
15.7639 | 2018-11-29 10:20 | 0.2272 | 207.2417
15.7708 | 2018-11-29 10:30 | 0.2934 | 202.019
15.7778 | 2018-11-29 10:40 | 0.34024 | 186.5819
15.7847 | 2018-11-29 10:50 | 0.45049 | 187.1408
15.7917 | 2018-11-29 11:00 | 0.40556 | 200.0435
15.7986 | 2018-11-29 11:10 | 0.40556 | 200.0435
15.8056 | 2018-11-29 11:20 | 0.36283 | 189.3585
15.8125 | 2018-11-29 11:30 | 0.44538 | 175.4928
15.8194 | 2018-11-29 11:40 | 0.42901 | 196.6609
15.8264 | 2018-11-29 11:50 | 0.43538 | 191.2583
15.8333 | 2018-11-29 12:00 | 0.48546 | 202.6562
15.8403 | 2018-11-29 12:10 | 0.48546 | 202.6562
15.8472 | 2018-11-29 12:20 | 0.53385 | 186.8854
15.8542 | 2018-11-29 12:30 | 0.51484 | 190.6333
15.8611 | 2018-11-29 12:40 | 0.44471 | 186.326
15.8681 | 2018-11-29 12:50 | 0.44327 | 195.5725
15.875 | 2018-11-29 13:00 | 0.42424 | 194.8879
15.8819 | 2018-11-29 13:10 | 0.42424 | 194.8879
15.8889 | 2018-11-29 13:20 | 0.3991 | 191.5633
15.8958 | 2018-11-29 13:30 | 0.32244 | 188.3814
15.9028 | 2018-11-29 13:40 | 0.36021 | 187.6577
15.9097 | 2018-11-29 13:50 | 0.40206 | 179.0024
15.9167 | 2018-11-29 14:00 | 0.31014 | 188.1562
15.9236 | 2018-11-29 14:10 | 0.31014 | 188.1562
15.9306 | 2018-11-29 14:20 | 0.21046 | 190.4023
15.9375 | 2018-11-29 14:30 | 0.19801 | 179.4213
15.9444 | 2018-11-29 14:40 | 0.18604 | 181.232
15.9514 | 2018-11-29 14:50 | 0.070519 | 161.822
15.9583 | 2018-11-29 15:00 | 0.067912 | 76.373
15.9653 | 2018-11-29 15:10 | 0.067912 | 76.373
15.9722 | 2018-11-29 15:20 | 0.14277 | 78.6901
15.9792 | 2018-11-29 15:30 | 0.20441 | 33.2236
15.9861 | 2018-11-29 15:40 | 0.24601 | 27.6067
15.9931 | 2018-11-29 15:50 | 0.26884 | 8.3411
16 | 2018-11-29 16:00 | 0.42661 | 17.8828
16.0069 | 2018-11-29 16:10 | 0.42661 | 17.8828
16.0139 | 2018-11-29 16:20 | 0.49165 | 5.9541
16.0208 | 2018-11-29 16:30 | 0.564 | 0.10159
16.0278 | 2018-11-29 16:40 | 0.6627 | 10.7843
16.0347 | 2018-11-29 16:50 | 0.65151 | 11.6894
16.0417 | 2018-11-29 17:00 | 0.73063 | 12.2481
16.0486 | 2018-11-29 17:10 | 0.73063 | 12.2481
16.0556 | 2018-11-29 17:20 | 0.8457 | 10.6987
16.0625 | 2018-11-29 17:30 | 0.82887 | 2.6277
16.0694 | 2018-11-29 17:40 | 0.78192 | 11.2093
16.0764 | 2018-11-29 17:50 | 0.7123 | 3.4609
16.0833 | 2018-11-29 18:00 | 0.56474 | 7.427
16.0903 | 2018-11-29 18:10 | 0.56474 | 7.427
16.0972 | 2018-11-29 18:20 | 0.6939 | 13.7559
16.1042 | 2018-11-29 18:30 | 0.73903 | 3.025
16.1111 | 2018-11-29 18:40 | 0.68364 | 5.0351
16.1181 | 2018-11-29 18:50 | 0.66445 | 11.5467
16.125 | 2018-11-29 19:00 | 0.68105 | 15.5872
16.1319 | 2018-11-29 19:10 | 0.68105 | 15.5872
16.1389 | 2018-11-29 19:20 | 0.5927 | 7.9524
16.1458 | 2018-11-29 19:30 | 0.64024 | 8.6237
16.1528 | 2018-11-29 19:40 | 0.48255 | 10.1455
16.1597 | 2018-11-29 19:50 | 0.55732 | 9.2933
16.1667 | 2018-11-29 20:00 | 0.46415 | 15.6232
16.1736 | 2018-11-29 20:10 | 0.46415 | 15.6232
16.1806 | 2018-11-29 20:20 | 0.40282 | 11.3099
16.1875 | 2018-11-29 20:30 | 0.40509 | 9.9506
16.1944 | 2018-11-29 20:40 | 0.35294 | 6.0175
16.2014 | 2018-11-29 20:50 | 0.36282 | 11.1241
16.2083 | 2018-11-29 21:00 | 0.29783 | 6.3614
16.2153 | 2018-11-29 21:10 | 0.29783 | 6.3614
16.2222 | 2018-11-29 21:20 | 0.29077 | 334.7569
16.2292 | 2018-11-29 21:30 | 0.1899 | 330.33
16.2361 | 2018-11-29 21:40 | 0.096047 | 14.4703
16.2431 | 2018-11-29 21:50 | 0.067209 | 313.1913
16.25 | 2018-11-29 22:00 | 0.1151 | 240.3169
16.2569 | 2018-11-29 22:10 | 0.1151 | 240.3169
16.2639 | 2018-11-29 22:20 | 0.069635 | 192.4396
16.2708 | 2018-11-29 22:30 | 0.1272 | 216.6897
16.2778 | 2018-11-29 22:40 | 0.3132 | 195.3674
16.2847 | 2018-11-29 22:50 | 0.23436 | 213.6901
16.2917 | 2018-11-29 23:00 | 0.34122 | 198.8067
16.2986 | 2018-11-29 23:10 | 0.34122 | 198.8067
16.3056 | 2018-11-29 23:20 | 0.43764 | 204.574
16.3125 | 2018-11-29 23:30 | 0.40036 | 201.6951
16.3194 | 2018-11-29 23:40 | 0.47521 | 191.9011
16.3264 | 2018-11-29 23:50 | 0.43983 | 192.7408
16.3333 | 2018-11-30 | 0.44902 | 207.0216
16.3403 | 2018-11-30 00:10 | 0.44902 | 207.0216
16.3472 | 2018-11-30 00:20 | 0.50294 | 190.1928
16.3542 | 2018-11-30 00:30 | 0.57962 | 187.2354
16.3611 | 2018-11-30 00:40 | 0.51968 | 189.8611
16.3681 | 2018-11-30 00:50 | 0.456 | 180
16.375 | 2018-11-30 01:00 | 0.45723 | 190.204
16.3819 | 2018-11-30 01:10 | 0.45723 | 190.204
16.3889 | 2018-11-30 01:20 | 0.49155 | 185.8382
16.3958 | 2018-11-30 01:30 | 0.42064 | 192.9129
16.4028 | 2018-11-30 01:40 | 0.47563 | 192.1368
16.4097 | 2018-11-30 01:50 | 0.5052 | 191.5323
16.4167 | 2018-11-30 02:00 | 0.36276 | 197.4859
16.4236 | 2018-11-30 02:10 | 0.36276 | 197.4859
16.4306 | 2018-11-30 02:20 | 0.33095 | 184.3323
16.4375 | 2018-11-30 02:30 | 0.38801 | 190.0935
16.4444 | 2018-11-30 02:40 | 0.31873 | 194.9083
16.4514 | 2018-11-30 02:50 | 0.27141 | 183.1681
16.4583 | 2018-11-30 03:00 | 0.14023 | 176.7295
16.4653 | 2018-11-30 03:10 | 0.14023 | 176.7295
16.4722 | 2018-11-30 03:20 | 0.11811 | 201.351
16.4792 | 2018-11-30 03:30 | 0.052173 | 77.8285
16.4861 | 2018-11-30 03:40 | 0.036249 | 114.444
16.4931 | 2018-11-30 03:50 | 0.085866 | 26.2666
16.5 | 2018-11-30 04:00 | 0.19517 | 21.965
16.5069 | 2018-11-30 04:10 | 0.19517 | 21.965
16.5139 | 2018-11-30 04:20 | 0.38777 | 15.8642
16.5208 | 2018-11-30 04:30 | 0.48274 | 7.1397
16.5278 | 2018-11-30 04:40 | 0.52191 | 10.5994
16.5347 | 2018-11-30 04:50 | 0.52991 | 4.8714
16.5417 | 2018-11-30 05:00 | 0.56178 | 8.909
16.5486 | 2018-11-30 05:10 | 0.56178 | 8.909
16.5556 | 2018-11-30 05:20 | 0.65169 | 14.1215
16.5625 | 2018-11-30 05:30 | 0.74121 | 10.4155
16.5694 | 2018-11-30 05:40 | 0.79272 | 7.4657
16.5764 | 2018-11-30 05:50 | 0.78238 | 12.0999
16.5833 | 2018-11-30 06:00 | 0.74635 | 12.3789
16.5903 | 2018-11-30 06:10 | 0.74635 | 12.3789
16.5972 | 2018-11-30 06:20 | 0.6948 | 10.1131
16.6042 | 2018-11-30 06:30 | 0.78692 | 10.396
16.6111 | 2018-11-30 06:40 | 0.80171 | 5.5115
16.6181 | 2018-11-30 06:50 | 0.7339 | 10.7587
16.625 | 2018-11-30 07:00 | 0.56663 | 6.4854
16.6319 | 2018-11-30 07:10 | 0.56663 | 6.4854
16.6389 | 2018-11-30 07:20 | 0.6834 | 15.3581
16.6458 | 2018-11-30 07:30 | 0.56294 | 12.308
16.6528 | 2018-11-30 07:40 | 0.60952 | 14.5378
16.6597 | 2018-11-30 07:50 | 0.60072 | 9.7759
16.6667 | 2018-11-30 08:00 | 0.63311 | 9.7301
16.6736 | 2018-11-30 08:10 | 0.63311 | 9.7301
16.6806 | 2018-11-30 08:20 | 0.45951 | 5.996
16.6875 | 2018-11-30 08:30 | 0.41689 | 6.75
16.6944 | 2018-11-30 08:40 | 0.48068 | 11.5203
16.7014 | 2018-11-30 08:50 | 0.37101 | 359.6911
16.7083 | 2018-11-30 09:00 | 0.44041 | 5.9954
16.7153 | 2018-11-30 09:10 | 0.44041 | 5.9954
16.7222 | 2018-11-30 09:20 | 0.35696 | 8.5387
16.7292 | 2018-11-30 09:30 | 0.30624 | 2.2457
16.7361 | 2018-11-30 09:40 | 0.23261 | 14.6934
16.7431 | 2018-11-30 09:50 | 0.16476 | 341.2351
16.75 | 2018-11-30 10:00 | 0.1685 | 4.4248
16.7569 | 2018-11-30 10:10 | 0.1685 | 4.4248
16.7639 | 2018-11-30 10:20 | 0.10891 | 346.7294
16.7708 | 2018-11-30 10:30 | 0.14256 | 325.8641
16.7778 | 2018-11-30 10:40 | 0.080081 | 344.0546
16.7847 | 2018-11-30 10:50 | 0.023324 | 210.9638
16.7917 | 2018-11-30 11:00 | 0.1028 | 217.0928
16.7986 | 2018-11-30 11:10 | 0.1028 | 217.0928
16.8056 | 2018-11-30 11:20 | 0.20887 | 205.829
16.8125 | 2018-11-30 11:30 | 0.28625 | 192.9196
16.8194 | 2018-11-30 11:40 | 0.29635 | 191.8787
16.8264 | 2018-11-30 11:50 | 0.40541 | 198.7031
16.8333 | 2018-11-30 12:00 | 0.41856 | 202.0302
16.8403 | 2018-11-30 12:10 | 0.41856 | 202.0302
16.8472 | 2018-11-30 12:20 | 0.43245 | 193.7792
16.8542 | 2018-11-30 12:30 | 0.52454 | 188.3309
16.8611 | 2018-11-30 12:40 | 0.4858 | 194.1793
16.8681 | 2018-11-30 12:50 | 0.5674 | 188.6156
16.875 | 2018-11-30 13:00 | 0.56123 | 194.2343
16.8819 | 2018-11-30 13:10 | 0.56123 | 194.2343
16.8889 | 2018-11-30 13:20 | 0.48726 | 194.3785
16.8958 | 2018-11-30 13:30 | 0.53808 | 189.3048
16.9028 | 2018-11-30 13:40 | 0.52719 | 190.7131
16.9097 | 2018-11-30 13:50 | 0.65481 | 192.6142
16.9167 | 2018-11-30 14:00 | 0.59256 | 185.3257
16.9236 | 2018-11-30 14:10 | 0.59256 | 185.3257
16.9306 | 2018-11-30 14:20 | 0.5103 | 194.0635
16.9375 | 2018-11-30 14:30 | 0.505 | 186.2525
16.9444 | 2018-11-30 14:40 | 0.51661 | 186.7811
16.9514 | 2018-11-30 14:50 | 0.49702 | 193.1415
16.9583 | 2018-11-30 15:00 | 0.523 | 188.6879
16.9653 | 2018-11-30 15:10 | 0.523 | 188.6879
16.9722 | 2018-11-30 15:20 | 0.34121 | 177.9846
16.9792 | 2018-11-30 15:30 | 0.31803 | 203.3405
16.9861 | 2018-11-30 15:40 | 0.32585 | 187.583
16.9931 | 2018-11-30 15:50 | 0.25267 | 173.4094
17 | 2018-11-30 16:00 | 0.20506 | 178.6028
17.0069 | 2018-11-30 16:10 | 0.20506 | 178.6028
17.0139 | 2018-11-30 16:20 | 0.15893 | 195.6978
17.0208 | 2018-11-30 16:30 | 0.083241 | 141.3402
17.0278 | 2018-11-30 16:40 | 0.073 | 0
17.0347 | 2018-11-30 16:50 | 0.12215 | 39.6855
17.0417 | 2018-11-30 17:00 | 0.28132 | 27.2937
17.0486 | 2018-11-30 17:10 | 0.28132 | 27.2937
17.0556 | 2018-11-30 17:20 | 0.31054 | 18.2016
17.0625 | 2018-11-30 17:30 | 0.42804 | 25.6072
17.0694 | 2018-11-30 17:40 | 0.47487 | 12.2802
17.0764 | 2018-11-30 17:50 | 0.43342 | 357.4875
17.0833 | 2018-11-30 18:00 | 0.5022 | 5.37
17.0903 | 2018-11-30 18:10 | 0.5022 | 5.37
17.0972 | 2018-11-30 18:20 | 0.54533 | 1.9967
17.1042 | 2018-11-30 18:30 | 0.60647 | 9.5866
17.1111 | 2018-11-30 18:40 | 0.59536 | 5.1073
17.1181 | 2018-11-30 18:50 | 0.61318 | 22.1311
17.125 | 2018-11-30 19:00 | 0.63625 | 1.6211
17.1319 | 2018-11-30 19:10 | 0.63625 | 1.6211
17.1389 | 2018-11-30 19:20 | 0.70172 | 10.9256
17.1458 | 2018-11-30 19:30 | 0.66237 | 9.6472
17.1528 | 2018-11-30 19:40 | 0.59227 | 6.885
17.1597 | 2018-11-30 19:50 | 0.57272 | 15.0796
17.1667 | 2018-11-30 20:00 | 0.50024 | 12.7027
17.1736 | 2018-11-30 20:10 | 0.50024 | 12.7027
17.1806 | 2018-11-30 20:20 | 0.44021 | 17.8587
17.1875 | 2018-11-30 20:30 | 0.37337 | 4.9166
17.1944 | 2018-11-30 20:40 | 0.42692 | 16.1851
17.2014 | 2018-11-30 20:50 | 0.4634 | 6.941
17.2083 | 2018-11-30 21:00 | 0.41181 | 6.6936
17.2153 | 2018-11-30 21:10 | 0.41181 | 6.6936
17.2222 | 2018-11-30 21:20 | 0.4199 | 11.8184
17.2292 | 2018-11-30 21:30 | 0.19967 | 20.5225
17.2361 | 2018-11-30 21:40 | 0.27638 | 10.2121
17.2431 | 2018-11-30 21:50 | 0.30911 | 349.5625
17.25 | 2018-11-30 22:00 | 0.24175 | 353.1102
17.2569 | 2018-11-30 22:10 | 0.24175 | 353.1102
17.2639 | 2018-11-30 22:20 | 0.12855 | 346.5043
17.2708 | 2018-11-30 22:30 | 0.11732 | 341.1017
17.2778 | 2018-11-30 22:40 | 0.13277 | 309.8056
17.2847 | 2018-11-30 22:50 | 0.10956 | 201.413
17.2917 | 2018-11-30 23:00 | 0.074847 | 202.7965
17.2986 | 2018-11-30 23:10 | 0.074847 | 202.7965
17.3056 | 2018-11-30 23:20 | 0.19234 | 224.5787
17.3125 | 2018-11-30 23:30 | 0.24601 | 213.5609
17.3194 | 2018-11-30 23:40 | 0.29887 | 197.5256
17.3264 | 2018-11-30 23:50 | 0.31133 | 200.2976
17.3333 | 2018-12-01 | 0.3545 | 198.0772
17.3403 | 2018-12-01 00:10 | 0.3545 | 198.0772
17.3472 | 2018-12-01 00:20 | 0.49716 | 191.6038
17.3542 | 2018-12-01 00:30 | 0.47718 | 200.4858
17.3611 | 2018-12-01 00:40 | 0.53974 | 192.9548
17.3681 | 2018-12-01 00:50 | 0.432 | 196.1276
17.375 | 2018-12-01 01:00 | 0.44949 | 192.9851
17.3819 | 2018-12-01 01:10 | 0.44949 | 192.9851
17.3889 | 2018-12-01 01:20 | 0.57048 | 198.1809
17.3958 | 2018-12-01 01:30 | 0.59175 | 190.4174
17.4028 | 2018-12-01 01:40 | 0.57674 | 189.985
17.4097 | 2018-12-01 01:50 | 0.59878 | 187.9677
17.4167 | 2018-12-01 02:00 | 0.6499 | 195.2551
17.4236 | 2018-12-01 02:10 | 0.6499 | 195.2551
17.4306 | 2018-12-01 02:20 | 0.60563 | 197.687
17.4375 | 2018-12-01 02:30 | 0.50884 | 190.0732
17.4444 | 2018-12-01 02:40 | 0.59279 | 184.4506
17.4514 | 2018-12-01 02:50 | 0.50545 | 194.2012
17.4583 | 2018-12-01 03:00 | 0.49257 | 190.0551
17.4653 | 2018-12-01 03:10 | 0.49257 | 190.0551
17.4722 | 2018-12-01 03:20 | 0.46441 | 191.5519
17.4792 | 2018-12-01 03:30 | 0.42221 | 187.0745
17.4861 | 2018-12-01 03:40 | 0.44745 | 184.6148
17.4931 | 2018-12-01 03:50 | 0.36576 | 191.0334
17.5 | 2018-12-01 04:00 | 0.30088 | 184.3841
17.5069 | 2018-12-01 04:10 | 0.30088 | 184.3841
17.5139 | 2018-12-01 04:20 | 0.26658 | 187.9781
17.5208 | 2018-12-01 04:30 | 0.25707 | 178.6626
17.5278 | 2018-12-01 04:40 | 0.20906 | 185.7651
17.5347 | 2018-12-01 04:50 | 0.11413 | 188.0591
17.5417 | 2018-12-01 05:00 | 0.10778 | 152.9595
17.5486 | 2018-12-01 05:10 | 0.10778 | 152.9595
17.5556 | 2018-12-01 05:20 | 0.10791 | 32.5119
17.5625 | 2018-12-01 05:30 | 0.19454 | 26.565
17.5694 | 2018-12-01 05:40 | 0.29193 | 22.3481
17.5764 | 2018-12-01 05:50 | 0.27238 | 29.9536
17.5833 | 2018-12-01 06:00 | 0.38694 | 25.2405
17.5903 | 2018-12-01 06:10 | 0.38694 | 25.2405
17.5972 | 2018-12-01 06:20 | 0.46084 | 17.2947
17.6042 | 2018-12-01 06:30 | 0.5279 | 9.9262
17.6111 | 2018-12-01 06:40 | 0.55733 | 9.9187
17.6181 | 2018-12-01 06:50 | 0.63036 | 15.6457
17.625 | 2018-12-01 07:00 | 0.63684 | 10.5865
17.6319 | 2018-12-01 07:10 | 0.63684 | 10.5865
17.6389 | 2018-12-01 07:20 | 0.86057 | 11.5972
17.6458 | 2018-12-01 07:30 | 0.73212 | 10.8648
17.6528 | 2018-12-01 07:40 | 0.64796 | 7.0921
17.6597 | 2018-12-01 07:50 | 0.91515 | 12.0467
17.6667 | 2018-12-01 08:00 | 0.72551 | 7.6834
17.6736 | 2018-12-01 08:10 | 0.72551 | 7.6834
17.6806 | 2018-12-01 08:20 | 0.7418 | 12.2188
17.6875 | 2018-12-01 08:30 | 0.63625 | 15.8712
17.6944 | 2018-12-01 08:40 | 0.59566 | 2.6943
17.7014 | 2018-12-01 08:50 | 0.61854 | 5.1944
17.7083 | 2018-12-01 09:00 | 0.52912 | 11.225
17.7153 | 2018-12-01 09:10 | 0.52912 | 11.225
17.7222 | 2018-12-01 09:20 | 0.60156 | 12.1879
17.7292 | 2018-12-01 09:30 | 0.58758 | 4.1968
17.7361 | 2018-12-01 09:40 | 0.40625 | 10.0652
17.7431 | 2018-12-01 09:50 | 0.46194 | 6.4635
17.75 | 2018-12-01 10:00 | 0.59103 | 12.5078
17.7569 | 2018-12-01 10:10 | 0.59103 | 12.5078
17.7639 | 2018-12-01 10:20 | 0.33355 | 15.1195
17.7708 | 2018-12-01 10:30 | 0.39785 | 9.8411
17.7778 | 2018-12-01 10:40 | 0.49679 | 13.0292
17.7847 | 2018-12-01 10:50 | 0.42953 | 12.0948
17.7917 | 2018-12-01 11:00 | 0.32156 | 16.0678
17.7986 | 2018-12-01 11:10 | 0.32156 | 16.0678
17.8056 | 2018-12-01 11:20 | 0.2244 | 353.6034
17.8125 | 2018-12-01 11:30 | 0.16858 | 14.7782
17.8194 | 2018-12-01 11:40 | 0.090355 | 5.0796
17.8264 | 2018-12-01 11:50 | 0.13823 | 356.6822
17.8333 | 2018-12-01 12:00 | 0.14239 | 29.4454
17.8403 | 2018-12-01 12:10 | 0.14239 | 29.4454
17.8472 | 2018-12-01 12:20 | 0.01077 | 21.8014
17.8542 | 2018-12-01 12:30 | 0.031241 | 219.8056
17.8611 | 2018-12-01 12:40 | 0.22079 | 197.1218
17.8681 | 2018-12-01 12:50 | 0.20938 | 186.5819
17.875 | 2018-12-01 13:00 | 0.25537 | 211.387
17.8819 | 2018-12-01 13:10 | 0.25537 | 211.387
17.8889 | 2018-12-01 13:20 | 0.43466 | 186.3402
17.8958 | 2018-12-01 13:30 | 0.37138 | 186.4935
17.9028 | 2018-12-01 13:40 | 0.42238 | 182.4424
17.9097 | 2018-12-01 13:50 | 0.42706 | 186.8588
17.9167 | 2018-12-01 14:00 | 0.45032 | 188.8139
17.9236 | 2018-12-01 14:10 | 0.45032 | 188.8139
17.9306 | 2018-12-01 14:20 | 0.38953 | 190.5022
17.9375 | 2018-12-01 14:30 | 0.41668 | 194.1696
17.9444 | 2018-12-01 14:40 | 0.42186 | 183.6695
17.9514 | 2018-12-01 14:50 | 0.41309 | 184.1647
17.9583 | 2018-12-01 15:00 | 0.4251 | 178.7869
17.9653 | 2018-12-01 15:10 | 0.4251 | 178.7869
17.9722 | 2018-12-01 15:20 | 0.35327 | 186.5014
17.9792 | 2018-12-01 15:30 | 0.45869 | 189.0311
17.9861 | 2018-12-01 15:40 | 0.42187 | 187.7652
17.9931 | 2018-12-01 15:50 | 0.44722 | 184.2317
18 | 2018-12-01 16:00 | 0.36242 | 197.835
18.0069 | 2018-12-01 16:10 | 0.36242 | 197.835
18.0139 | 2018-12-01 16:20 | 0.40206 | 190.751
18.0208 | 2018-12-01 16:30 | 0.29812 | 194.9686
18.0278 | 2018-12-01 16:40 | 0.35331 | 188.9558
18.0347 | 2018-12-01 16:50 | 0.24958 | 176.0943
18.0417 | 2018-12-01 17:00 | 0.22277 | 207.8304
18.0486 | 2018-12-01 17:10 | 0.22277 | 207.8304
18.0556 | 2018-12-01 17:20 | 0.17908 | 159.7435
18.0625 | 2018-12-01 17:30 | 0.087 | 180
18.0694 | 2018-12-01 17:40 | 0.064815 | 141.8924
18.0764 | 2018-12-01 17:50 | 0.011045 | 84.8056
18.0833 | 2018-12-01 18:00 | 0.1607 | 51.0618
18.0903 | 2018-12-01 18:10 | 0.1607 | 51.0618
18.0972 | 2018-12-01 18:20 | 0.1734 | 52.7336
18.1042 | 2018-12-01 18:30 | 0.32465 | 30.7519
18.1111 | 2018-12-01 18:40 | 0.29979 | 18.6767
18.1181 | 2018-12-01 18:50 | 0.41412 | 21.2362
18.125 | 2018-12-01 19:00 | 0.41522 | 13.9358
18.1319 | 2018-12-01 19:10 | 0.41522 | 13.9358
18.1389 | 2018-12-01 19:20 | 0.43765 | 10.0004
18.1458 | 2018-12-01 19:30 | 0.46836 | 6.8671
18.1528 | 2018-12-01 19:40 | 0.53922 | 13.1858
18.1597 | 2018-12-01 19:50 | 0.39146 | 2.782
18.1667 | 2018-12-01 20:00 | 0.54906 | 0.83485
18.1736 | 2018-12-01 20:10 | 0.54906 | 0.83485
18.1806 | 2018-12-01 20:20 | 0.70717 | 15.3333
18.1875 | 2018-12-01 20:30 | 0.65414 | 5.6147
18.1944 | 2018-12-01 20:40 | 0.66825 | 14.8265
18.2014 | 2018-12-01 20:50 | 0.63808 | 6.479
18.2083 | 2018-12-01 21:00 | 0.61258 | 4.1189
18.2153 | 2018-12-01 21:10 | 0.61258 | 4.1189
18.2222 | 2018-12-01 21:20 | 0.56816 | 15.3082
18.2292 | 2018-12-01 21:30 | 0.55483 | 15.3638
18.2361 | 2018-12-01 21:40 | 0.51655 | 9.8088
18.2431 | 2018-12-01 21:50 | 0.61172 | 10.7405
18.25 | 2018-12-01 22:00 | 0.49005 | 12.7317
18.2569 | 2018-12-01 22:10 | 0.49005 | 12.7317
18.2639 | 2018-12-01 22:20 | 0.62617 | 12.638
18.2708 | 2018-12-01 22:30 | 0.42336 | 15.4807
18.2778 | 2018-12-01 22:40 | 0.28079 | 4.2892
18.2847 | 2018-12-01 22:50 | 0.34624 | 2.1517
18.2917 | 2018-12-01 23:00 | 0.26184 | 4.6001
18.2986 | 2018-12-01 23:10 | 0.26184 | 4.6001
18.3056 | 2018-12-01 23:20 | 0.20712 | 1.9368
18.3125 | 2018-12-01 23:30 | 0.20883 | 13.5704
18.3194 | 2018-12-01 23:40 | 0.093941 | 348.3312
18.3264 | 2018-12-01 23:50 | 0.022561 | 12.8043
18.3333 | 2018-12-02 | 0.027295 | 351.573
18.3403 | 2018-12-02 00:10 | 0.027295 | 351.573
18.3472 | 2018-12-02 00:20 | 0.13396 | 235.9541
18.3542 | 2018-12-02 00:30 | 0.12258 | 191.7683
18.3611 | 2018-12-02 00:40 | 0.10907 | 182.1017
18.3681 | 2018-12-02 00:50 | 0.27017 | 205.4269
18.375 | 2018-12-02 01:00 | 0.33014 | 198.5447
18.3819 | 2018-12-02 01:10 | 0.33014 | 198.5447
18.3889 | 2018-12-02 01:20 | 0.32747 | 193.0602
18.3958 | 2018-12-02 01:30 | 0.43977 | 202.5998
18.4028 | 2018-12-02 01:40 | 0.4778 | 192.2036
18.4097 | 2018-12-02 01:50 | 0.46598 | 195.0502
18.4167 | 2018-12-02 02:00 | 0.50799 | 188.0344
18.4236 | 2018-12-02 02:10 | 0.50799 | 188.0344
18.4306 | 2018-12-02 02:20 | 0.6084 | 185.0921
18.4375 | 2018-12-02 02:30 | 0.58266 | 187.991
18.4444 | 2018-12-02 02:40 | 0.45834 | 184.3795
18.4514 | 2018-12-02 02:50 | 0.67013 | 191.3602
18.4583 | 2018-12-02 03:00 | 0.60137 | 182.0012
18.4653 | 2018-12-02 03:10 | 0.60137 | 182.0012
18.4722 | 2018-12-02 03:20 | 0.62816 | 191.292
18.4792 | 2018-12-02 03:30 | 0.65911 | 195.217
18.4861 | 2018-12-02 03:40 | 0.5234 | 188.2385
18.4931 | 2018-12-02 03:50 | 0.56663 | 190.5762
18.5 | 2018-12-02 04:00 | 0.60024 | 181.6229
18.5069 | 2018-12-02 04:10 | 0.60024 | 181.6229
18.5139 | 2018-12-02 04:20 | 0.49418 | 186.5066
18.5208 | 2018-12-02 04:30 | 0.40721 | 181.8295
18.5278 | 2018-12-02 04:40 | 0.45266 | 186.2144
18.5347 | 2018-12-02 04:50 | 0.43572 | 183.2892
18.5417 | 2018-12-02 05:00 | 0.44888 | 174.7594
18.5486 | 2018-12-02 05:10 | 0.44888 | 174.7594
18.5556 | 2018-12-02 05:20 | 0.27105 | 181.057
18.5625 | 2018-12-02 05:30 | 0.33 | 180
18.5694 | 2018-12-02 05:40 | 0.24726 | 189.3099
18.5764 | 2018-12-02 05:50 | 0.24285 | 192.6056
18.5833 | 2018-12-02 06:00 | 0.1455 | 162.8104
18.5903 | 2018-12-02 06:10 | 0.1455 | 162.8104
18.5972 | 2018-12-02 06:20 | 0.062626 | 109.5923
18.6042 | 2018-12-02 06:30 | 0.17996 | 48.6044
18.6111 | 2018-12-02 06:40 | 0.18886 | 24.3937
18.6181 | 2018-12-02 06:50 | 0.23338 | 11.1173
18.625 | 2018-12-02 07:00 | 0.36689 | 28.3113
18.6319 | 2018-12-02 07:10 | 0.36689 | 28.3113
18.6389 | 2018-12-02 07:20 | 0.42547 | 2.6943
18.6458 | 2018-12-02 07:30 | 0.47225 | 15.9787
18.6528 | 2018-12-02 07:40 | 0.57271 | 10.5643
18.6597 | 2018-12-02 07:50 | 0.68618 | 5.5195
18.6667 | 2018-12-02 08:00 | 0.70777 | 5.92
18.6736 | 2018-12-02 08:10 | 0.70777 | 5.92
18.6806 | 2018-12-02 08:20 | 0.70388 | 8.5791
18.6875 | 2018-12-02 08:30 | 0.65863 | 6.8013
18.6944 | 2018-12-02 08:40 | 0.80937 | 12.5595
18.7014 | 2018-12-02 08:50 | 0.74688 | 9.7902
18.7083 | 2018-12-02 09:00 | 0.739 | 8.9525
18.7153 | 2018-12-02 09:10 | 0.739 | 8.9525
18.7222 | 2018-12-02 09:20 | 0.78502 | 15.8953
18.7292 | 2018-12-02 09:30 | 0.67759 | 12.7031
18.7361 | 2018-12-02 09:40 | 0.75261 | 15.5689
18.7431 | 2018-12-02 09:50 | 0.54221 | 7.9508
18.75 | 2018-12-02 10:00 | 0.49541 | 8.4736
18.7569 | 2018-12-02 10:10 | 0.49541 | 8.4736
18.7639 | 2018-12-02 10:20 | 0.66799 | 10.8726
18.7708 | 2018-12-02 10:30 | 0.51466 | 14.1713
18.7778 | 2018-12-02 10:40 | 0.60025 | 10.0743
18.7847 | 2018-12-02 10:50 | 0.53274 | 6.7915
18.7917 | 2018-12-02 11:00 | 0.58167 | 8.0047
18.7986 | 2018-12-02 11:10 | 0.58167 | 8.0047
18.8056 | 2018-12-02 11:20 | 0.53346 | 10.8044
18.8125 | 2018-12-02 11:30 | 0.414 | 0.27679
18.8194 | 2018-12-02 11:40 | 0.43748 | 9.0748
18.8264 | 2018-12-02 11:50 | 0.446 | 0
18.8333 | 2018-12-02 12:00 | 0.32225 | 6.7722
18.8403 | 2018-12-02 12:10 | 0.32225 | 6.7722
18.8472 | 2018-12-02 12:20 | 0.27005 | 1.0609
18.8542 | 2018-12-02 12:30 | 0.26049 | 3.5215
18.8611 | 2018-12-02 12:40 | 0.25533 | 2.9184
18.8681 | 2018-12-02 12:50 | 0.23311 | 346.858
18.875 | 2018-12-02 13:00 | 0.11002 | 334.1336
18.8819 | 2018-12-02 13:10 | 0.11002 | 334.1336
18.8889 | 2018-12-02 13:20 | 0.018868 | 212.0054
18.8958 | 2018-12-02 13:30 | 0.086023 | 252.4076
18.9028 | 2018-12-02 13:40 | 0.14353 | 230.6544
18.9097 | 2018-12-02 13:50 | 0.21883 | 210.7841
18.9167 | 2018-12-02 14:00 | 0.37415 | 213.775
18.9236 | 2018-12-02 14:10 | 0.37415 | 213.775
18.9306 | 2018-12-02 14:20 | 0.35243 | 205.9107
18.9375 | 2018-12-02 14:30 | 0.39971 | 198.5256
18.9444 | 2018-12-02 14:40 | 0.40691 | 188.9067
18.9514 | 2018-12-02 14:50 | 0.47755 | 194.1817
18.9583 | 2018-12-02 15:00 | 0.45985 | 194.0967
18.9653 | 2018-12-02 15:10 | 0.45985 | 194.0967
18.9722 | 2018-12-02 15:20 | 0.57802 | 185.8585
18.9792 | 2018-12-02 15:30 | 0.50654 | 192.7742
18.9861 | 2018-12-02 15:40 | 0.5432 | 189.9652
18.9931 | 2018-12-02 15:50 | 0.56522 | 190.9123
19 | 2018-12-02 16:00 | 0.55068 | 192.7997
19.0069 | 2018-12-02 16:10 | 0.55068 | 192.7997
19.0139 | 2018-12-02 16:20 | 0.64083 | 189.5211
19.0208 | 2018-12-02 16:30 | 0.52853 | 186.6275
19.0278 | 2018-12-02 16:40 | 0.63936 | 190.8178
19.0347 | 2018-12-02 16:50 | 0.58107 | 184.8373
19.0417 | 2018-12-02 17:00 | 0.57578 | 187.3842
19.0486 | 2018-12-02 17:10 | 0.57578 | 187.3842
19.0556 | 2018-12-02 17:20 | 0.58502 | 191.1371
19.0625 | 2018-12-02 17:30 | 0.50462 | 191.7776
19.0694 | 2018-12-02 17:40 | 0.36244 | 186.6544
19.0764 | 2018-12-02 17:50 | 0.43052 | 204.4219
19.0833 | 2018-12-02 18:00 | 0.37402 | 193.2932
19.0903 | 2018-12-02 18:10 | 0.37402 | 193.2932
19.0972 | 2018-12-02 18:20 | 0.34814 | 181.646
19.1042 | 2018-12-02 18:30 | 0.2567 | 184.2446
19.1111 | 2018-12-02 18:40 | 0.16907 | 173.5475
19.1181 | 2018-12-02 18:50 | 0.13906 | 181.6483
19.125 | 2018-12-02 19:00 | 0.043081 | 158.1986
19.1319 | 2018-12-02 19:10 | 0.043081 | 158.1986
19.1389 | 2018-12-02 19:20 | 0.12042 | 41.6335
19.1458 | 2018-12-02 19:30 | 0.18569 | 7.7374
19.1528 | 2018-12-02 19:40 | 0.24071 | 28.2685
19.1597 | 2018-12-02 19:50 | 0.32517 | 19.7723
19.1667 | 2018-12-02 20:00 | 0.37443 | 2.7554
19.1736 | 2018-12-02 20:10 | 0.37443 | 2.7554
19.1806 | 2018-12-02 20:20 | 0.47347 | 2.5421
19.1875 | 2018-12-02 20:30 | 0.52621 | 6.3282
19.1944 | 2018-12-02 20:40 | 0.57082 | 7.4487
19.2014 | 2018-12-02 20:50 | 0.48442 | 4.3806
19.2083 | 2018-12-02 21:00 | 0.54027 | 3.9269
19.2153 | 2018-12-02 21:10 | 0.54027 | 3.9269
19.2222 | 2018-12-02 21:20 | 0.6553 | 9.6636
19.2292 | 2018-12-02 21:30 | 0.67727 | 15.0622
19.2361 | 2018-12-02 21:40 | 0.55115 | 358.6484
19.2431 | 2018-12-02 21:50 | 0.66199 | 13.0076
19.25 | 2018-12-02 22:00 | 0.65556 | 12.5099
19.2569 | 2018-12-02 22:10 | 0.65556 | 12.5099
19.2639 | 2018-12-02 22:20 | 0.68583 | 4.1809
19.2708 | 2018-12-02 22:30 | 0.64776 | 12.6631
19.2778 | 2018-12-02 22:40 | 0.67477 | 14.5923
19.2847 | 2018-12-02 22:50 | 0.63966 | 2.5985
19.2917 | 2018-12-02 23:00 | 0.70134 | 10.7652
19.2986 | 2018-12-02 23:10 | 0.70134 | 10.7652
19.3056 | 2018-12-02 23:20 | 0.49701 | 7.2823
19.3125 | 2018-12-02 23:30 | 0.54695 | 13.4265
19.3194 | 2018-12-02 23:40 | 0.52046 | 355.7026
19.3264 | 2018-12-02 23:50 | 0.45255 | 8.1301
19.3333 | 2018-12-03 | 0.49617 | 9.0447
19.3403 | 2018-12-03 00:10 | 0.49617 | 9.0447
19.3472 | 2018-12-03 00:20 | 0.29233 | 8.6568
19.3542 | 2018-12-03 00:30 | 0.21737 | 8.4656
19.3611 | 2018-12-03 00:40 | 0.33003 | 4.5185
19.3681 | 2018-12-03 00:50 | 0.30401 | 16.8256
19.375 | 2018-12-03 01:00 | 0.14641 | 23.7638
19.3819 | 2018-12-03 01:10 | 0.14641 | 23.7638
19.3889 | 2018-12-03 01:20 | 0.066648 | 332.2815
19.3958 | 2018-12-03 01:30 | 0.033941 | 315
19.4028 | 2018-12-03 01:40 | 0.047885 | 241.2941
19.4097 | 2018-12-03 01:50 | 0.071589 | 241.645
19.4167 | 2018-12-03 02:00 | 0.15708 | 204.444
19.4236 | 2018-12-03 02:10 | 0.15708 | 204.444
19.4306 | 2018-12-03 02:20 | 0.23114 | 218.8534
19.4375 | 2018-12-03 02:30 | 0.33629 | 203.6684
19.4444 | 2018-12-03 02:40 | 0.38347 | 193.4202
19.4514 | 2018-12-03 02:50 | 0.39312 | 199.3107
19.4583 | 2018-12-03 03:00 | 0.39396 | 196.3649
19.4653 | 2018-12-03 03:10 | 0.39396 | 196.3649
19.4722 | 2018-12-03 03:20 | 0.4753 | 190.0569
19.4792 | 2018-12-03 03:30 | 0.59472 | 196.9115
19.4861 | 2018-12-03 03:40 | 0.5505 | 186.4666
19.4931 | 2018-12-03 03:50 | 0.57065 | 189.9905
19.5 | 2018-12-03 04:00 | 0.58921 | 189.5742
19.5069 | 2018-12-03 04:10 | 0.58921 | 189.5742
19.5139 | 2018-12-03 04:20 | 0.54139 | 193.2405
19.5208 | 2018-12-03 04:30 | 0.58658 | 195.2209
19.5278 | 2018-12-03 04:40 | 0.554 | 184.8667
19.5347 | 2018-12-03 04:50 | 0.5399 | 189.8113
19.5417 | 2018-12-03 05:00 | 0.60189 | 188.0224
19.5486 | 2018-12-03 05:10 | 0.60189 | 188.0224
19.5556 | 2018-12-03 05:20 | 0.58874 | 191.4626
19.5625 | 2018-12-03 05:30 | 0.5467 | 202.249
19.5694 | 2018-12-03 05:40 | 0.42941 | 187.2243
19.5764 | 2018-12-03 05:50 | 0.46957 | 190.3048
19.5833 | 2018-12-03 06:00 | 0.55287 | 183.2143
19.5903 | 2018-12-03 06:10 | 0.55287 | 183.2143
19.5972 | 2018-12-03 06:20 | 0.37944 | 187.7244
19.6042 | 2018-12-03 06:30 | 0.37237 | 187.7167
19.6111 | 2018-12-03 06:40 | 0.2813 | 182.6488
19.6181 | 2018-12-03 06:50 | 0.28588 | 197.9279
19.625 | 2018-12-03 07:00 | 0.20409 | 178.3153
19.6319 | 2018-12-03 07:10 | 0.20409 | 178.3153
19.6389 | 2018-12-03 07:20 | 0.039395 | 203.9625
19.6458 | 2018-12-03 07:30 | 0.046519 | 64.5366
19.6528 | 2018-12-03 07:40 | 0.15789 | 27.5388
19.6597 | 2018-12-03 07:50 | 0.24242 | 34.4111
19.6667 | 2018-12-03 08:00 | 0.26633 | 24.1591
19.6736 | 2018-12-03 08:10 | 0.26633 | 24.1591
19.6806 | 2018-12-03 08:20 | 0.48175 | 20.918
19.6875 | 2018-12-03 08:30 | 0.45667 | 4.8991
19.6944 | 2018-12-03 08:40 | 0.5205 | 9.0642
19.7014 | 2018-12-03 08:50 | 0.60321 | 8.8689
19.7083 | 2018-12-03 09:00 | 0.66436 | 6.5688
19.7153 | 2018-12-03 09:10 | 0.66436 | 6.5688
19.7222 | 2018-12-03 09:20 | 0.67672 | 10.214
19.7292 | 2018-12-03 09:30 | 0.61465 | 4.1985
19.7361 | 2018-12-03 09:40 | 0.63914 | 11.1869
19.7431 | 2018-12-03 09:50 | 0.61896 | 16.3269
19.75 | 2018-12-03 10:00 | 0.8371 | 10.5314
19.7569 | 2018-12-03 10:10 | 0.8371 | 10.5314
19.7639 | 2018-12-03 10:20 | 0.7032 | 5.4674
19.7708 | 2018-12-03 10:30 | 0.68155 | 3.87
19.7778 | 2018-12-03 10:40 | 0.69646 | 7.176
19.7847 | 2018-12-03 10:50 | 0.61502 | 9.2632
19.7917 | 2018-12-03 11:00 | 0.64476 | 7.6651
19.7986 | 2018-12-03 11:10 | 0.64476 | 7.6651
19.8056 | 2018-12-03 11:20 | 0.60719 | 15.1806
19.8125 | 2018-12-03 11:30 | 0.60149 | 13.8514
19.8194 | 2018-12-03 11:40 | 0.58365 | 10.9634
19.8264 | 2018-12-03 11:50 | 0.64202 | 10.1372
19.8333 | 2018-12-03 12:00 | 0.61664 | 4.1849
19.8403 | 2018-12-03 12:10 | 0.61664 | 4.1849
19.8472 | 2018-12-03 12:20 | 0.40013 | 12.2648
19.8542 | 2018-12-03 12:30 | 0.41871 | 11.0147
19.8611 | 2018-12-03 12:40 | 0.4316 | 15.453
19.8681 | 2018-12-03 12:50 | 0.44165 | 3.1151
19.875 | 2018-12-03 13:00 | 0.42106 | 11.2299
19.8819 | 2018-12-03 13:10 | 0.42106 | 11.2299
19.8889 | 2018-12-03 13:20 | 0.22206 | 1.2902
19.8958 | 2018-12-03 13:30 | 0.33044 | 357.051
19.9028 | 2018-12-03 13:40 | 0.16325 | 356.8396
19.9097 | 2018-12-03 13:50 | 0.16447 | 340.4633
19.9167 | 2018-12-03 14:00 | 0.064281 | 5.3558
19.9236 | 2018-12-03 14:10 | 0.064281 | 5.3558
19.9306 | 2018-12-03 14:20 | 0.095341 | 245.8545
19.9375 | 2018-12-03 14:30 | 0.2324 | 230.7626
19.9444 | 2018-12-03 14:40 | 0.21652 | 205.1448
19.9514 | 2018-12-03 14:50 | 0.26229 | 200.3004
19.9583 | 2018-12-03 15:00 | 0.35319 | 195.0986
19.9653 | 2018-12-03 15:10 | 0.35319 | 195.0986
19.9722 | 2018-12-03 15:20 | 0.45569 | 204.0901
19.9792 | 2018-12-03 15:30 | 0.54502 | 201.5281
19.9861 | 2018-12-03 15:40 | 0.59412 | 195.3228
19.9931 | 2018-12-03 15:50 | 0.67683 | 190.7289
20 | 2018-12-03 16:00 | 0.53168 | 189.0903
20.0069 | 2018-12-03 16:10 | 0.53168 | 189.0903
20.0139 | 2018-12-03 16:20 | 0.72174 | 188.9272
20.0208 | 2018-12-03 16:30 | 0.65043 | 190.2733
20.0278 | 2018-12-03 16:40 | 0.73852 | 194.1868
20.0347 | 2018-12-03 16:50 | 0.71275 | 192.0667
20.0417 | 2018-12-03 17:00 | 0.67427 | 191.8099
20.0486 | 2018-12-03 17:10 | 0.67427 | 191.8099
20.0556 | 2018-12-03 17:20 | 0.73132 | 193.2001
20.0625 | 2018-12-03 17:30 | 0.76783 | 192.715
20.0694 | 2018-12-03 17:40 | 0.78393 | 187.6236
20.0764 | 2018-12-03 17:50 | 0.69385 | 186.0393
20.0833 | 2018-12-03 18:00 | 0.73869 | 188.7992
20.0903 | 2018-12-03 18:10 | 0.73869 | 188.7992
20.0972 | 2018-12-03 18:20 | 0.687 | 191.1627
20.1042 | 2018-12-03 18:30 | 0.57096 | 189.5778
20.1111 | 2018-12-03 18:40 | 0.64773 | 187.6297
20.1181 | 2018-12-03 18:50 | 0.57467 | 192.9722
20.125 | 2018-12-03 19:00 | 0.47752 | 185.8897
20.1319 | 2018-12-03 19:10 | 0.47752 | 185.8897
20.1389 | 2018-12-03 19:20 | 0.34504 | 179.1697
20.1458 | 2018-12-03 19:30 | 0.41251 | 190.193
20.1528 | 2018-12-03 19:40 | 0.43276 | 185.1705
20.1597 | 2018-12-03 19:50 | 0.18469 | 184.9697
20.1667 | 2018-12-03 20:00 | 0.17141 | 160.9308
20.1736 | 2018-12-03 20:10 | 0.17141 | 160.9308
20.1806 | 2018-12-03 20:20 | 0.041049 | 55.9228
20.1875 | 2018-12-03 20:30 | 0.04998 | 109.8852
20.1944 | 2018-12-03 20:40 | 0.22275 | 25.5297
20.2014 | 2018-12-03 20:50 | 0.24573 | 11.2642
20.2083 | 2018-12-03 21:00 | 0.37541 | 15.9244
20.2153 | 2018-12-03 21:10 | 0.37541 | 15.9244
20.2222 | 2018-12-03 21:20 | 0.47371 | 13.3028
20.2292 | 2018-12-03 21:30 | 0.47321 | 15.9454
20.2361 | 2018-12-03 21:40 | 0.50265 | 11.2429
20.2431 | 2018-12-03 21:50 | 0.54244 | 6.4568
20.25 | 2018-12-03 22:00 | 0.56739 | 7.9016
20.2569 | 2018-12-03 22:10 | 0.56739 | 7.9016
20.2639 | 2018-12-03 22:20 | 0.69893 | 351.3598
20.2708 | 2018-12-03 22:30 | 0.59391 | 6.5746
20.2778 | 2018-12-03 22:40 | 0.6323 | 11.772
20.2847 | 2018-12-03 22:50 | 0.79153 | 18.1832
20.2917 | 2018-12-03 23:00 | 0.78576 | 8.5632
20.2986 | 2018-12-03 23:10 | 0.78576 | 8.5632
20.3056 | 2018-12-03 23:20 | 0.61177 | 13.0367
20.3125 | 2018-12-03 23:30 | 0.66062 | 7.48
20.3194 | 2018-12-03 23:40 | 0.59247 | 5.2295
20.3264 | 2018-12-03 23:50 | 0.51633 | 8.24
20.3333 | 2018-12-04 | 0.56859 | 13.0097
20.3403 | 2018-12-04 00:10 | 0.56859 | 13.0097
20.3472 | 2018-12-04 00:20 | 0.48113 | 3.9329
20.3542 | 2018-12-04 00:30 | 0.51168 | 11.7272
20.3611 | 2018-12-04 00:40 | 0.45809 | 1.1258
20.3681 | 2018-12-04 00:50 | 0.48856 | 4.5786
20.375 | 2018-12-04 01:00 | 0.37583 | 5.6499
20.3819 | 2018-12-04 01:10 | 0.37583 | 5.6499
20.3889 | 2018-12-04 01:20 | 0.32801 | 359.476
20.3958 | 2018-12-04 01:30 | 0.37497 | 4.1292
20.4028 | 2018-12-04 01:40 | 0.3265 | 3.1604
20.4097 | 2018-12-04 01:50 | 0.21896 | 16.4486
20.4167 | 2018-12-04 02:00 | 0.14239 | 10.5208
20.4236 | 2018-12-04 02:10 | 0.14239 | 10.5208
20.4306 | 2018-12-04 02:20 | 0.14819 | 338.6294
20.4375 | 2018-12-04 02:30 | 0.047885 | 208.7059
20.4444 | 2018-12-04 02:40 | 0.098473 | 235.3416
20.4514 | 2018-12-04 02:50 | 0.1373 | 200.0188
20.4583 | 2018-12-04 03:00 | 0.2284 | 217.1709
20.4653 | 2018-12-04 03:10 | 0.2284 | 217.1709
20.4722 | 2018-12-04 03:20 | 0.3136 | 194.2135
20.4792 | 2018-12-04 03:30 | 0.36447 | 200.2249
20.4861 | 2018-12-04 03:40 | 0.39461 | 201.5587
20.4931 | 2018-12-04 03:50 | 0.47697 | 191.734
20.5 | 2018-12-04 04:00 | 0.55496 | 193.3351
20.5069 | 2018-12-04 04:10 | 0.55496 | 193.3351
20.5139 | 2018-12-04 04:20 | 0.55128 | 193.9606
20.5208 | 2018-12-04 04:30 | 0.4636 | 186.0672
20.5278 | 2018-12-04 04:40 | 0.49661 | 184.6199
20.5347 | 2018-12-04 04:50 | 0.52321 | 185.2638
20.5417 | 2018-12-04 05:00 | 0.60929 | 190.0189
20.5486 | 2018-12-04 05:10 | 0.60929 | 190.0189
20.5556 | 2018-12-04 05:20 | 0.59799 | 186.6259
20.5625 | 2018-12-04 05:30 | 0.58073 | 187.3208
20.5694 | 2018-12-04 05:40 | 0.60034 | 185.0648
20.5764 | 2018-12-04 05:50 | 0.55918 | 178.5653
20.5833 | 2018-12-04 06:00 | 0.65556 | 177.6395
20.5903 | 2018-12-04 06:10 | 0.65556 | 177.6395
20.5972 | 2018-12-04 06:20 | 0.56442 | 187.9435
20.6042 | 2018-12-04 06:30 | 0.5695 | 186.3513
20.6111 | 2018-12-04 06:40 | 0.55956 | 190.6071
20.6181 | 2018-12-04 06:50 | 0.54577 | 176.9541
20.625 | 2018-12-04 07:00 | 0.6267 | 186.2291
20.6319 | 2018-12-04 07:10 | 0.6267 | 186.2291
20.6389 | 2018-12-04 07:20 | 0.54601 | 180.4197
20.6458 | 2018-12-04 07:30 | 0.46131 | 192.1381
20.6528 | 2018-12-04 07:40 | 0.32735 | 192.1681
20.6597 | 2018-12-04 07:50 | 0.30204 | 180.9485
20.6667 | 2018-12-04 08:00 | 0.2621 | 185.2538
20.6736 | 2018-12-04 08:10 | 0.2621 | 185.2538
20.6806 | 2018-12-04 08:20 | 0.18123 | 197.3352
20.6875 | 2018-12-04 08:30 | 0.098813 | 144.0579
20.6944 | 2018-12-04 08:40 | 0.055109 | 101.5138
20.7014 | 2018-12-04 08:50 | 0.14135 | 18.5631
20.7083 | 2018-12-04 09:00 | 0.20568 | 14.6443
20.7153 | 2018-12-04 09:10 | 0.20568 | 14.6443
20.7222 | 2018-12-04 09:20 | 0.38766 | 9.8025
20.7292 | 2018-12-04 09:30 | 0.433 | 19.5648
20.7361 | 2018-12-04 09:40 | 0.47618 | 12.9856
20.7431 | 2018-12-04 09:50 | 0.57325 | 12.7998
20.75 | 2018-12-04 10:00 | 0.7176 | 11.5761
20.7569 | 2018-12-04 10:10 | 0.7176 | 11.5761
20.7639 | 2018-12-04 10:20 | 0.72652 | 12.9651
20.7708 | 2018-12-04 10:30 | 0.70654 | 13.5052
20.7778 | 2018-12-04 10:40 | 0.74614 | 12.3039
20.7847 | 2018-12-04 10:50 | 0.78604 | 11.5958
20.7917 | 2018-12-04 11:00 | 0.76919 | 11.7774
20.7986 | 2018-12-04 11:10 | 0.76919 | 11.7774
20.8056 | 2018-12-04 11:20 | 0.71934 | 12.6066
20.8125 | 2018-12-04 11:30 | 0.73926 | 14.4122
20.8194 | 2018-12-04 11:40 | 0.82521 | 12.3857
20.8264 | 2018-12-04 11:50 | 0.76277 | 10.4997
20.8333 | 2018-12-04 12:00 | 0.60569 | 5.4
20.8403 | 2018-12-04 12:10 | 0.60569 | 5.4
20.8472 | 2018-12-04 12:20 | 0.73027 | 3.3757
20.8542 | 2018-12-04 12:30 | 0.59066 | 5.4403
20.8611 | 2018-12-04 12:40 | 0.6098 | 6.4024
20.8681 | 2018-12-04 12:50 | 0.64605 | 10.6142
20.875 | 2018-12-04 13:00 | 0.4411 | 5.5943
20.8819 | 2018-12-04 13:10 | 0.4411 | 5.5943
20.8889 | 2018-12-04 13:20 | 0.53573 | 7.6158
20.8958 | 2018-12-04 13:30 | 0.49451 | 9.3099
20.9028 | 2018-12-04 13:40 | 0.44131 | 10.4442
20.9097 | 2018-12-04 13:50 | 0.3928 | 3.6491
20.9167 | 2018-12-04 14:00 | 0.35573 | 5.6465
20.9236 | 2018-12-04 14:10 | 0.35573 | 5.6465
20.9306 | 2018-12-04 14:20 | 0.21229 | 357.0298
20.9375 | 2018-12-04 14:30 | 0.20577 | 338.9225
20.9444 | 2018-12-04 14:40 | 0.17253 | 325.3889
20.9514 | 2018-12-04 14:50 | 0.17224 | 2.9953
20.9583 | 2018-12-04 15:00 | 0.0089443 | 243.435
20.9653 | 2018-12-04 15:10 | 0.0089443 | 243.435
20.9722 | 2018-12-04 15:20 | 0.10817 | 199.44
20.9792 | 2018-12-04 15:30 | 0.17217 | 186.671
20.9861 | 2018-12-04 15:40 | 0.32452 | 197.2066
20.9931 | 2018-12-04 15:50 | 0.34757 | 203.3934
21 | 2018-12-04 16:00 | 0.36473 | 199.8757
21.0069 | 2018-12-04 16:10 | 0.36473 | 199.8757
21.0139 | 2018-12-04 16:20 | 0.51655 | 189.1341
21.0208 | 2018-12-04 16:30 | 0.65623 | 185.6845
21.0278 | 2018-12-04 16:40 | 0.47725 | 189.2847
21.0347 | 2018-12-04 16:50 | 0.51637 | 187.4553
21.0417 | 2018-12-04 17:00 | 0.63013 | 194.5214
21.0486 | 2018-12-04 17:10 | 0.63013 | 194.5214
21.0556 | 2018-12-04 17:20 | 0.637 | 179.91
21.0625 | 2018-12-04 17:30 | 0.68546 | 182.0902
21.0694 | 2018-12-04 17:40 | 0.66526 | 183.5334
21.0764 | 2018-12-04 17:50 | 0.71039 | 194.0949
21.0833 | 2018-12-04 18:00 | 0.64835 | 193.2861
21.0903 | 2018-12-04 18:10 | 0.64835 | 193.2861
21.0972 | 2018-12-04 18:20 | 0.64872 | 189.4042
21.1042 | 2018-12-04 18:30 | 0.64085 | 188.9773
21.1111 | 2018-12-04 18:40 | 0.68488 | 190.6865
21.1181 | 2018-12-04 18:50 | 0.613 | 183.2731
21.125 | 2018-12-04 19:00 | 0.59424 | 191.6503
21.1319 | 2018-12-04 19:10 | 0.59424 | 191.6503
21.1389 | 2018-12-04 19:20 | 0.62618 | 185.7743
21.1458 | 2018-12-04 19:30 | 0.55255 | 200.6653
21.1528 | 2018-12-04 19:40 | 0.60101 | 180.3813
21.1597 | 2018-12-04 19:50 | 0.45444 | 185.9364
21.1667 | 2018-12-04 20:00 | 0.416 | 180.1377
21.1736 | 2018-12-04 20:10 | 0.416 | 180.1377
21.1806 | 2018-12-04 20:20 | 0.40344 | 175.1656
21.1875 | 2018-12-04 20:30 | 0.2793 | 177.3322
21.1944 | 2018-12-04 20:40 | 0.24002 | 180.7162
21.2014 | 2018-12-04 20:50 | 0.20271 | 184.8106
21.2083 | 2018-12-04 21:00 | 0.13621 | 142.4571
21.2153 | 2018-12-04 21:10 | 0.13621 | 142.4571
21.2222 | 2018-12-04 21:20 | 0.042059 | 151.607
21.2292 | 2018-12-04 21:30 | 0.1669 | 10.704
21.2361 | 2018-12-04 21:40 | 0.266 | 17.2769
21.2431 | 2018-12-04 21:50 | 0.49496 | 17.5198
21.25 | 2018-12-04 22:00 | 0.55921 | 17.2685
21.2569 | 2018-12-04 22:10 | 0.55921 | 17.2685
21.2639 | 2018-12-04 22:20 | 0.58591 | 8.1439
21.2708 | 2018-12-04 22:30 | 0.60398 | 15.8542
21.2778 | 2018-12-04 22:40 | 0.62013 | 8.0648
21.2847 | 2018-12-04 22:50 | 0.79128 | 3.2602
21.2917 | 2018-12-04 23:00 | 0.59247 | 11.291
21.2986 | 2018-12-04 23:10 | 0.59247 | 11.291
21.3056 | 2018-12-04 23:20 | 0.72512 | 6.8114
21.3125 | 2018-12-04 23:30 | 0.77801 | 10.8911
21.3194 | 2018-12-04 23:40 | 0.76636 | 16.4486
21.3264 | 2018-12-04 23:50 | 0.92493 | 7.0174
21.3333 | 2018-12-05 | 0.7854 | 6.0663
21.3403 | 2018-12-05 00:10 | 0.7854 | 6.0663
21.3472 | 2018-12-05 00:20 | 0.74222 | 6.11
21.3542 | 2018-12-05 00:30 | 0.65494 | 3.0634
21.3611 | 2018-12-05 00:40 | 0.75476 | 9.687
21.3681 | 2018-12-05 00:50 | 0.66724 | 8.4458
21.375 | 2018-12-05 01:00 | 0.61226 | 17.7839
21.3819 | 2018-12-05 01:10 | 0.61226 | 17.7839
21.3889 | 2018-12-05 01:20 | 0.55107 | 9.1888
21.3958 | 2018-12-05 01:30 | 0.50756 | 11.7084
21.4028 | 2018-12-05 01:40 | 0.52118 | 10.1672
21.4097 | 2018-12-05 01:50 | 0.42604 | 359.1931
21.4167 | 2018-12-05 02:00 | 0.34525 | 8.9985
21.4236 | 2018-12-05 02:10 | 0.34525 | 8.9985
21.4306 | 2018-12-05 02:20 | 0.30516 | 1.8779
21.4375 | 2018-12-05 02:30 | 0.23902 | 0.71916
21.4444 | 2018-12-05 02:40 | 0.1786 | 335.8746
21.4514 | 2018-12-05 02:50 | 0.24903 | 0.92034
21.4583 | 2018-12-05 03:00 | 0.090078 | 337.1355
21.4653 | 2018-12-05 03:10 | 0.090078 | 337.1355
21.4722 | 2018-12-05 03:20 | 0.063008 | 270.9094
21.4792 | 2018-12-05 03:30 | 0.058249 | 235.4915
21.4861 | 2018-12-05 03:40 | 0.19088 | 215.1887
21.4931 | 2018-12-05 03:50 | 0.2869 | 201.4677
21.5 | 2018-12-05 04:00 | 0.47363 | 205.9158
21.5069 | 2018-12-05 04:10 | 0.47363 | 205.9158
21.5139 | 2018-12-05 04:20 | 0.4218 | 194.6952
21.5208 | 2018-12-05 04:30 | 0.48335 | 190.008
21.5278 | 2018-12-05 04:40 | 0.58684 | 190.5057
21.5347 | 2018-12-05 04:50 | 0.49158 | 190.0755
21.5417 | 2018-12-05 05:00 | 0.5555 | 189.4284
21.5486 | 2018-12-05 05:10 | 0.5555 | 189.4284
21.5556 | 2018-12-05 05:20 | 0.5981 | 193.7342
21.5625 | 2018-12-05 05:30 | 0.58429 | 189.0593
21.5694 | 2018-12-05 05:40 | 0.61678 | 177.119
21.5764 | 2018-12-05 05:50 | 0.61801 | 187.999
21.5833 | 2018-12-05 06:00 | 0.68132 | 187.1667
21.5903 | 2018-12-05 06:10 | 0.68132 | 187.1667
21.5972 | 2018-12-05 06:20 | 0.6425 | 185.9857
21.6042 | 2018-12-05 06:30 | 0.61321 | 181.4951
21.6111 | 2018-12-05 06:40 | 0.567 | 180.2021
21.6181 | 2018-12-05 06:50 | 0.59957 | 189.1167
21.625 | 2018-12-05 07:00 | 0.60582 | 190.8462
21.6319 | 2018-12-05 07:10 | 0.60582 | 190.8462
21.6389 | 2018-12-05 07:20 | 0.56147 | 188.7074
21.6458 | 2018-12-05 07:30 | 0.60807 | 180.8481
21.6528 | 2018-12-05 07:40 | 0.50529 | 185.4511
21.6597 | 2018-12-05 07:50 | 0.42502 | 180.5392
21.6667 | 2018-12-05 08:00 | 0.47489 | 188.2325
21.6736 | 2018-12-05 08:10 | 0.47489 | 188.2325
21.6806 | 2018-12-05 08:20 | 0.37991 | 185.7406
21.6875 | 2018-12-05 08:30 | 0.37563 | 174.6537
21.6944 | 2018-12-05 08:40 | 0.41059 | 176.9285
21.7014 | 2018-12-05 08:50 | 0.34264 | 183.5137
21.7083 | 2018-12-05 09:00 | 0.17515 | 186.5569
21.7153 | 2018-12-05 09:10 | 0.17515 | 186.5569
21.7222 | 2018-12-05 09:20 | 0.11807 | 152.7839
21.7292 | 2018-12-05 09:30 | 0.079404 | 58.9125
21.7361 | 2018-12-05 09:40 | 0.24476 | 31.8069
21.7431 | 2018-12-05 09:50 | 0.32335 | 27.0405
21.75 | 2018-12-05 10:00 | 0.37607 | 21.0375
21.7569 | 2018-12-05 10:10 | 0.37607 | 21.0375
21.7639 | 2018-12-05 10:20 | 0.43805 | 19.4691
21.7708 | 2018-12-05 10:30 | 0.63837 | 9.8312
21.7778 | 2018-12-05 10:40 | 0.66033 | 17.7215
21.7847 | 2018-12-05 10:50 | 0.66739 | 11.0574
21.7917 | 2018-12-05 11:00 | 0.76287 | 8.7462
21.7986 | 2018-12-05 11:10 | 0.76287 | 8.7462
21.8056 | 2018-12-05 11:20 | 0.91466 | 3.4474
21.8125 | 2018-12-05 11:30 | 0.85299 | 7.3416
21.8194 | 2018-12-05 11:40 | 0.94646 | 11.3337
21.8264 | 2018-12-05 11:50 | 0.88021 | 8.2958
21.8333 | 2018-12-05 12:00 | 0.89817 | 8.1933
21.8403 | 2018-12-05 12:10 | 0.89817 | 8.1933
21.8472 | 2018-12-05 12:20 | 0.73703 | 8.9767
21.8542 | 2018-12-05 12:30 | 0.85391 | 8.2819
21.8611 | 2018-12-05 12:40 | 0.87316 | 10.6922
21.8681 | 2018-12-05 12:50 | 0.83624 | 8.5274
21.875 | 2018-12-05 13:00 | 0.79408 | 11.5505
21.8819 | 2018-12-05 13:10 | 0.79408 | 11.5505
21.8889 | 2018-12-05 13:20 | 0.71803 | 4.313
21.8958 | 2018-12-05 13:30 | 0.64122 | 10.2409
21.9028 | 2018-12-05 13:40 | 0.66215 | 14.5189
21.9097 | 2018-12-05 13:50 | 0.54775 | 11.3715
21.9167 | 2018-12-05 14:00 | 0.56148 | 14.3332
21.9236 | 2018-12-05 14:10 | 0.56148 | 14.3332
21.9306 | 2018-12-05 14:20 | 0.41627 | 9.9601
21.9375 | 2018-12-05 14:30 | 0.42262 | 353.6149
21.9444 | 2018-12-05 14:40 | 0.35697 | 12.1284
21.9514 | 2018-12-05 14:50 | 0.45407 | 9.3793
21.9583 | 2018-12-05 15:00 | 0.35983 | 7.1843
21.9653 | 2018-12-05 15:10 | 0.35983 | 7.1843
21.9722 | 2018-12-05 15:20 | 0.233 | 359.7541
21.9792 | 2018-12-05 15:30 | 0.15108 | 350.4753
21.9861 | 2018-12-05 15:40 | 0.25077 | 341.6373
21.9931 | 2018-12-05 15:50 | 0.022361 | 63.435
22 | 2018-12-05 16:00 | 0.090028 | 347.8163
22.0069 | 2018-12-05 16:10 | 0.090028 | 347.8163
22.0139 | 2018-12-05 16:20 | 0.17084 | 190.4548
22.0208 | 2018-12-05 16:30 | 0.30637 | 207.4014
22.0278 | 2018-12-05 16:40 | 0.37436 | 201.6309
22.0347 | 2018-12-05 16:50 | 0.38241 | 195.7807
22.0417 | 2018-12-05 17:00 | 0.40754 | 200.3915
22.0486 | 2018-12-05 17:10 | 0.40754 | 200.3915
22.0556 | 2018-12-05 17:20 | 0.48326 | 200.7226
22.0625 | 2018-12-05 17:30 | 0.53808 | 183.6228
22.0694 | 2018-12-05 17:40 | 0.59001 | 188.185
22.0764 | 2018-12-05 17:50 | 0.51069 | 188.5585
22.0833 | 2018-12-05 18:00 | 0.66682 | 189.8437
22.0903 | 2018-12-05 18:10 | 0.66682 | 189.8437
22.0972 | 2018-12-05 18:20 | 0.64354 | 190.3845
22.1042 | 2018-12-05 18:30 | 0.67941 | 190.5161
22.1111 | 2018-12-05 18:40 | 0.73934 | 190.0484
22.1181 | 2018-12-05 18:50 | 0.61876 | 191.655
22.125 | 2018-12-05 19:00 | 0.72689 | 193.7686
22.1319 | 2018-12-05 19:10 | 0.72689 | 193.7686
22.1389 | 2018-12-05 19:20 | 0.61934 | 192.7797
22.1458 | 2018-12-05 19:30 | 0.65409 | 186.4079
22.1528 | 2018-12-05 19:40 | 0.5536 | 195.2914
22.1597 | 2018-12-05 19:50 | 0.68569 | 185.9434
22.1667 | 2018-12-05 20:00 | 0.57914 | 187.6404
22.1736 | 2018-12-05 20:10 | 0.57914 | 187.6404
22.1806 | 2018-12-05 20:20 | 0.57573 | 188.0879
22.1875 | 2018-12-05 20:30 | 0.39802 | 185.7679
22.1944 | 2018-12-05 20:40 | 0.39845 | 184.895
22.2014 | 2018-12-05 20:50 | 0.41558 | 191.6614
22.2083 | 2018-12-05 21:00 | 0.38283 | 188.1089
22.2153 | 2018-12-05 21:10 | 0.38283 | 188.1089
22.2222 | 2018-12-05 21:20 | 0.21593 | 174.6855
22.2292 | 2018-12-05 21:30 | 0.17047 | 157.9489
22.2361 | 2018-12-05 21:40 | 0.14972 | 149.4957
22.2431 | 2018-12-05 21:50 | 0.11411 | 177.4886
22.25 | 2018-12-05 22:00 | 0.086371 | 5.3145
22.2569 | 2018-12-05 22:10 | 0.086371 | 5.3145
22.2639 | 2018-12-05 22:20 | 0.34975 | 18.3313
22.2708 | 2018-12-05 22:30 | 0.33295 | 21.8653
22.2778 | 2018-12-05 22:40 | 0.47052 | 14.2725
22.2847 | 2018-12-05 22:50 | 0.46565 | 15.8271
22.2917 | 2018-12-05 23:00 | 0.49463 | 10.7193
22.2986 | 2018-12-05 23:10 | 0.49463 | 10.7193
22.3056 | 2018-12-05 23:20 | 0.57128 | 5.1218
22.3125 | 2018-12-05 23:30 | 0.60945 | 8.9677
22.3194 | 2018-12-05 23:40 | 0.64877 | 10.9289
22.3264 | 2018-12-05 23:50 | 0.73951 | 14.4872
22.3333 | 2018-12-06 | 0.74963 | 10.5305
22.3403 | 2018-12-06 00:10 | 0.74963 | 10.5305
22.3472 | 2018-12-06 00:20 | 0.73737 | 8.1081
22.3542 | 2018-12-06 00:30 | 0.76996 | 5.8143
22.3611 | 2018-12-06 00:40 | 0.83061 | 8.7252
22.3681 | 2018-12-06 00:50 | 0.73355 | 9.2569
22.375 | 2018-12-06 01:00 | 0.86946 | 12.7575
22.3819 | 2018-12-06 01:10 | 0.86946 | 12.7575
22.3889 | 2018-12-06 01:20 | 0.65454 | 6.7559
22.3958 | 2018-12-06 01:30 | 0.59471 | 4.3396
22.4028 | 2018-12-06 01:40 | 0.67127 | 10.0376
22.4097 | 2018-12-06 01:50 | 0.63328 | 9.8193
22.4167 | 2018-12-06 02:00 | 0.69578 | 2.7185
22.4236 | 2018-12-06 02:10 | 0.69578 | 2.7185
22.4306 | 2018-12-06 02:20 | 0.44742 | 12.3899
22.4375 | 2018-12-06 02:30 | 0.42322 | 11.3099
22.4444 | 2018-12-06 02:40 | 0.42597 | 7.8257
22.4514 | 2018-12-06 02:50 | 0.30743 | 9.7381
22.4583 | 2018-12-06 03:00 | 0.39538 | 9.4623
22.4653 | 2018-12-06 03:10 | 0.39538 | 9.4623
22.4722 | 2018-12-06 03:20 | 0.34321 | 10.917
22.4792 | 2018-12-06 03:30 | 0.24291 | 4.9595
22.4861 | 2018-12-06 03:40 | 0.2524 | 17.2863
22.4931 | 2018-12-06 03:50 | 0.17249 | 4.3223
22.5 | 2018-12-06 04:00 | 0.098005 | 323.7147
22.5069 | 2018-12-06 04:10 | 0.098005 | 323.7147
22.5139 | 2018-12-06 04:20 | 0.16155 | 195.0685
22.5208 | 2018-12-06 04:30 | 0.27259 | 198.8338
22.5278 | 2018-12-06 04:40 | 0.32869 | 187.3412
22.5347 | 2018-12-06 04:50 | 0.43287 | 201.4081
22.5417 | 2018-12-06 05:00 | 0.42513 | 199.7989
22.5486 | 2018-12-06 05:10 | 0.42513 | 199.7989
22.5556 | 2018-12-06 05:20 | 0.46775 | 191.7183
22.5625 | 2018-12-06 05:30 | 0.59728 | 195.3392
22.5694 | 2018-12-06 05:40 | 0.55087 | 198.6323
22.5764 | 2018-12-06 05:50 | 0.57181 | 187.4357
22.5833 | 2018-12-06 06:00 | 0.63487 | 190.6197
22.5903 | 2018-12-06 06:10 | 0.63487 | 190.6197
22.5972 | 2018-12-06 06:20 | 0.64748 | 185.9395
22.6042 | 2018-12-06 06:30 | 0.68637 | 189.476
22.6111 | 2018-12-06 06:40 | 0.69369 | 191.8121
22.6181 | 2018-12-06 06:50 | 0.63981 | 193.9276
22.625 | 2018-12-06 07:00 | 0.63841 | 188.7393
22.6319 | 2018-12-06 07:10 | 0.63841 | 188.7393
22.6389 | 2018-12-06 07:20 | 0.72293 | 192.7867
22.6458 | 2018-12-06 07:30 | 0.84641 | 187.0578
22.6528 | 2018-12-06 07:40 | 0.60565 | 189.6956
22.6597 | 2018-12-06 07:50 | 0.70067 | 189.5295
22.6667 | 2018-12-06 08:00 | 0.58363 | 186.3944
22.6736 | 2018-12-06 08:10 | 0.58363 | 186.3944
22.6806 | 2018-12-06 08:20 | 0.64641 | 193.3268
22.6875 | 2018-12-06 08:30 | 0.62052 | 191.0564
22.6944 | 2018-12-06 08:40 | 0.54818 | 183.7654
22.7014 | 2018-12-06 08:50 | 0.58912 | 194.2485
22.7083 | 2018-12-06 09:00 | 0.38581 | 183.7153
22.7153 | 2018-12-06 09:10 | 0.38581 | 183.7153
22.7222 | 2018-12-06 09:20 | 0.33574 | 188.5645
22.7292 | 2018-12-06 09:30 | 0.36142 | 174.9204
22.7361 | 2018-12-06 09:40 | 0.26672 | 171.8091
22.7431 | 2018-12-06 09:50 | 0.16857 | 160.5977
22.75 | 2018-12-06 10:00 | 0.12567 | 154.0466
22.7569 | 2018-12-06 10:10 | 0.12567 | 154.0466
22.7639 | 2018-12-06 10:20 | 0.17171 | 34.8007
22.7708 | 2018-12-06 10:30 | 0.34937 | 25.2448
22.7778 | 2018-12-06 10:40 | 0.34883 | 30.6821
22.7847 | 2018-12-06 10:50 | 0.44842 | 18.1925
22.7917 | 2018-12-06 11:00 | 0.46816 | 13.0863
22.7986 | 2018-12-06 11:10 | 0.46816 | 13.0863
22.8056 | 2018-12-06 11:20 | 0.62626 | 7.4314
22.8125 | 2018-12-06 11:30 | 0.58325 | 11.2714
22.8194 | 2018-12-06 11:40 | 0.66 | 10.4757
22.8264 | 2018-12-06 11:50 | 0.76578 | 9.1671
22.8333 | 2018-12-06 12:00 | 0.82464 | 7.8058
22.8403 | 2018-12-06 12:10 | 0.82464 | 7.8058
22.8472 | 2018-12-06 12:20 | 0.89357 | 12.0142
22.8542 | 2018-12-06 12:30 | 0.84561 | 5.2926
22.8611 | 2018-12-06 12:40 | 0.97165 | 13.4499
22.8681 | 2018-12-06 12:50 | 0.77627 | 7.8483
22.875 | 2018-12-06 13:00 | 0.83951 | 8.632
22.8819 | 2018-12-06 13:10 | 0.83951 | 8.632
22.8889 | 2018-12-06 13:20 | 0.94041 | 10.0433
22.8958 | 2018-12-06 13:30 | 0.83812 | 12.2619
22.9028 | 2018-12-06 13:40 | 0.87703 | 11.3099
22.9097 | 2018-12-06 13:50 | 0.73803 | 11.9646
22.9167 | 2018-12-06 14:00 | 0.70123 | 10.2683
22.9236 | 2018-12-06 14:10 | 0.70123 | 10.2683
22.9306 | 2018-12-06 14:20 | 0.71736 | 6.3226
22.9375 | 2018-12-06 14:30 | 0.70644 | 9.8623
22.9444 | 2018-12-06 14:40 | 0.6323 | 10.8479
22.9514 | 2018-12-06 14:50 | 0.55383 | 7.5741
22.9583 | 2018-12-06 15:00 | 0.53416 | 5.1556
22.9653 | 2018-12-06 15:10 | 0.53416 | 5.1556
22.9722 | 2018-12-06 15:20 | 0.49922 | 5.4022
22.9792 | 2018-12-06 15:30 | 0.39561 | 3.1879
22.9861 | 2018-12-06 15:40 | 0.39507 | 10.0584
22.9931 | 2018-12-06 15:50 | 0.33326 | 13.5359
23 | 2018-12-06 16:00 | 0.28804 | 0.99462
23.0069 | 2018-12-06 16:10 | 0.28804 | 0.99462
23.0139 | 2018-12-06 16:20 | 0.14208 | 22.775
23.0208 | 2018-12-06 16:30 | 0.11807 | 321.1886
23.0278 | 2018-12-06 16:40 | 0.032527 | 45
23.0347 | 2018-12-06 16:50 | 0.0886 | 249.5196
23.0417 | 2018-12-06 17:00 | 0.16119 | 201.4714
23.0486 | 2018-12-06 17:10 | 0.16119 | 201.4714
23.0556 | 2018-12-06 17:20 | 0.35624 | 202.9663
23.0625 | 2018-12-06 17:30 | 0.41532 | 192.7982
23.0694 | 2018-12-06 17:40 | 0.45425 | 187.8447
23.0764 | 2018-12-06 17:50 | 0.48614 | 199.5904
23.0833 | 2018-12-06 18:00 | 0.61973 | 191.1649
23.0903 | 2018-12-06 18:10 | 0.61973 | 191.1649
23.0972 | 2018-12-06 18:20 | 0.59486 | 191.9333
23.1042 | 2018-12-06 18:30 | 0.61154 | 192.9455
23.1111 | 2018-12-06 18:40 | 0.63896 | 186.3798
23.1181 | 2018-12-06 18:50 | 0.67597 | 193.6045
23.125 | 2018-12-06 19:00 | 0.74801 | 197.3449
23.1319 | 2018-12-06 19:10 | 0.74801 | 197.3449
23.1389 | 2018-12-06 19:20 | 0.59807 | 180.8622
23.1458 | 2018-12-06 19:30 | 0.68525 | 194.9691
23.1528 | 2018-12-06 19:40 | 0.74051 | 187.6049
23.1597 | 2018-12-06 19:50 | 0.72297 | 190.4395
23.1667 | 2018-12-06 20:00 | 0.74744 | 188.618
23.1736 | 2018-12-06 20:10 | 0.74744 | 188.618
23.1806 | 2018-12-06 20:20 | 0.60046 | 192.6013
23.1875 | 2018-12-06 20:30 | 0.57658 | 191.5048
23.1944 | 2018-12-06 20:40 | 0.53659 | 192.9226
23.2014 | 2018-12-06 20:50 | 0.60177 | 188.6014
23.2083 | 2018-12-06 21:00 | 0.52623 | 188.0839
23.2153 | 2018-12-06 21:10 | 0.52623 | 188.0839
23.2222 | 2018-12-06 21:20 | 0.47405 | 185.3257
23.2292 | 2018-12-06 21:30 | 0.34637 | 193.3542
23.2361 | 2018-12-06 21:40 | 0.44785 | 192.6398
23.2431 | 2018-12-06 21:50 | 0.28176 | 198.6279
23.25 | 2018-12-06 22:00 | 0.33543 | 194.3262
23.2569 | 2018-12-06 22:10 | 0.33543 | 194.3262
23.2639 | 2018-12-06 22:20 | 0.13601 | 180.8425
23.2708 | 2018-12-06 22:30 | 0.02 | 36.8699
23.2778 | 2018-12-06 22:40 | 0.13086 | 350.3217
23.2847 | 2018-12-06 22:50 | 0.19104 | 19.5731
23.2917 | 2018-12-06 23:00 | 0.27198 | 25.246
23.2986 | 2018-12-06 23:10 | 0.27198 | 25.246
23.3056 | 2018-12-06 23:20 | 0.54139 | 18.6358
23.3125 | 2018-12-06 23:30 | 0.37049 | 16.6252
23.3194 | 2018-12-06 23:40 | 0.58075 | 12.0259
23.3264 | 2018-12-06 23:50 | 0.58898 | 3.3093
23.3333 | 2018-12-07 | 0.54612 | 12.5857
23.3403 | 2018-12-07 00:10 | 0.54612 | 12.5857
23.3472 | 2018-12-07 00:20 | 0.65508 | 10.5552
23.3542 | 2018-12-07 00:30 | 0.69131 | 11.2612
23.3611 | 2018-12-07 00:40 | 0.72232 | 11.8233
23.3681 | 2018-12-07 00:50 | 0.89356 | 8.8193
23.375 | 2018-12-07 01:00 | 0.77364 | 5.5632
23.3819 | 2018-12-07 01:10 | 0.77364 | 5.5632
23.3889 | 2018-12-07 01:20 | 0.76459 | 5.554
23.3958 | 2018-12-07 01:30 | 0.75405 | 12.5618
23.4028 | 2018-12-07 01:40 | 0.77735 | 10.2257
23.4097 | 2018-12-07 01:50 | 0.79196 | 7.0353
23.4167 | 2018-12-07 02:00 | 0.74347 | 6.953
23.4236 | 2018-12-07 02:10 | 0.74347 | 6.953
23.4306 | 2018-12-07 02:20 | 0.62444 | 11.4539
23.4375 | 2018-12-07 02:30 | 0.60927 | 5.9352
23.4444 | 2018-12-07 02:40 | 0.6234 | 9.417
23.4514 | 2018-12-07 02:50 | 0.52513 | 8.7628
23.4583 | 2018-12-07 03:00 | 0.43962 | 9.9551
23.4653 | 2018-12-07 03:10 | 0.43962 | 9.9551
23.4722 | 2018-12-07 03:20 | 0.55271 | 7.485
23.4792 | 2018-12-07 03:30 | 0.416 | 0.27546
23.4861 | 2018-12-07 03:40 | 0.39195 | 7.0344
23.4931 | 2018-12-07 03:50 | 0.403 | 0
23.5 | 2018-12-07 04:00 | 0.2018 | 354.8827
23.5069 | 2018-12-07 04:10 | 0.2018 | 354.8827
23.5139 | 2018-12-07 04:20 | 0.18128 | 356.8377
23.5208 | 2018-12-07 04:30 | 0.14072 | 309.2321
23.5278 | 2018-12-07 04:40 | 0.07931 | 311.9335
23.5347 | 2018-12-07 04:50 | 0.038013 | 178.4926
23.5417 | 2018-12-07 05:00 | 0.055946 | 208.8557
23.5486 | 2018-12-07 05:10 | 0.055946 | 208.8557
23.5556 | 2018-12-07 05:20 | 0.28372 | 197.2215
23.5625 | 2018-12-07 05:30 | 0.37239 | 208.9052
23.5694 | 2018-12-07 05:40 | 0.456 | 198.276
23.5764 | 2018-12-07 05:50 | 0.46493 | 189.908
23.5833 | 2018-12-07 06:00 | 0.45265 | 195.1108
23.5903 | 2018-12-07 06:10 | 0.45265 | 195.1108
23.5972 | 2018-12-07 06:20 | 0.50525 | 196.6775
23.6042 | 2018-12-07 06:30 | 0.59816 | 191.0845
23.6111 | 2018-12-07 06:40 | 0.66189 | 198.9551
23.6181 | 2018-12-07 06:50 | 0.58787 | 183.1204
23.625 | 2018-12-07 07:00 | 0.62032 | 192.7592
23.6319 | 2018-12-07 07:10 | 0.62032 | 192.7592
23.6389 | 2018-12-07 07:20 | 0.6401 | 194.7527
23.6458 | 2018-12-07 07:30 | 0.70672 | 185.0329
23.6528 | 2018-12-07 07:40 | 0.71219 | 192.2408
23.6597 | 2018-12-07 07:50 | 0.62293 | 192.1397
23.6667 | 2018-12-07 08:00 | 0.60346 | 193.4145
23.6736 | 2018-12-07 08:10 | 0.60346 | 193.4145
23.6806 | 2018-12-07 08:20 | 0.59786 | 192.3625
23.6875 | 2018-12-07 08:30 | 0.63258 | 186.9003
23.6944 | 2018-12-07 08:40 | 0.57326 | 196.728
23.7014 | 2018-12-07 08:50 | 0.521 | 187.9435
23.7083 | 2018-12-07 09:00 | 0.48049 | 191.4035
23.7153 | 2018-12-07 09:10 | 0.48049 | 191.4035
23.7222 | 2018-12-07 09:20 | 0.47297 | 193.4486
23.7292 | 2018-12-07 09:30 | 0.40749 | 182.8132
23.7361 | 2018-12-07 09:40 | 0.40528 | 177.8789
23.7431 | 2018-12-07 09:50 | 0.26223 | 188.9953
23.75 | 2018-12-07 10:00 | 0.34 | 188.7974
23.7569 | 2018-12-07 10:10 | 0.34 | 188.7974
23.7639 | 2018-12-07 10:20 | 0.13606 | 181.6847
23.7708 | 2018-12-07 10:30 | 0.090078 | 202.8645
23.7778 | 2018-12-07 10:40 | 0.13161 | 60.9031
23.7847 | 2018-12-07 10:50 | 0.10262 | 37.875
23.7917 | 2018-12-07 11:00 | 0.31705 | 6.5198
23.7986 | 2018-12-07 11:10 | 0.31705 | 6.5198
23.8056 | 2018-12-07 11:20 | 0.43684 | 10.1523
23.8125 | 2018-12-07 11:30 | 0.44388 | 9.335
23.8194 | 2018-12-07 11:40 | 0.48293 | 13.2881
23.8264 | 2018-12-07 11:50 | 0.67194 | 8.8175
23.8333 | 2018-12-07 12:00 | 0.6368 | 7.0357
23.8403 | 2018-12-07 12:10 | 0.6368 | 7.0357
23.8472 | 2018-12-07 12:20 | 0.77029 | 14.1264
23.8542 | 2018-12-07 12:30 | 0.86998 | 7.2639
23.8611 | 2018-12-07 12:40 | 0.75269 | 11.3398
23.8681 | 2018-12-07 12:50 | 0.86262 | 9.8117
23.875 | 2018-12-07 13:00 | 0.80355 | 14.4859
23.8819 | 2018-12-07 13:10 | 0.80355 | 14.4859
23.8889 | 2018-12-07 13:20 | 0.83092 | 6.8428
23.8958 | 2018-12-07 13:30 | 0.68688 | 8.1183
23.9028 | 2018-12-07 13:40 | 0.96001 | 15.9618
23.9097 | 2018-12-07 13:50 | 0.89409 | 7.7132
23.9167 | 2018-12-07 14:00 | 0.92626 | 11.0794
23.9236 | 2018-12-07 14:10 | 0.92626 | 11.0794
23.9306 | 2018-12-07 14:20 | 0.85315 | 16.9694
23.9375 | 2018-12-07 14:30 | 0.75205 | 6.6431
23.9444 | 2018-12-07 14:40 | 0.77631 | 3.3231
23.9514 | 2018-12-07 14:50 | 0.64237 | 8.6851
23.9583 | 2018-12-07 15:00 | 0.78407 | 4.1689
23.9653 | 2018-12-07 15:10 | 0.78407 | 4.1689
23.9722 | 2018-12-07 15:20 | 0.4848 | 11.5417
23.9792 | 2018-12-07 15:30 | 0.49407 | 12.1515
23.9861 | 2018-12-07 15:40 | 0.48251 | 9.4233
23.9931 | 2018-12-07 15:50 | 0.47736 | 4.3251
24 | 2018-12-07 16:00 | 0.34797 | 6.1038
24.0069 | 2018-12-07 16:10 | 0.34797 | 6.1038
24.0139 | 2018-12-07 16:20 | 0.26936 | 357.0208
24.0208 | 2018-12-07 16:30 | 0.29705 | 4.8277
24.0278 | 2018-12-07 16:40 | 0.23417 | 2.2026
24.0347 | 2018-12-07 16:50 | 0.14069 | 13.1472
24.0417 | 2018-12-07 17:00 | 0.17129 | 356.6532
24.0486 | 2018-12-07 17:10 | 0.17129 | 356.6532
24.0556 | 2018-12-07 17:20 | 0.1768 | 225.9167
24.0625 | 2018-12-07 17:30 | 0.097499 | 201.0375
24.0694 | 2018-12-07 17:40 | 0.29071 | 203.3021
24.0764 | 2018-12-07 17:50 | 0.319 | 208.2521
24.0833 | 2018-12-07 18:00 | 0.40929 | 197.1954
24.0903 | 2018-12-07 18:10 | 0.40929 | 197.1954
24.0972 | 2018-12-07 18:20 | 0.49997 | 198.9061
24.1042 | 2018-12-07 18:30 | 0.51324 | 198.3996
24.1111 | 2018-12-07 18:40 | 0.54093 | 201.5851
24.1181 | 2018-12-07 18:50 | 0.67856 | 191.4755
24.125 | 2018-12-07 19:00 | 0.62556 | 193.2143
24.1319 | 2018-12-07 19:10 | 0.62556 | 193.2143
24.1389 | 2018-12-07 19:20 | 0.57371 | 197.5506
24.1458 | 2018-12-07 19:30 | 0.69926 | 193.4798
24.1528 | 2018-12-07 19:40 | 0.70745 | 188.8632
24.1597 | 2018-12-07 19:50 | 0.66867 | 190.2512
24.1667 | 2018-12-07 20:00 | 0.67173 | 190.7244
24.1736 | 2018-12-07 20:10 | 0.67173 | 190.7244
24.1806 | 2018-12-07 20:20 | 0.74547 | 187.554
24.1875 | 2018-12-07 20:30 | 0.66173 | 185.2023
24.1944 | 2018-12-07 20:40 | 0.788 | 190.0122
24.2014 | 2018-12-07 20:50 | 0.63159 | 188.2841
24.2083 | 2018-12-07 21:00 | 0.61314 | 194.3535
24.2153 | 2018-12-07 21:10 | 0.61314 | 194.3535
24.2222 | 2018-12-07 21:20 | 0.56163 | 187.3654
24.2292 | 2018-12-07 21:30 | 0.61523 | 190.9629
24.2361 | 2018-12-07 21:40 | 0.57219 | 185.0131
24.2431 | 2018-12-07 21:50 | 0.44309 | 199.3755
24.25 | 2018-12-07 22:00 | 0.44256 | 199.9499
24.2569 | 2018-12-07 22:10 | 0.44256 | 199.9499
24.2639 | 2018-12-07 22:20 | 0.34462 | 190.3643
24.2708 | 2018-12-07 22:30 | 0.25761 | 193.0113
24.2778 | 2018-12-07 22:40 | 0.16813 | 195.5241
24.2847 | 2018-12-07 22:50 | 0.13823 | 183.3178
24.2917 | 2018-12-07 23:00 | 0.087824 | 172.1467
24.2986 | 2018-12-07 23:10 | 0.087824 | 172.1467
24.3056 | 2018-12-07 23:20 | 0.15911 | 357.8389
24.3125 | 2018-12-07 23:30 | 0.22911 | 7.7764
24.3194 | 2018-12-07 23:40 | 0.3246 | 21.5064
24.3264 | 2018-12-07 23:50 | 0.4835 | 9.4039
24.3333 | 2018-12-08 | 0.55412 | 16.2437
24.3403 | 2018-12-08 00:10 | 0.55412 | 16.2437
24.3472 | 2018-12-08 00:20 | 0.63612 | 10.2323
24.3542 | 2018-12-08 00:30 | 0.60731 | 14.1049
24.3611 | 2018-12-08 00:40 | 0.63852 | 8.1936
24.3681 | 2018-12-08 00:50 | 0.59581 | 8.0077
24.375 | 2018-12-08 01:00 | 0.77491 | 14.2694
24.3819 | 2018-12-08 01:10 | 0.77491 | 14.2694
24.3889 | 2018-12-08 01:20 | 0.79653 | 16.9335
24.3958 | 2018-12-08 01:30 | 0.84149 | 8.6116
24.4028 | 2018-12-08 01:40 | 0.79365 | 5.4951
24.4097 | 2018-12-08 01:50 | 0.86788 | 9.0825
24.4167 | 2018-12-08 02:00 | 0.90314 | 7.6994
24.4236 | 2018-12-08 02:10 | 0.90314 | 7.6994
24.4306 | 2018-12-08 02:20 | 0.78529 | 12.7266
24.4375 | 2018-12-08 02:30 | 0.70002 | 9.2067
24.4444 | 2018-12-08 02:40 | 0.94337 | 8.9032
24.4514 | 2018-12-08 02:50 | 0.60429 | 15.2551
24.4583 | 2018-12-08 03:00 | 0.75076 | 11.759
24.4653 | 2018-12-08 03:10 | 0.75076 | 11.759
24.4722 | 2018-12-08 03:20 | 0.64552 | 5.0659
24.4792 | 2018-12-08 03:30 | 0.6378 | 2.8759
24.4861 | 2018-12-08 03:40 | 0.59554 | 8.4975
24.4931 | 2018-12-08 03:50 | 0.49443 | 5.6875
24.5 | 2018-12-08 04:00 | 0.51241 | 4.2529
24.5069 | 2018-12-08 04:10 | 0.51241 | 4.2529
24.5139 | 2018-12-08 04:20 | 0.42432 | 7.1753
24.5208 | 2018-12-08 04:30 | 0.26315 | 1.9599
24.5278 | 2018-12-08 04:40 | 0.27735 | 7.4581
24.5347 | 2018-12-08 04:50 | 0.26631 | 7.552
24.5417 | 2018-12-08 05:00 | 0.23259 | 348.5934
24.5486 | 2018-12-08 05:10 | 0.23259 | 348.5934
24.5556 | 2018-12-08 05:20 | 0.17671 | 331.9847
24.5625 | 2018-12-08 05:30 | 0.086348 | 256.6075
24.5694 | 2018-12-08 05:40 | 0.15227 | 213.4813
24.5764 | 2018-12-08 05:50 | 0.12816 | 196.3139
24.5833 | 2018-12-08 06:00 | 0.3168 | 201.8686
24.5903 | 2018-12-08 06:10 | 0.3168 | 201.8686
24.5972 | 2018-12-08 06:20 | 0.38959 | 195.1777
24.6042 | 2018-12-08 06:30 | 0.48415 | 202.5926
24.6111 | 2018-12-08 06:40 | 0.51655 | 199.8031
24.6181 | 2018-12-08 06:50 | 0.56385 | 188.2594
24.625 | 2018-12-08 07:00 | 0.57524 | 189.7079
24.6319 | 2018-12-08 07:10 | 0.57524 | 189.7079
24.6389 | 2018-12-08 07:20 | 0.59106 | 193.8011
24.6458 | 2018-12-08 07:30 | 0.64375 | 192.2875
24.6528 | 2018-12-08 07:40 | 0.59953 | 185.2636
24.6597 | 2018-12-08 07:50 | 0.59397 | 188.1301
24.6667 | 2018-12-08 08:00 | 0.74071 | 193.9049
24.6736 | 2018-12-08 08:10 | 0.74071 | 193.9049
24.6806 | 2018-12-08 08:20 | 0.66735 | 195.2024
24.6875 | 2018-12-08 08:30 | 0.68288 | 191.1454
24.6944 | 2018-12-08 08:40 | 0.69526 | 189.8552
24.7014 | 2018-12-08 08:50 | 0.73259 | 192.936
24.7083 | 2018-12-08 09:00 | 0.7379 | 192.2846
24.7153 | 2018-12-08 09:10 | 0.7379 | 192.2846
24.7222 | 2018-12-08 09:20 | 0.57797 | 194.3248
24.7292 | 2018-12-08 09:30 | 0.5128 | 187.8457
24.7361 | 2018-12-08 09:40 | 0.62061 | 195.5142
24.7431 | 2018-12-08 09:50 | 0.55449 | 194.8382
24.75 | 2018-12-08 10:00 | 0.59597 | 196.9755
24.7569 | 2018-12-08 10:10 | 0.59597 | 196.9755
24.7639 | 2018-12-08 10:20 | 0.43615 | 187.9072
24.7708 | 2018-12-08 10:30 | 0.35895 | 199.1921
24.7778 | 2018-12-08 10:40 | 0.31057 | 197.6182
24.7847 | 2018-12-08 10:50 | 0.24319 | 198.9565
24.7917 | 2018-12-08 11:00 | 0.20496 | 199.6726
24.7986 | 2018-12-08 11:10 | 0.20496 | 199.6726
24.8056 | 2018-12-08 11:20 | 0.13119 | 236.1888
24.8125 | 2018-12-08 11:30 | 0.10604 | 344.1288
24.8194 | 2018-12-08 11:40 | 0.06631 | 336.9149
24.8264 | 2018-12-08 11:50 | 0.21086 | 354.8302
24.8333 | 2018-12-08 12:00 | 0.30728 | 5.2282
24.8403 | 2018-12-08 12:10 | 0.30728 | 5.2282
24.8472 | 2018-12-08 12:20 | 0.46003 | 15.6374
24.8542 | 2018-12-08 12:30 | 0.51833 | 19.0292
24.8611 | 2018-12-08 12:40 | 0.60031 | 11.1415
24.8681 | 2018-12-08 12:50 | 0.65298 | 6.3305
24.875 | 2018-12-08 13:00 | 0.7038 | 5.9536
24.8819 | 2018-12-08 13:10 | 0.7038 | 5.9536
24.8889 | 2018-12-08 13:20 | 0.80451 | 14.4681
24.8958 | 2018-12-08 13:30 | 0.71815 | 12.5461
24.9028 | 2018-12-08 13:40 | 0.90314 | 7.6994
24.9097 | 2018-12-08 13:50 | 0.76448 | 9.9429
24.9167 | 2018-12-08 14:00 | 0.72899 | 10.8321
24.9236 | 2018-12-08 14:10 | 0.72899 | 10.8321
24.9306 | 2018-12-08 14:20 | 0.70884 | 4.1259
24.9375 | 2018-12-08 14:30 | 0.80096 | 6.3797
24.9444 | 2018-12-08 14:40 | 0.7808 | 6.9885
24.9514 | 2018-12-08 14:50 | 0.73658 | 14.2249
24.9583 | 2018-12-08 15:00 | 0.83496 | 2.7459
24.9653 | 2018-12-08 15:10 | 0.83496 | 2.7459
24.9722 | 2018-12-08 15:20 | 0.68461 | 16.0259
24.9792 | 2018-12-08 15:30 | 0.57315 | 10.2512
24.9861 | 2018-12-08 15:40 | 0.6341 | 9.1652
24.9931 | 2018-12-08 15:50 | 0.47289 | 3.5159
25 | 2018-12-08 16:00 | 0.60482 | 11.3471
25.0069 | 2018-12-08 16:10 | 0.60482 | 11.3471
25.0139 | 2018-12-08 16:20 | 0.49192 | 13.1605
25.0208 | 2018-12-08 16:30 | 0.36715 | 4.5304
25.0278 | 2018-12-08 16:40 | 0.3262 | 4.9241
25.0347 | 2018-12-08 16:50 | 0.35257 | 3.2519
25.0417 | 2018-12-08 17:00 | 0.24906 | 5.2986
25.0486 | 2018-12-08 17:10 | 0.24906 | 5.2986
25.0556 | 2018-12-08 17:20 | 0.18191 | 346.6513
25.0625 | 2018-12-08 17:30 | 0.20263 | 355.4712
25.0694 | 2018-12-08 17:40 | 0.057706 | 332.1027
25.0764 | 2018-12-08 17:50 | 0.065788 | 250.4633
25.0833 | 2018-12-08 18:00 | 0.13208 | 212.0054
25.0903 | 2018-12-08 18:10 | 0.13208 | 212.0054
25.0972 | 2018-12-08 18:20 | 0.30686 | 209.907
25.1042 | 2018-12-08 18:30 | 0.35758 | 195.2411
25.1111 | 2018-12-08 18:40 | 0.44981 | 204.2858
25.1181 | 2018-12-08 18:50 | 0.49332 | 205.8379
25.125 | 2018-12-08 19:00 | 0.55222 | 189.2747
25.1319 | 2018-12-08 19:10 | 0.55222 | 189.2747
25.1389 | 2018-12-08 19:20 | 0.58189 | 197.8122
25.1458 | 2018-12-08 19:30 | 0.63228 | 195.5969
25.1528 | 2018-12-08 19:40 | 0.63052 | 190.9713
25.1597 | 2018-12-08 19:50 | 0.69742 | 184.7705
25.1667 | 2018-12-08 20:00 | 0.67161 | 188.0457
25.1736 | 2018-12-08 20:10 | 0.67161 | 188.0457
25.1806 | 2018-12-08 20:20 | 0.78122 | 193.6983
25.1875 | 2018-12-08 20:30 | 0.71977 | 188.9519
25.1944 | 2018-12-08 20:40 | 0.73399 | 192.351
25.2014 | 2018-12-08 20:50 | 0.77254 | 190.7427
25.2083 | 2018-12-08 21:00 | 0.75017 | 187.3524
25.2153 | 2018-12-08 21:10 | 0.75017 | 187.3524
25.2222 | 2018-12-08 21:20 | 0.63448 | 196.2927
25.2292 | 2018-12-08 21:30 | 0.6605 | 186.6946
25.2361 | 2018-12-08 21:40 | 0.65884 | 190.406
25.2431 | 2018-12-08 21:50 | 0.61448 | 190.5967
25.25 | 2018-12-08 22:00 | 0.54974 | 186.6855
25.2569 | 2018-12-08 22:10 | 0.54974 | 186.6855
25.2639 | 2018-12-08 22:20 | 0.45365 | 186.2007
25.2708 | 2018-12-08 22:30 | 0.47866 | 192.6716
25.2778 | 2018-12-08 22:40 | 0.43213 | 192.4281
25.2847 | 2018-12-08 22:50 | 0.32383 | 197.9873
25.2917 | 2018-12-08 23:00 | 0.30813 | 169.5288
25.2986 | 2018-12-08 23:10 | 0.30813 | 169.5288
25.3056 | 2018-12-08 23:20 | 0.17516 | 203.1986
25.3125 | 2018-12-08 23:30 | 0.025179 | 263.1572
25.3194 | 2018-12-08 23:40 | 0.06229 | 47.6026
25.3264 | 2018-12-08 23:50 | 0.073246 | 345.774
25.3333 | 2018-12-09 | 0.25329 | 7.7142
25.3403 | 2018-12-09 00:10 | 0.25329 | 7.7142
25.3472 | 2018-12-09 00:20 | 0.37535 | 7.6552
25.3542 | 2018-12-09 00:30 | 0.48093 | 6.327
25.3611 | 2018-12-09 00:40 | 0.49912 | 9.6888
25.3681 | 2018-12-09 00:50 | 0.61735 | 8.852
25.375 | 2018-12-09 01:00 | 0.68012 | 7.6893
25.3819 | 2018-12-09 01:10 | 0.68012 | 7.6893
25.3889 | 2018-12-09 01:20 | 0.75538 | 7.4543
25.3958 | 2018-12-09 01:30 | 0.6447 | 6.1439
25.4028 | 2018-12-09 01:40 | 0.81131 | 7.1513
25.4097 | 2018-12-09 01:50 | 0.75937 | 12.627
25.4167 | 2018-12-09 02:00 | 0.82039 | 10.7484
25.4236 | 2018-12-09 02:10 | 0.82039 | 10.7484
25.4306 | 2018-12-09 02:20 | 0.84167 | 4.5658
25.4375 | 2018-12-09 02:30 | 0.71888 | 13.8429
25.4444 | 2018-12-09 02:40 | 0.80124 | 5.1556
25.4514 | 2018-12-09 02:50 | 0.75182 | 4.9598
25.4583 | 2018-12-09 03:00 | 0.78251 | 11.4248
25.4653 | 2018-12-09 03:10 | 0.78251 | 11.4248
25.4722 | 2018-12-09 03:20 | 0.78872 | 3.7802
25.4792 | 2018-12-09 03:30 | 0.70768 | 8.4507
25.4861 | 2018-12-09 03:40 | 0.68488 | 11.9662
25.4931 | 2018-12-09 03:50 | 0.63594 | 18.2355
25.5 | 2018-12-09 04:00 | 0.70564 | 4.9592
25.5069 | 2018-12-09 04:10 | 0.70564 | 4.9592
25.5139 | 2018-12-09 04:20 | 0.49631 | 4.1596
25.5208 | 2018-12-09 04:30 | 0.47077 | 6.2192
25.5278 | 2018-12-09 04:40 | 0.44441 | 2.4504
25.5347 | 2018-12-09 04:50 | 0.43188 | 9.4623
25.5417 | 2018-12-09 05:00 | 0.31637 | 16.7166
25.5486 | 2018-12-09 05:10 | 0.31637 | 16.7166
25.5556 | 2018-12-09 05:20 | 0.41448 | 357.2343
25.5625 | 2018-12-09 05:30 | 0.36675 | 346.7595
25.5694 | 2018-12-09 05:40 | 0.27693 | 10.823
25.5764 | 2018-12-09 05:50 | 0.19972 | 355.1172
25.5833 | 2018-12-09 06:00 | 0.1073 | 309.327
25.5903 | 2018-12-09 06:10 | 0.1073 | 309.327
25.5972 | 2018-12-09 06:20 | 0.1142 | 217.1709
25.6042 | 2018-12-09 06:30 | 0.12249 | 185.1521
25.6111 | 2018-12-09 06:40 | 0.2956 | 196.1051
25.6181 | 2018-12-09 06:50 | 0.43128 | 204.9607
25.625 | 2018-12-09 07:00 | 0.43248 | 205.9133
25.6319 | 2018-12-09 07:10 | 0.43248 | 205.9133
25.6389 | 2018-12-09 07:20 | 0.52295 | 200.1329
25.6458 | 2018-12-09 07:30 | 0.42744 | 189.1538
25.6528 | 2018-12-09 07:40 | 0.49386 | 189.5577
25.6597 | 2018-12-09 07:50 | 0.61707 | 192.2569
25.6667 | 2018-12-09 08:00 | 0.69409 | 190.7109
25.6736 | 2018-12-09 08:10 | 0.69409 | 190.7109
25.6806 | 2018-12-09 08:20 | 0.67157 | 195.547
25.6875 | 2018-12-09 08:30 | 0.62601 | 194.5246
25.6944 | 2018-12-09 08:40 | 0.63416 | 188.6156
25.7014 | 2018-12-09 08:50 | 0.78759 | 183.6399
25.7083 | 2018-12-09 09:00 | 0.80927 | 192.8513
25.7153 | 2018-12-09 09:10 | 0.80927 | 192.8513
25.7222 | 2018-12-09 09:20 | 0.79253 | 191.7211
25.7292 | 2018-12-09 09:30 | 0.84167 | 183.6103
25.7361 | 2018-12-09 09:40 | 0.61826 | 192.3278
25.7431 | 2018-12-09 09:50 | 0.73611 | 188.5154
25.75 | 2018-12-09 10:00 | 0.58707 | 185.866
25.7569 | 2018-12-09 10:10 | 0.58707 | 185.866
25.7639 | 2018-12-09 10:20 | 0.62021 | 185.8301
25.7708 | 2018-12-09 10:30 | 0.62197 | 187.9477
25.7778 | 2018-12-09 10:40 | 0.58075 | 184.4441
25.7847 | 2018-12-09 10:50 | 0.48519 | 195.2966
25.7917 | 2018-12-09 11:00 | 0.40171 | 174.7152
25.7986 | 2018-12-09 11:10 | 0.40171 | 174.7152
25.8056 | 2018-12-09 11:20 | 0.32909 | 191.0368
25.8125 | 2018-12-09 11:30 | 0.20506 | 178.6028
25.8194 | 2018-12-09 11:40 | 0.1825 | 160.4729
25.8264 | 2018-12-09 11:50 | 0.16621 | 201.1613
25.8333 | 2018-12-09 12:00 | 0.11316 | 183.0394
25.8403 | 2018-12-09 12:10 | 0.11316 | 183.0394
25.8472 | 2018-12-09 12:20 | 0.199 | 0
25.8542 | 2018-12-09 12:30 | 0.31088 | 21.1169
25.8611 | 2018-12-09 12:40 | 0.34525 | 10.008
25.8681 | 2018-12-09 12:50 | 0.42023 | 7.1081
25.875 | 2018-12-09 13:00 | 0.48785 | 21.1471
25.8819 | 2018-12-09 13:10 | 0.48785 | 21.1471
25.8889 | 2018-12-09 13:20 | 0.49751 | 6.8108
25.8958 | 2018-12-09 13:30 | 0.5838 | 9.9625
25.9028 | 2018-12-09 13:40 | 0.66541 | 8.5563
25.9097 | 2018-12-09 13:50 | 0.63627 | 12.1577
25.9167 | 2018-12-09 14:00 | 0.65116 | 4.6686
25.9236 | 2018-12-09 14:10 | 0.65116 | 4.6686
25.9306 | 2018-12-09 14:20 | 0.76205 | 10.204
25.9375 | 2018-12-09 14:30 | 0.80792 | 6.3245
25.9444 | 2018-12-09 14:40 | 0.66261 | 12.4632
25.9514 | 2018-12-09 14:50 | 0.76989 | 9.1932
25.9583 | 2018-12-09 15:00 | 0.68123 | 8.3561
25.9653 | 2018-12-09 15:10 | 0.68123 | 8.3561
25.9722 | 2018-12-09 15:20 | 0.67344 | 5.7953
25.9792 | 2018-12-09 15:30 | 0.75015 | 11.5346
25.9861 | 2018-12-09 15:40 | 0.75401 | 4.1831
25.9931 | 2018-12-09 15:50 | 0.65371 | 17.6311
26 | 2018-12-09 16:00 | 0.62496 | 8.558
26.0069 | 2018-12-09 16:10 | 0.62496 | 8.558
26.0139 | 2018-12-09 16:20 | 0.59475 | 7.2445
26.0208 | 2018-12-09 16:30 | 0.5869 | 9.4142
26.0278 | 2018-12-09 16:40 | 0.48342 | 4.3896
26.0347 | 2018-12-09 16:50 | 0.47456 | 7.0202
26.0417 | 2018-12-09 17:00 | 0.44914 | 353.2231
26.0486 | 2018-12-09 17:10 | 0.44914 | 353.2231
26.0556 | 2018-12-09 17:20 | 0.2786 | 7.8393
26.0625 | 2018-12-09 17:30 | 0.2996 | 356.364
26.0694 | 2018-12-09 17:40 | 0.23965 | 11.3099
26.0764 | 2018-12-09 17:50 | 0.19992 | 334.204
26.0833 | 2018-12-09 18:00 | 0.06265 | 335.4803
26.0903 | 2018-12-09 18:10 | 0.06265 | 335.4803
26.0972 | 2018-12-09 18:20 | 0.053852 | 285.0685
26.1042 | 2018-12-09 18:30 | 0.17901 | 208.7126
26.1111 | 2018-12-09 18:40 | 0.20609 | 212.919
26.1181 | 2018-12-09 18:50 | 0.32483 | 214.7175
26.125 | 2018-12-09 19:00 | 0.44811 | 206.7938
26.1319 | 2018-12-09 19:10 | 0.44811 | 206.7938
26.1389 | 2018-12-09 19:20 | 0.38106 | 191.0445
26.1458 | 2018-12-09 19:30 | 0.51512 | 187.2492
26.1528 | 2018-12-09 19:40 | 0.51049 | 191.0678
26.1597 | 2018-12-09 19:50 | 0.49814 | 191.5806
26.1667 | 2018-12-09 20:00 | 0.49568 | 197.0092
26.1736 | 2018-12-09 20:10 | 0.49568 | 197.0092
26.1806 | 2018-12-09 20:20 | 0.66938 | 191.8975
26.1875 | 2018-12-09 20:30 | 0.73368 | 194.2825
26.1944 | 2018-12-09 20:40 | 0.77645 | 191.8165
26.2014 | 2018-12-09 20:50 | 0.66151 | 191.5987
26.2083 | 2018-12-09 21:00 | 0.69996 | 194.0561
26.2153 | 2018-12-09 21:10 | 0.69996 | 194.0561
26.2222 | 2018-12-09 21:20 | 0.75776 | 187.6596
26.2292 | 2018-12-09 21:30 | 0.74506 | 189.4244
26.2361 | 2018-12-09 21:40 | 0.69351 | 184.8803
26.2431 | 2018-12-09 21:50 | 0.75725 | 188.9648
26.25 | 2018-12-09 22:00 | 0.65635 | 183.6689
26.2569 | 2018-12-09 22:10 | 0.65635 | 183.6689
26.2639 | 2018-12-09 22:20 | 0.59414 | 181.2538
26.2708 | 2018-12-09 22:30 | 0.63153 | 183.9951
26.2778 | 2018-12-09 22:40 | 0.65037 | 189.7375
26.2847 | 2018-12-09 22:50 | 0.53129 | 176.0066
26.2917 | 2018-12-09 23:00 | 0.48754 | 177.2961
26.2986 | 2018-12-09 23:10 | 0.48754 | 177.2961
26.3056 | 2018-12-09 23:20 | 0.36145 | 186.6728
26.3125 | 2018-12-09 23:30 | 0.44515 | 184.1223
26.3194 | 2018-12-09 23:40 | 0.39537 | 182.4644
26.3264 | 2018-12-09 23:50 | 0.31484 | 186.1995
26.3333 | 2018-12-10 | 0.10331 | 175.5588
26.3403 | 2018-12-10 00:10 | 0.10331 | 175.5588
26.3472 | 2018-12-10 00:20 | 0.1504 | 175.8058
26.3542 | 2018-12-10 00:30 | 0.063246 | 145.3048
26.3611 | 2018-12-10 00:40 | 0.19739 | 24.2278
26.3681 | 2018-12-10 00:50 | 0.24233 | 21.8014
26.375 | 2018-12-10 01:00 | 0.30453 | 15.8162
26.3819 | 2018-12-10 01:10 | 0.30453 | 15.8162
26.3889 | 2018-12-10 01:20 | 0.52151 | 17.6359
26.3958 | 2018-12-10 01:30 | 0.54161 | 14.652
26.4028 | 2018-12-10 01:40 | 0.58921 | 17.4816
26.4097 | 2018-12-10 01:50 | 0.59623 | 8.2932
26.4167 | 2018-12-10 02:00 | 0.57525 | 1.6935
26.4236 | 2018-12-10 02:10 | 0.57525 | 1.6935
26.4306 | 2018-12-10 02:20 | 0.70117 | 6.9628
26.4375 | 2018-12-10 02:30 | 0.75302 | 359.5435
26.4444 | 2018-12-10 02:40 | 0.81063 | 8.37
26.4514 | 2018-12-10 02:50 | 0.92208 | 8.4816
26.4583 | 2018-12-10 03:00 | 0.81572 | 10.5247
26.4653 | 2018-12-10 03:10 | 0.81572 | 10.5247
26.4722 | 2018-12-10 03:20 | 0.78765 | 10.6822
26.4792 | 2018-12-10 03:30 | 0.87681 | 8.1301
26.4861 | 2018-12-10 03:40 | 0.7687 | 12.3186
26.4931 | 2018-12-10 03:50 | 0.66867 | 6.009
26.5 | 2018-12-10 04:00 | 0.68975 | 11.033
26.5069 | 2018-12-10 04:10 | 0.68975 | 11.033
26.5139 | 2018-12-10 04:20 | 0.67005 | 0.6841
26.5208 | 2018-12-10 04:30 | 0.60143 | 5.1513
26.5278 | 2018-12-10 04:40 | 0.66509 | 3.2754
26.5347 | 2018-12-10 04:50 | 0.60726 | 8.2368
26.5417 | 2018-12-10 05:00 | 0.55395 | 6.8428
26.5486 | 2018-12-10 05:10 | 0.55395 | 6.8428
26.5556 | 2018-12-10 05:20 | 0.42115 | 8.0531
26.5625 | 2018-12-10 05:30 | 0.3604 | 357.2964
26.5694 | 2018-12-10 05:40 | 0.30203 | 359.2411
26.5764 | 2018-12-10 05:50 | 0.4433 | 6.9968
26.5833 | 2018-12-10 06:00 | 0.31283 | 348.0076
26.5903 | 2018-12-10 06:10 | 0.31283 | 348.0076
26.5972 | 2018-12-10 06:20 | 0.16858 | 352.1583
26.6042 | 2018-12-10 06:30 | 0.080802 | 306.4444
26.6111 | 2018-12-10 06:40 | 0.12356 | 258.3263
26.6181 | 2018-12-10 06:50 | 0.081988 | 210.0049
26.625 | 2018-12-10 07:00 | 0.19587 | 225.2068
26.6319 | 2018-12-10 07:10 | 0.19587 | 225.2068
26.6389 | 2018-12-10 07:20 | 0.30992 | 222.9079
26.6458 | 2018-12-10 07:30 | 0.33743 | 208.6918
26.6528 | 2018-12-10 07:40 | 0.38866 | 201.7467
26.6597 | 2018-12-10 07:50 | 0.40821 | 193.4575
26.6667 | 2018-12-10 08:00 | 0.53827 | 200.556
26.6736 | 2018-12-10 08:10 | 0.53827 | 200.556
26.6806 | 2018-12-10 08:20 | 0.56267 | 191.6894
26.6875 | 2018-12-10 08:30 | 0.57589 | 189.495
26.6944 | 2018-12-10 08:40 | 0.60876 | 191.7529
26.7014 | 2018-12-10 08:50 | 0.61038 | 188.2894
26.7083 | 2018-12-10 09:00 | 0.65344 | 185.8851
26.7153 | 2018-12-10 09:10 | 0.65344 | 185.8851
26.7222 | 2018-12-10 09:20 | 0.62162 | 186.1875
26.7292 | 2018-12-10 09:30 | 0.65338 | 190.2264
26.7361 | 2018-12-10 09:40 | 0.73879 | 188.3275
26.7431 | 2018-12-10 09:50 | 0.73151 | 191.4328
26.75 | 2018-12-10 10:00 | 0.7492 | 190.77
26.7569 | 2018-12-10 10:10 | 0.7492 | 190.77
26.7639 | 2018-12-10 10:20 | 0.6708 | 188.7462
26.7708 | 2018-12-10 10:30 | 0.72835 | 188.6864
26.7778 | 2018-12-10 10:40 | 0.64496 | 189.0096
26.7847 | 2018-12-10 10:50 | 0.69514 | 181.154
26.7917 | 2018-12-10 11:00 | 0.52956 | 185.6352
26.7986 | 2018-12-10 11:10 | 0.52956 | 185.6352
26.8056 | 2018-12-10 11:20 | 0.5363 | 181.9234
26.8125 | 2018-12-10 11:30 | 0.37558 | 190.7415
26.8194 | 2018-12-10 11:40 | 0.4961 | 183.8141
26.8264 | 2018-12-10 11:50 | 0.34547 | 177.0134
26.8333 | 2018-12-10 12:00 | 0.32617 | 170.8265
26.8403 | 2018-12-10 12:10 | 0.32617 | 170.8265
26.8472 | 2018-12-10 12:20 | 0.33729 | 188.01
26.8542 | 2018-12-10 12:30 | 0.23759 | 171.5289
26.8611 | 2018-12-10 12:40 | 0.16492 | 159.0373
26.8681 | 2018-12-10 12:50 | 0.07225 | 228.3665
26.875 | 2018-12-10 13:00 | 0.10102 | 31.6447
26.8819 | 2018-12-10 13:10 | 0.10102 | 31.6447
26.8889 | 2018-12-10 13:20 | 0.36547 | 22.3545
26.8958 | 2018-12-10 13:30 | 0.40257 | 17.9399
26.9028 | 2018-12-10 13:40 | 0.51323 | 20.4123
26.9097 | 2018-12-10 13:50 | 0.47224 | 24.1226
26.9167 | 2018-12-10 14:00 | 0.53256 | 16.3592
26.9236 | 2018-12-10 14:10 | 0.53256 | 16.3592
26.9306 | 2018-12-10 14:20 | 0.63499 | 18.5491
26.9375 | 2018-12-10 14:30 | 0.69656 | 357.6962
26.9444 | 2018-12-10 14:40 | 0.61448 | 8.3279
26.9514 | 2018-12-10 14:50 | 0.77096 | 5.8067
26.9583 | 2018-12-10 15:00 | 0.64897 | 5.4822
26.9653 | 2018-12-10 15:10 | 0.64897 | 5.4822
26.9722 | 2018-12-10 15:20 | 0.73801 | 9.909
26.9792 | 2018-12-10 15:30 | 0.84554 | 7.1334
26.9861 | 2018-12-10 15:40 | 0.82252 | 3.4851
26.9931 | 2018-12-10 15:50 | 0.7689 | 9.2051
27 | 2018-12-10 16:00 | 0.77451 | 2.0718
27.0069 | 2018-12-10 16:10 | 0.77451 | 2.0718
27.0139 | 2018-12-10 16:20 | 0.63031 | 8.1172
27.0208 | 2018-12-10 16:30 | 0.6226 | 8.9631
27.0278 | 2018-12-10 16:40 | 0.63266 | 5.26
27.0347 | 2018-12-10 16:50 | 0.60319 | 1.425
27.0417 | 2018-12-10 17:00 | 0.53808 | 3.6228
27.0486 | 2018-12-10 17:10 | 0.53808 | 3.6228
27.0556 | 2018-12-10 17:20 | 0.44416 | 1.5482
27.0625 | 2018-12-10 17:30 | 0.43819 | 1.7001
27.0694 | 2018-12-10 17:40 | 0.40588 | 352.0695
27.0764 | 2018-12-10 17:50 | 0.43966 | 356.8708
27.0833 | 2018-12-10 18:00 | 0.27772 | 4.1297
27.0903 | 2018-12-10 18:10 | 0.27772 | 4.1297
27.0972 | 2018-12-10 18:20 | 0.22006 | 344.448
27.1042 | 2018-12-10 18:30 | 0.12843 | 319.7375
27.1111 | 2018-12-10 18:40 | 0.10651 | 304.2869
27.1181 | 2018-12-10 18:50 | 0.11811 | 267.5737
27.125 | 2018-12-10 19:00 | 0.13515 | 257.6091
27.1319 | 2018-12-10 19:10 | 0.13515 | 257.6091
27.1389 | 2018-12-10 19:20 | 0.1476 | 205.697
27.1458 | 2018-12-10 19:30 | 0.28486 | 211.0672
27.1528 | 2018-12-10 19:40 | 0.38856 | 194.6085
27.1597 | 2018-12-10 19:50 | 0.37753 | 207.7868
27.1667 | 2018-12-10 20:00 | 0.43615 | 187.9072
27.1736 | 2018-12-10 20:10 | 0.43615 | 187.9072
27.1806 | 2018-12-10 20:20 | 0.47344 | 186.9149
27.1875 | 2018-12-10 20:30 | 0.59721 | 183.6481
27.1944 | 2018-12-10 20:40 | 0.60998 | 188.6747
27.2014 | 2018-12-10 20:50 | 0.59876 | 186.4247
27.2083 | 2018-12-10 21:00 | 0.6069 | 184.5363
27.2153 | 2018-12-10 21:10 | 0.6069 | 184.5363
27.2222 | 2018-12-10 21:20 | 0.70796 | 188.0385
27.2292 | 2018-12-10 21:30 | 0.75477 | 188.2267
27.2361 | 2018-12-10 21:40 | 0.61486 | 189.1712
27.2431 | 2018-12-10 21:50 | 0.72046 | 190.2337
27.25 | 2018-12-10 22:00 | 0.61577 | 186.3402
27.2569 | 2018-12-10 22:10 | 0.61577 | 186.3402
27.2639 | 2018-12-10 22:20 | 0.61516 | 181.3041
27.2708 | 2018-12-10 22:30 | 0.65149 | 183.8726
27.2778 | 2018-12-10 22:40 | 0.64038 | 181.9688
27.2847 | 2018-12-10 22:50 | 0.58247 | 189.7858
27.2917 | 2018-12-10 23:00 | 0.62926 | 181.6392
27.2986 | 2018-12-10 23:10 | 0.62926 | 181.6392
27.3056 | 2018-12-10 23:20 | 0.39679 | 183.6124
27.3125 | 2018-12-10 23:30 | 0.43533 | 182.238
27.3194 | 2018-12-10 23:40 | 0.55003 | 179.375
27.3264 | 2018-12-10 23:50 | 0.41622 | 166.6649
27.3333 | 2018-12-11 | 0.40081 | 174.5597
27.3403 | 2018-12-11 00:10 | 0.40081 | 174.5597
27.3472 | 2018-12-11 00:20 | 0.32421 | 167.8929
27.3542 | 2018-12-11 00:30 | 0.24666 | 175.8151
27.3611 | 2018-12-11 00:40 | 0.22897 | 185.2624
27.3681 | 2018-12-11 00:50 | 0.15845 | 136.5343
27.375 | 2018-12-11 01:00 | 0.1921 | 139.0105
27.3819 | 2018-12-11 01:10 | 0.1921 | 139.0105
27.3889 | 2018-12-11 01:20 | 0.17608 | 45.6903
27.3958 | 2018-12-11 01:30 | 0.18524 | 37.9835
27.4028 | 2018-12-11 01:40 | 0.35046 | 22.8336
27.4097 | 2018-12-11 01:50 | 0.42743 | 30.0442
27.4167 | 2018-12-11 02:00 | 0.56317 | 13.7648
27.4236 | 2018-12-11 02:10 | 0.56317 | 13.7648
27.4306 | 2018-12-11 02:20 | 0.57919 | 14.3961
27.4375 | 2018-12-11 02:30 | 0.59353 | 14.7386
27.4444 | 2018-12-11 02:40 | 0.68865 | 7.3417
27.4514 | 2018-12-11 02:50 | 0.6613 | 8.5222
27.4583 | 2018-12-11 03:00 | 0.68967 | 9.0936
27.4653 | 2018-12-11 03:10 | 0.68967 | 9.0936
27.4722 | 2018-12-11 03:20 | 0.92081 | 9.1861
27.4792 | 2018-12-11 03:30 | 0.8562 | 9.6824
27.4861 | 2018-12-11 03:40 | 0.72521 | 10.0858
27.4931 | 2018-12-11 03:50 | 0.89285 | 13.2736
27.5 | 2018-12-11 04:00 | 0.66501 | 0.25848
27.5069 | 2018-12-11 04:10 | 0.66501 | 0.25848
27.5139 | 2018-12-11 04:20 | 0.67458 | 8.01
27.5208 | 2018-12-11 04:30 | 0.77531 | 9.353
27.5278 | 2018-12-11 04:40 | 0.80276 | 6.8683
27.5347 | 2018-12-11 04:50 | 0.65938 | 10.6624
27.5417 | 2018-12-11 05:00 | 0.59005 | 6.7155
27.5486 | 2018-12-11 05:10 | 0.59005 | 6.7155
27.5556 | 2018-12-11 05:20 | 0.49552 | 6.8382
27.5625 | 2018-12-11 05:30 | 0.57219 | 5.0131
27.5694 | 2018-12-11 05:40 | 0.47327 | 358.0626
27.5764 | 2018-12-11 05:50 | 0.531 | 0.1079
27.5833 | 2018-12-11 06:00 | 0.31827 | 2.341
27.5903 | 2018-12-11 06:10 | 0.31827 | 2.341
27.5972 | 2018-12-11 06:20 | 0.33972 | 12.2361
27.6042 | 2018-12-11 06:30 | 0.19972 | 4.8828
27.6111 | 2018-12-11 06:40 | 0.21926 | 346.2806
27.6181 | 2018-12-11 06:50 | 0.21285 | 354.8787
27.625 | 2018-12-11 07:00 | 0.22436 | 348.6901
27.6319 | 2018-12-11 07:10 | 0.22436 | 348.6901
27.6389 | 2018-12-11 07:20 | 0.08132 | 343.5707
27.6458 | 2018-12-11 07:30 | 0.090443 | 234.9042
27.6528 | 2018-12-11 07:40 | 0.19576 | 250.9171
27.6597 | 2018-12-11 07:50 | 0.28265 | 214.4772
27.6667 | 2018-12-11 08:00 | 0.31143 | 204.6723
27.6736 | 2018-12-11 08:10 | 0.31143 | 204.6723
27.6806 | 2018-12-11 08:20 | 0.35468 | 195.3685
27.6875 | 2018-12-11 08:30 | 0.35379 | 191.2464
27.6944 | 2018-12-11 08:40 | 0.46109 | 190.7494
27.7014 | 2018-12-11 08:50 | 0.55324 | 187.8958
27.7083 | 2018-12-11 09:00 | 0.63334 | 186.7098
27.7153 | 2018-12-11 09:10 | 0.63334 | 186.7098
27.7222 | 2018-12-11 09:20 | 0.52582 | 194.0891
27.7292 | 2018-12-11 09:30 | 0.51019 | 186.4146
27.7361 | 2018-12-11 09:40 | 0.51832 | 184.0935
27.7431 | 2018-12-11 09:50 | 0.53374 | 187.6443
27.75 | 2018-12-11 10:00 | 0.51482 | 183.2292
27.7569 | 2018-12-11 10:10 | 0.51482 | 183.2292
27.7639 | 2018-12-11 10:20 | 0.58399 | 185.7985
27.7708 | 2018-12-11 10:30 | 0.62283 | 186.3605
27.7778 | 2018-12-11 10:40 | 0.65722 | 183.4893
27.7847 | 2018-12-11 10:50 | 0.70032 | 188.2921
27.7917 | 2018-12-11 11:00 | 0.54726 | 181.7801
27.7986 | 2018-12-11 11:10 | 0.54726 | 181.7801
27.8056 | 2018-12-11 11:20 | 0.58921 | 193.0456
27.8125 | 2018-12-11 11:30 | 0.58068 | 189.9165
27.8194 | 2018-12-11 11:40 | 0.59386 | 184.5393
27.8264 | 2018-12-11 11:50 | 0.58508 | 186.7728
27.8333 | 2018-12-11 12:00 | 0.35813 | 186.2519
27.8403 | 2018-12-11 12:10 | 0.35813 | 186.2519
27.8472 | 2018-12-11 12:20 | 0.46047 | 187.9893
27.8542 | 2018-12-11 12:30 | 0.42544 | 175.2811
27.8611 | 2018-12-11 12:40 | 0.319 | 180
27.8681 | 2018-12-11 12:50 | 0.15308 | 151.0908
27.875 | 2018-12-11 13:00 | 0.26123 | 162.3974
27.8819 | 2018-12-11 13:10 | 0.26123 | 162.3974
27.8889 | 2018-12-11 13:20 | 0.21927 | 165.2032
27.8958 | 2018-12-11 13:30 | 0.2129 | 133.6678
27.9028 | 2018-12-11 13:40 | 0.11924 | 101.1215
27.9097 | 2018-12-11 13:50 | 0.19801 | 44.1816
27.9167 | 2018-12-11 14:00 | 0.2523 | 27.8855
27.9236 | 2018-12-11 14:10 | 0.2523 | 27.8855
27.9306 | 2018-12-11 14:20 | 0.4105 | 24.005
27.9375 | 2018-12-11 14:30 | 0.56123 | 13.8134
27.9444 | 2018-12-11 14:40 | 0.61504 | 10.8714
27.9514 | 2018-12-11 14:50 | 0.51384 | 11.791
27.9583 | 2018-12-11 15:00 | 0.5713 | 7.0379
27.9653 | 2018-12-11 15:10 | 0.5713 | 7.0379
27.9722 | 2018-12-11 15:20 | 0.62825 | 14.9432
27.9792 | 2018-12-11 15:30 | 0.80317 | 8.6648
27.9861 | 2018-12-11 15:40 | 0.66547 | 11.9685
27.9931 | 2018-12-11 15:50 | 0.738 | 0.077637
28 | 2018-12-11 16:00 | 0.90874 | 12.8434
28.0069 | 2018-12-11 16:10 | 0.90874 | 12.8434
28.0139 | 2018-12-11 16:20 | 0.83951 | 6.5663
28.0208 | 2018-12-11 16:30 | 0.60641 | 5.1089
28.0278 | 2018-12-11 16:40 | 0.70507 | 4.3925
28.0347 | 2018-12-11 16:50 | 0.73107 | 359.2162
28.0417 | 2018-12-11 17:00 | 0.63186 | 2.9937
28.0486 | 2018-12-11 17:10 | 0.63186 | 2.9937
28.0556 | 2018-12-11 17:20 | 0.67793 | 5.3322
28.0625 | 2018-12-11 17:30 | 0.64937 | 1.9415
28.0694 | 2018-12-11 17:40 | 0.48846 | 6.8195
28.0764 | 2018-12-11 17:50 | 0.41574 | 5.2443
28.0833 | 2018-12-11 18:00 | 0.37449 | 7.8272
28.0903 | 2018-12-11 18:10 | 0.37449 | 7.8272
28.0972 | 2018-12-11 18:20 | 0.25013 | 1.8328
28.1042 | 2018-12-11 18:30 | 0.25833 | 2.8846
28.1111 | 2018-12-11 18:40 | 0.22702 | 14.2811
28.1181 | 2018-12-11 18:50 | 0.17564 | 329.9314
28.125 | 2018-12-11 19:00 | 0.17579 | 351.8238
28.1319 | 2018-12-11 19:10 | 0.17579 | 351.8238
28.1389 | 2018-12-11 19:20 | 0.11962 | 293.1357
28.1458 | 2018-12-11 19:30 | 0.12648 | 236.9382
28.1528 | 2018-12-11 19:40 | 0.14151 | 248.8753
28.1597 | 2018-12-11 19:50 | 0.15443 | 209.0546
28.1667 | 2018-12-11 20:00 | 0.22176 | 211.5398
28.1736 | 2018-12-11 20:10 | 0.22176 | 211.5398
28.1806 | 2018-12-11 20:20 | 0.50325 | 197.1027
28.1875 | 2018-12-11 20:30 | 0.47246 | 202.6572
28.1944 | 2018-12-11 20:40 | 0.52919 | 199.7704
28.2014 | 2018-12-11 20:50 | 0.49081 | 187.1395
28.2083 | 2018-12-11 21:00 | 0.54911 | 189.8569
28.2153 | 2018-12-11 21:10 | 0.54911 | 189.8569
28.2222 | 2018-12-11 21:20 | 0.47762 | 186.009
28.2292 | 2018-12-11 21:30 | 0.51154 | 187.6391
28.2361 | 2018-12-11 21:40 | 0.59242 | 183.9685
28.2431 | 2018-12-11 21:50 | 0.61847 | 177.776
28.25 | 2018-12-11 22:00 | 0.58802 | 179.5128
28.2569 | 2018-12-11 22:10 | 0.58802 | 179.5128
28.2639 | 2018-12-11 22:20 | 0.59085 | 185.6334
28.2708 | 2018-12-11 22:30 | 0.622 | 185.6281
28.2778 | 2018-12-11 22:40 | 0.5388 | 184.6842
28.2847 | 2018-12-11 22:50 | 0.59619 | 184.9073
28.2917 | 2018-12-11 23:00 | 0.5067 | 190.0014
28.2986 | 2018-12-11 23:10 | 0.5067 | 190.0014
28.3056 | 2018-12-11 23:20 | 0.57419 | 187.7067
28.3125 | 2018-12-11 23:30 | 0.64587 | 190.527
28.3194 | 2018-12-11 23:40 | 0.54653 | 186.5139
28.3264 | 2018-12-11 23:50 | 0.569 | 180.1007
28.3333 | 2018-12-12 | 0.53653 | 185.5618
28.3403 | 2018-12-12 00:10 | 0.53653 | 185.5618
28.3472 | 2018-12-12 00:20 | 0.48949 | 182.576
28.3542 | 2018-12-12 00:30 | 0.35456 | 183.2336
28.3611 | 2018-12-12 00:40 | 0.43209 | 181.1935
28.3681 | 2018-12-12 00:50 | 0.23265 | 188.6525
28.375 | 2018-12-12 01:00 | 0.164 | 157.0308
28.3819 | 2018-12-12 01:10 | 0.164 | 157.0308
28.3889 | 2018-12-12 01:20 | 0.12925 | 152.8402
28.3958 | 2018-12-12 01:30 | 0.23238 | 148.9094
28.4028 | 2018-12-12 01:40 | 0.1009 | 109.692
28.4097 | 2018-12-12 01:50 | 0.13636 | 69.8374
28.4167 | 2018-12-12 02:00 | 0.10102 | 68.5146
28.4236 | 2018-12-12 02:10 | 0.10102 | 68.5146
28.4306 | 2018-12-12 02:20 | 0.34698 | 15.7186
28.4375 | 2018-12-12 02:30 | 0.46512 | 33.6901
28.4444 | 2018-12-12 02:40 | 0.55799 | 15.3812
28.4514 | 2018-12-12 02:50 | 0.61466 | 10.6884
28.4583 | 2018-12-12 03:00 | 0.59641 | 18.678
28.4653 | 2018-12-12 03:10 | 0.59641 | 18.678
28.4722 | 2018-12-12 03:20 | 0.66368 | 2.5908
28.4792 | 2018-12-12 03:30 | 0.75147 | 3.5858
28.4861 | 2018-12-12 03:40 | 0.77764 | 4.7208
28.4931 | 2018-12-12 03:50 | 0.64386 | 7.0478
28.5 | 2018-12-12 04:00 | 0.59604 | 12.0075
28.5069 | 2018-12-12 04:10 | 0.59604 | 12.0075
28.5139 | 2018-12-12 04:20 | 0.85482 | 12.3616
28.5208 | 2018-12-12 04:30 | 0.82472 | 6.7545
28.5278 | 2018-12-12 04:40 | 0.72976 | 5.82
28.5347 | 2018-12-12 04:50 | 0.75352 | 6.9364
28.5417 | 2018-12-12 05:00 | 0.70018 | 6.9728
28.5486 | 2018-12-12 05:10 | 0.70018 | 6.9728
28.5556 | 2018-12-12 05:20 | 0.66879 | 5.2332
28.5625 | 2018-12-12 05:30 | 0.62184 | 8.508
28.5694 | 2018-12-12 05:40 | 0.5878 | 7.3305
28.5764 | 2018-12-12 05:50 | 0.53615 | 8.6893
28.5833 | 2018-12-12 06:00 | 0.49529 | 1.967
28.5903 | 2018-12-12 06:10 | 0.49529 | 1.967
28.5972 | 2018-12-12 06:20 | 0.43672 | 18.1445
28.6042 | 2018-12-12 06:30 | 0.49992 | 10.8379
28.6111 | 2018-12-12 06:40 | 0.34232 | 12.6559
28.6181 | 2018-12-12 06:50 | 0.44204 | 15.4825
28.625 | 2018-12-12 07:00 | 0.39148 | 4.9824
28.6319 | 2018-12-12 07:10 | 0.39148 | 4.9824
28.6389 | 2018-12-12 07:20 | 0.22178 | 350.9199
28.6458 | 2018-12-12 07:30 | 0.21652 | 3.9725
28.6528 | 2018-12-12 07:40 | 0.21974 | 4.6987
28.6597 | 2018-12-12 07:50 | 0.076662 | 300.5792
28.6667 | 2018-12-12 08:00 | 0.1077 | 301.3287
28.6736 | 2018-12-12 08:10 | 0.1077 | 301.3287
28.6806 | 2018-12-12 08:20 | 0.080081 | 254.0546
28.6875 | 2018-12-12 08:30 | 0.17475 | 214.5085
28.6944 | 2018-12-12 08:40 | 0.25701 | 202.174
28.7014 | 2018-12-12 08:50 | 0.289 | 208.0725
28.7083 | 2018-12-12 09:00 | 0.33316 | 202.4082
28.7153 | 2018-12-12 09:10 | 0.33316 | 202.4082
28.7222 | 2018-12-12 09:20 | 0.41503 | 185.6694
28.7292 | 2018-12-12 09:30 | 0.42308 | 181.0835
28.7361 | 2018-12-12 09:40 | 0.53018 | 186.2805
28.7431 | 2018-12-12 09:50 | 0.45699 | 183.764
28.75 | 2018-12-12 10:00 | 0.43599 | 186.7175
28.7569 | 2018-12-12 10:10 | 0.43599 | 186.7175
28.7639 | 2018-12-12 10:20 | 0.58187 | 194.6333
28.7708 | 2018-12-12 10:30 | 0.52612 | 188.7462
28.7778 | 2018-12-12 10:40 | 0.58032 | 186.133
28.7847 | 2018-12-12 10:50 | 0.63018 | 181.3639
28.7917 | 2018-12-12 11:00 | 0.62063 | 188.9918
28.7986 | 2018-12-12 11:10 | 0.62063 | 188.9918
28.8056 | 2018-12-12 11:20 | 0.55046 | 185.4206
28.8125 | 2018-12-12 11:30 | 0.51972 | 191.6559
28.8194 | 2018-12-12 11:40 | 0.68359 | 189.0903
28.8264 | 2018-12-12 11:50 | 0.48778 | 192.0701
28.8333 | 2018-12-12 12:00 | 0.50021 | 185.3915
28.8403 | 2018-12-12 12:10 | 0.50021 | 185.3915
28.8472 | 2018-12-12 12:20 | 0.41894 | 183.8323
28.8542 | 2018-12-12 12:30 | 0.45816 | 178.4991
28.8611 | 2018-12-12 12:40 | 0.44817 | 185.6343
28.8681 | 2018-12-12 12:50 | 0.35807 | 181.1202
28.875 | 2018-12-12 13:00 | 0.43115 | 192.4567
28.8819 | 2018-12-12 13:10 | 0.43115 | 192.4567
28.8889 | 2018-12-12 13:20 | 0.2939 | 175.5116
28.8958 | 2018-12-12 13:30 | 0.15357 | 158.6143
28.9028 | 2018-12-12 13:40 | 0.2129 | 154.3978
28.9097 | 2018-12-12 13:50 | 0.1328 | 142.9575
28.9167 | 2018-12-12 14:00 | 0.15729 | 101.7386
28.9236 | 2018-12-12 14:10 | 0.15729 | 101.7386
28.9306 | 2018-12-12 14:20 | 0.22365 | 38.0997
28.9375 | 2018-12-12 14:30 | 0.36806 | 26.2866
28.9444 | 2018-12-12 14:40 | 0.36135 | 30.6103
28.9514 | 2018-12-12 14:50 | 0.37975 | 21.6333
28.9583 | 2018-12-12 15:00 | 0.47557 | 21.9804
28.9653 | 2018-12-12 15:10 | 0.47557 | 21.9804
28.9722 | 2018-12-12 15:20 | 0.49833 | 23.7874
28.9792 | 2018-12-12 15:30 | 0.60659 | 15.6859
28.9861 | 2018-12-12 15:40 | 0.706 | 6.0982
28.9931 | 2018-12-12 15:50 | 0.70373 | 2.6063
29 | 2018-12-12 16:00 | 0.7456 | 15.6393
29.0069 | 2018-12-12 16:10 | 0.7456 | 15.6393
29.0139 | 2018-12-12 16:20 | 0.82629 | 9.0519
29.0208 | 2018-12-12 16:30 | 0.81395 | 12.0554
29.0278 | 2018-12-12 16:40 | 0.71415 | 9.6734
29.0347 | 2018-12-12 16:50 | 0.65392 | 10.4851
29.0417 | 2018-12-12 17:00 | 0.7178 | 16.8445
29.0486 | 2018-12-12 17:10 | 0.7178 | 16.8445
29.0556 | 2018-12-12 17:20 | 0.61764 | 4.1781
29.0625 | 2018-12-12 17:30 | 0.66911 | 15.4278
29.0694 | 2018-12-12 17:40 | 0.59424 | 11.6503
29.0764 | 2018-12-12 17:50 | 0.55092 | 4.7896
29.0833 | 2018-12-12 18:00 | 0.54667 | 5.6689
29.0903 | 2018-12-12 18:10 | 0.54667 | 5.6689
29.0972 | 2018-12-12 18:20 | 0.49618 | 11.627
29.1042 | 2018-12-12 18:30 | 0.47694 | 3.6063
29.1111 | 2018-12-12 18:40 | 0.3907 | 12.1152
29.1181 | 2018-12-12 18:50 | 0.43071 | 18.6873
29.125 | 2018-12-12 19:00 | 0.37834 | 6.3736
29.1319 | 2018-12-12 19:10 | 0.37834 | 6.3736
29.1389 | 2018-12-12 19:20 | 0.26155 | 3.7266
29.1458 | 2018-12-12 19:30 | 0.23801 | 0.48147
29.1528 | 2018-12-12 19:40 | 0.213 | 359.731
29.1597 | 2018-12-12 19:50 | 0.12443 | 13.4778
29.1667 | 2018-12-12 20:00 | 0.039699 | 49.0856
29.1736 | 2018-12-12 20:10 | 0.039699 | 49.0856
29.1806 | 2018-12-12 20:20 | 0.070831 | 210.5476
29.1875 | 2018-12-12 20:30 | 0.14866 | 169.1436
29.1944 | 2018-12-12 20:40 | 0.16134 | 219.2144
29.2014 | 2018-12-12 20:50 | 0.25581 | 189.9042
29.2083 | 2018-12-12 21:00 | 0.31306 | 181.0982
29.2153 | 2018-12-12 21:10 | 0.31306 | 181.0982
29.2222 | 2018-12-12 21:20 | 0.41914 | 181.5038
29.2292 | 2018-12-12 21:30 | 0.40265 | 191.896
29.2361 | 2018-12-12 21:40 | 0.34771 | 168.7224
29.2431 | 2018-12-12 21:50 | 0.48966 | 185.9784
29.25 | 2018-12-12 22:00 | 0.38382 | 188.0879
29.2569 | 2018-12-12 22:10 | 0.38382 | 188.0879
29.2639 | 2018-12-12 22:20 | 0.53565 | 175.5029
29.2708 | 2018-12-12 22:30 | 0.577 | 188.2705
29.2778 | 2018-12-12 22:40 | 0.50248 | 182.5094
29.2847 | 2018-12-12 22:50 | 0.62017 | 194.2827
29.2917 | 2018-12-12 23:00 | 0.54268 | 189.6532
29.2986 | 2018-12-12 23:10 | 0.54268 | 189.6532
29.3056 | 2018-12-12 23:20 | 0.55248 | 196.4012
29.3125 | 2018-12-12 23:30 | 0.47513 | 189.9381
29.3194 | 2018-12-12 23:40 | 0.52934 | 182.057
29.3264 | 2018-12-12 23:50 | 0.53568 | 182.8891
29.3333 | 2018-12-13 | 0.51 | 180.2247
29.3403 | 2018-12-13 00:10 | 0.51 | 180.2247
29.3472 | 2018-12-13 00:20 | 0.4241 | 181.216
29.3542 | 2018-12-13 00:30 | 0.40018 | 181.7184
29.3611 | 2018-12-13 00:40 | 0.46721 | 181.7171
29.3681 | 2018-12-13 00:50 | 0.30801 | 179.4419
29.375 | 2018-12-13 01:00 | 0.44701 | 179.6155
29.3819 | 2018-12-13 01:10 | 0.44701 | 179.6155
29.3889 | 2018-12-13 01:20 | 0.36346 | 187.9072
29.3958 | 2018-12-13 01:30 | 0.28411 | 178.3865
29.4028 | 2018-12-13 01:40 | 0.25378 | 168.8672
29.4097 | 2018-12-13 01:50 | 0.26808 | 174.8636
29.4167 | 2018-12-13 02:00 | 0.14872 | 150.1595
29.4236 | 2018-12-13 02:10 | 0.14872 | 150.1595
29.4306 | 2018-12-13 02:20 | 0.16534 | 120.1317
29.4375 | 2018-12-13 02:30 | 0.13897 | 76.2637
29.4444 | 2018-12-13 02:40 | 0.19054 | 30.6028
29.4514 | 2018-12-13 02:50 | 0.2348 | 37.2115
29.4583 | 2018-12-13 03:00 | 0.30157 | 21.8014
29.4653 | 2018-12-13 03:10 | 0.30157 | 21.8014
29.4722 | 2018-12-13 03:20 | 0.48915 | 15.6558
29.4792 | 2018-12-13 03:30 | 0.47074 | 10.4028
29.4861 | 2018-12-13 03:40 | 0.52823 | 12.3523
29.4931 | 2018-12-13 03:50 | 0.62654 | 13.1934
29.5 | 2018-12-13 04:00 | 0.58987 | 14.531
29.5069 | 2018-12-13 04:10 | 0.58987 | 14.531
29.5139 | 2018-12-13 04:20 | 0.73018 | 8.5851
29.5208 | 2018-12-13 04:30 | 0.77953 | 14.4106
29.5278 | 2018-12-13 04:40 | 0.87921 | 11.6806
29.5347 | 2018-12-13 04:50 | 0.72401 | 5.2303
29.5417 | 2018-12-13 05:00 | 0.81666 | 3.6507
29.5486 | 2018-12-13 05:10 | 0.81666 | 3.6507
29.5556 | 2018-12-13 05:20 | 0.68084 | 10.2371
29.5625 | 2018-12-13 05:30 | 0.84327 | 10.1772
29.5694 | 2018-12-13 05:40 | 0.75772 | 13.431
29.5764 | 2018-12-13 05:50 | 0.76305 | 12.4881
29.5833 | 2018-12-13 06:00 | 0.82664 | 4.5794
29.5903 | 2018-12-13 06:10 | 0.82664 | 4.5794
29.5972 | 2018-12-13 06:20 | 0.70414 | 8.1646
29.6042 | 2018-12-13 06:30 | 0.64716 | 8.5308
29.6111 | 2018-12-13 06:40 | 0.66627 | 4.7351
29.6181 | 2018-12-13 06:50 | 0.62897 | 3.1899
29.625 | 2018-12-13 07:00 | 0.68138 | 7.8447
29.6319 | 2018-12-13 07:10 | 0.68138 | 7.8447
29.6389 | 2018-12-13 07:20 | 0.52223 | 6.3765
29.6458 | 2018-12-13 07:30 | 0.36729 | 8.7699
29.6528 | 2018-12-13 07:40 | 0.41911 | 6.9894
29.6597 | 2018-12-13 07:50 | 0.35427 | 4.8577
29.6667 | 2018-12-13 08:00 | 0.29728 | 2.5063
29.6736 | 2018-12-13 08:10 | 0.29728 | 2.5063
29.6806 | 2018-12-13 08:20 | 0.28269 | 15.8062
29.6875 | 2018-12-13 08:30 | 0.10112 | 8.5308
29.6944 | 2018-12-13 08:40 | 0.177 | 329.8135
29.7014 | 2018-12-13 08:50 | 0.038588 | 148.7816
29.7083 | 2018-12-13 09:00 | 0.038013 | 26.565
29.7153 | 2018-12-13 09:10 | 0.038013 | 26.565
29.7222 | 2018-12-13 09:20 | 0.039446 | 210.4655
29.7292 | 2018-12-13 09:30 | 0.102 | 217.4316
29.7361 | 2018-12-13 09:40 | 0.21892 | 185.2418
29.7431 | 2018-12-13 09:50 | 0.15616 | 173.0115
29.75 | 2018-12-13 10:00 | 0.28618 | 185.2126
29.7569 | 2018-12-13 10:10 | 0.28618 | 185.2126
29.7639 | 2018-12-13 10:20 | 0.31281 | 191.0585
29.7708 | 2018-12-13 10:30 | 0.37006 | 189.4878
29.7778 | 2018-12-13 10:40 | 0.41029 | 190.817
29.7847 | 2018-12-13 10:50 | 0.43977 | 189.291
29.7917 | 2018-12-13 11:00 | 0.37553 | 183.0529
29.7986 | 2018-12-13 11:10 | 0.37553 | 183.0529
29.8056 | 2018-12-13 11:20 | 0.46099 | 189.9936
29.8125 | 2018-12-13 11:30 | 0.53413 | 189.3741
29.8194 | 2018-12-13 11:40 | 0.48213 | 176.0753
29.8264 | 2018-12-13 11:50 | 0.52585 | 192.1861
29.8333 | 2018-12-13 12:00 | 0.45575 | 186.2985
29.8403 | 2018-12-13 12:10 | 0.45575 | 186.2985
29.8472 | 2018-12-13 12:20 | 0.56286 | 188.2741
29.8542 | 2018-12-13 12:30 | 0.58159 | 184.24
29.8611 | 2018-12-13 12:40 | 0.49945 | 189.2171
29.8681 | 2018-12-13 12:50 | 0.5214 | 185.5028
29.875 | 2018-12-13 13:00 | 0.52228 | 190.8151
29.8819 | 2018-12-13 13:10 | 0.52228 | 190.8151
29.8889 | 2018-12-13 13:20 | 0.492 | 180.2329
29.8958 | 2018-12-13 13:30 | 0.46699 | 190.6121
29.9028 | 2018-12-13 13:40 | 0.43378 | 183.4363
29.9097 | 2018-12-13 13:50 | 0.36304 | 188.5542
29.9167 | 2018-12-13 14:00 | 0.32145 | 196.631
29.9236 | 2018-12-13 14:10 | 0.32145 | 196.631
29.9306 | 2018-12-13 14:20 | 0.21845 | 176.3255
29.9375 | 2018-12-13 14:30 | 0.11336 | 131.4237
29.9444 | 2018-12-13 14:40 | 0.11054 | 221.3322
29.9514 | 2018-12-13 14:50 | 0.11439 | 148.9503
29.9583 | 2018-12-13 15:00 | 0.065069 | 43.7546
29.9653 | 2018-12-13 15:10 | 0.065069 | 43.7546
29.9722 | 2018-12-13 15:20 | 0.2247 | 22.2276
29.9792 | 2018-12-13 15:30 | 0.24824 | 25.5328
29.9861 | 2018-12-13 15:40 | 0.26545 | 20.2782
29.9931 | 2018-12-13 15:50 | 0.28763 | 25.3178