## Info
Operator: | Yorkshire Water
Permit Ref: | FB3809MM
Site: | Knostrop STF
Date: | 2022-05-26
Full Waste Treatment BREF
Waste Treatment BAT Conclusions
This document has been compiled as a tool to help clearly identify where there may be gaps in complying with the Waste Treatment BAT conclusions. The information contained only relates to:
General BAT conclusions
General BAT conclusions for the biological treatment of waste
BAT conclusions for the aerobic treatment of waste
BAT conclusions for the anaerobic treatment of waste
BAT conclusions for the mechanical biological treatment (MBT) of waste
BAT conclusions for the physico-chemical treatment of solid and/or pasty waste
Additional BAT conclusions may apply depending on the operations carried out.
It can be used by applicants/operators or EA officers but is not a substitution for the official BAT documents or other official Environment Agency guidance.

## BAT Conclusions
BAT No. | Topic | Brief Description | BAT | Applicable BAT- AEL | Compliant now? | Derogation needed? | Provide brief comments on how compliance with BAT is (or will be) achieved Where "N/A" or "other" is given, please explain why
General BAT conclusions
1 | Overall performance | EMS Applicability The scope (e.g. level of detail) and nature of the EMS (e.g. standardised or non-standardised) will generally be related to the nature, scale and complexity of the installation, and the range of environmental impacts it may have (determined also by the type and amount of wastes processed). | In order to improve the overall environmental performance, BAT is to implement and adhere to an environmental management system (EMS) that incorporates all of the following features:
|  |  | i) commitment of the management, including senior management; |  | Yes | No | Yes, this is an integral part of the ISO 14001 system. Refer to Section III: Supporting Information, Form C2, Question 3d Management systems
|  |  | ii) definition, by the management, of an environmental policy that includes the continuous improvement of the environmental performance of the installation; |  | Yes | No | Yes, this is an integral part of the ISO 14001 system. Refer to Section III: Supporting Information, Form C2, Question 3d Management systems
|  |  | iii) planning and establishing the necessary procedures, objectives and targets, in conjunction with financial planning and investment; |  | Yes | No | Yes, this is an integral part of the ISO 14001 system. Refer to Section III: Supporting Information, Form C2, Question 3d Management systems
|  |  | iv) implementation of procedures paying particular attention to: (a) structure and responsibility, (b) recruitment, training, awareness and competence (c) communication, (d) employee involvement, (e) documentation, (f) effective process control, (g) maintenance programmes, (h) emergency preparedness and response, (i) safeguarding compliance with environmental legislation; |  | Yes | No | Yes, this is an integral part of the ISO 14001 system. Refer to Section III: Supporting Information, Form C2, Question 3d Management systems
|  |  | v) checking performance and taking corrective action, paying particular attention to: (a) monitoring and measurement (see also the JRC Reference Report on Monitoring of emissions to air and water from IED installations – ROM), (b) corrective and preventive action, (c) maintenance of records, (d) independent (where practicable) internal or external auditing in order to determine whether or not the EMS conforms to planned arrangements and has been properly implemented and maintained; |  | Yes | No | Yes, this is an integral part of the ISO 14001 system. Refer to Section III: Supporting Information, Form C2, Question 3d Management systems
|  |  | vi) review, by senior management, of the EMS and its continuing suitability, adequacy and effectiveness; |  | Yes | No | Yes, this is an integral part of the ISO 14001 system. Refer to Section III: Supporting Information, Form C2, Question 3d Management systems
|  |  | vii) following the development of cleaner technologies; |  | Yes | No | The Innovations Team at YW undertakes regular monitoring and review of new and innovative technologies and equipment to ensure the business continually improves its operations and activities. This includes consideration of cleaner technologies and improved environmental performance. Refer to Section III: Supporting Information, Form C2, Question 3d Management systems
|  |  | viii) consideration for the environmental impacts from the eventual decommissioning of the plant at the stage of designing a new plant, and throughout its operating life; |  | Yes | No | Yes, this is an integral part of the ISO 14001 system. Refer to Section III: Supporting Information, Form C2, Question 3d Management systems
|  |  | ix) application of sectoral benchmarking on a regular basis; |  | Yes | No | Yes, sectoral and cross-sector benchmarking also takes place as required. Refer to Section III: Supporting Information, Form C2, Question 3d Management systems
|  |  | x) waste stream management (see BAT 2); |  | Yes | No | ISO 14001 system. Refer to Section III: Supporting Information, Form C2, Question 3d Management systems. See also BAT 2 below.
|  |  | xi) an inventory of waste water and waste gas streams (see BAT 3); |  | Yes | No | Yes, this is an integral part of the ISO 14001 system. Refer to Section III: Supporting Information, Form C2, Question 3d Management systems. See also BAT 3 below.
|  |  | xii) residues management plan (see description in Section 6.5); |  | Yes | No | Yes, this is an integral part of the ISO 14001 system. Refer to Section III: Supporting Information, Form C2, Question 3d Management systems and also information provided in response to Form C3, Question 6.
|  |  | xiii) accident management plan (see description in Section 6.5); |  | Yes | No | This is provided in response to Section III: Supporting Information, Form C2, Question 6-5
2 | Overall performance | Improvement of overall environmental performance | In order to improve the overall environmental performance of the plant, BAT is to use all of the techniques given below.
|  |  | a) Set up and implement waste characterisation and pre-acceptance procedures |  | Yes | No | Refer to Section II: Technical Description and Section III: Supporting Information, Form C2, Question 3d Management systems (sub-section 'Waste Characterisation (Pre-acceptance and Acceptance). All sludges arriving at Knostrop STF are either indigenous primary and secondary sludges from the Knostrop WwTW or imported sludge and sludge cake from other YW sites. The volume and source of imports to the site is recorded by WaSP loggers.
|  |  | b) Set up and implement waste acceptance procedures |  | Yes | No | Refer to Section II: Technical Description and Section III: Supporting Information, Form C2, Question 3d Management systems and comments noted above.
|  |  | c) Set up and implement a waste tracking system and inventory |  | Yes | No | Refer to Section II: Technical Description and Section III: Supporting Information, Form C2, Question 3d Management systems and comments noted above.
|  |  | d) Set up and implement an output quality management system |  | Yes | No | Refer to Section II: Technical Description and Section III: Supporting Information, Form C2, Question 3d Management systems. HACCP processes are in place to manage and maintain the quality of digested sludge to ensure its suitability for land spreading.
|  |  | e) Ensure waste segregation |  | N/A (explain) | No | Waste received on site comprises only sewage sludge. Waste segregation, sorting and waste compatibility considerations are not relevant
|  |  | f) Ensure waste compatibility prior to mixing or blending of waste |  | N/A (explain) | No | Waste received on site comprises only sewage sludge. Waste segregation, sorting and waste compatibility considerations are not relevant
|  |  | g) Sort incoming solid waste |  | N/A (explain) | No | Waste received on site comprises only sewage sludge. Waste segregation, sorting and waste compatibility considerations are not relevant
3 | Overall performance | Inventory Applicability The scope (e.g. level of detail) and nature of the inventory will generally be related to the nature, scale and complexity of the installation, and the range of environmental impacts it may have (determined also by the type and amount of wastes processed). | In order to facilitate the reduction of emissions to water and air, BAT is to establish and to maintain an inventory of waste water and waste gas streams, as part of the environmental management system (see BAT 1), that incorporates all of the following features:
|  |  | (i) information about the characteristics of the waste to be treated and the waste treatment processes, including: (a) simplified process flow sheets that show the origin of the emissions; (b) descriptions of process-integrated techniques and waste water/waste gas treatment at source including their performances; |  | Yes | No | Refer to Section II: Technical Description and Section III: Supporting Information, Form C3, Question 2 Point source emissions to air, water and land
|  |  | (ii) information about the characteristics of the waste water streams, such as: (a) average values and variability of flow, pH, temperature, and conductivity; (b) average concentration and load values of relevant substances and their variability (e.g. COD/TOC, nitrogen species, phosphorus, metals, priority substances/micropollutants); (c) data on bioeliminability (e.g. BOD, BOD to COD ratio, Zahn-Wellens test, biological inhibition potential (e.g. inhibition of activated sludge)) (see BAT 52); |  | Other (explain) | No | All liquor from sludge thickening and dewatering processes, condensate (e.g. from biogas handling), cleaning / washdown effluent and the majority of surface water runoff (i.e. that which is not discharged via a soakaway) is collected and discharged via underground drainage systems to Knostrop WwTW for full treatment prior to discharge to to Wyke Beck and the River Aire. Knostrop WwTW treats these discharges effectively and has a history of compliance with conditions contained within its discharge permit. As both Knostrop STF and Knostrop WwTW are owned and operated by YW, separate monitoring of Knostrop STF discharges has not been necessary or required under any permitting regime. YW do not currently undertake any routine monitoring of these discharges (other than checks for process control purposes) and therefore the data referred to here is not currently available. YW recognises that there is a change in permitting regime and therefore commits to undertake initially a one-off programme of monitoring return liquors from emissions points S1, S2 and S3, or from a combined and representative sampling location, in order to obtain further information about the characteristics of the waste streams. The monitoring programme will comprise collection of quarterly wastewater samples from each emission point over a 12 month period (in case of any seasonal variation). YW will design a suite of monitoring determinands and submit to the Environment Agency for approval prior to undertaking the first analysis.
|  |  | (iii) information about the characteristics of the waste gas streams, such as: (a) average values and variability of flow and temperature; (b) average concentration and load values of relevant substances and their variability (e.g. organic compounds, POPs such as PCBs); (c) flammability, lower and higher explosive limits, reactivity; (d) presence of other substances that may affect the waste gas treatment system or plant safety (e.g. oxygen, nitrogen, water vapour, dust). |  | Yes | No | Refer to Section II: Technical Description and Section III: Supporting Information, Form C3, Question 2 Point source emissions to air, water and land
4 | Overall performance | Techniques for storage of waste | In order to reduce the environmental risk associated with the storage of waste, BAT is to use all of the techniques given below.
|  |  | a) Optimised storage location |  | Yes | No | Refer to Section II: Technical Description and Section III: Supporting Information, Form C3, Question 6e Describe how you avoid producing waste in line with Council Directive 2008/98/EC on waste. Waste materials are stored on site for the minimum period of time, in suitable, fit for purpose containers located on areas of hardstanding and away from sensitive receptors.
|  |  | b) Adequate storage capacity |  | Yes | No | Refer to Section II: Technical Description and Section III: Supporting Information, Form C3, Question 6e Describe how you avoid producing waste in line with Council Directive 2008/98/EC on waste. Waste materials are stored on site for the minimum period of time, in suitable, fit for purpose containers located on areas of hardstanding and away from sensitive receptors.
|  |  | c) Safe storage operation |  | Yes | No | Refer to Section II: Technical Description and Section III: Supporting Information, Form C3, Question 6e Describe how you avoid producing waste in line with Council Directive 2008/98/EC on waste. Waste materials are stored on site for the minimum period of time, in suitable, fit for purpose containers located on areas of hardstanding and away from sensitive receptors.
|  |  | d) Separate area for storage and handling of packaged hazardous waste |  | Yes | No | Refer to Section II: Technical Description and Section III: Supporting Information, Form C3, Question 6e Describe how you avoid producing waste in line with Council Directive 2008/98/EC on waste. Very limited quantities of hazardous waste are generated by site activities. These are segregated and stored in suitable, fit for purpose containers.
5 | Overall performance | Techniques for handling and transfer of waste | In order to reduce the environmental risk associated with the handling and transfer of waste, BAT is to set up and implement handling and transfer procedures. |  | Yes | No | Refer to Section II: Technical Description and Section III: Supporting Information, Form C3, Question 6e Describe how you avoid producing waste in line with Council Directive 2008/98/EC on waste and Section III: Supporting Information, Form C2, Question 3d Management systems. Waste procedures are included within the YW management system and training is provided to staff as required.
6 | Monitoring | Waste water - Monitor key parameters | For relevant emissions to water as identified by the inventory of waste water streams (see BAT 3), BAT is to monitor key process parameters (e.g. waste water flow, pH, temperature, conductivity, BOD) at key locations (e.g. at the inlet and/or outlet of the pre-treatment, at the inlet to the final treatment, at the point where the emission leaves the installation). |  | N/A (explain) | NA | No direct emissions to water other than uncontaminated roofwater runoff from two buildings which is isolated from other wastewater sources and is discharged to soakaway. No monitoring of these emissions is proposed or required. All other wastewater is returned to Knostrop WwTW for full treatment prior to discharge.
7 | Monitoring | Waste water - Monitoring frequencies and standards | BAT is to monitor emissions to water with at least the frequency given below, and in accordance with EN standards. If EN standards are not available, BAT is to use ISO, national or other international standards that ensure the provision of data of an equivalent scientific quality. | See 'Water emissions tables' tab | Other (explain) | Yes | There are no direct emissions to water other than clean rainwater runoff from the thickener and control building roofs which is discharged to soakaway. All liquor from sludge thickening and dewatering processes, condensate (e.g. from biogas handling), cleaning / washdown effluent and the majority of surface water runoff is collected and discharged via underground drainage systems to Knostrop WwTW for full treatment prior to discharge to to Wyke Beck and the River Aire. Knostrop WwTW treats these discharges effectively and has a history of compliance with conditions contained within its discharge permit. As both Knostrop STF and Knostrop WwTW are owned and operated by YW, separate monitoring of Knostrop STF discharges has not been necessary or required under any permitting regime. YW has committed to undertake a 12-month programme of characterisation monitoring. Until this has been completed no long term routine monitoring strategy can be established. YW therefore requires a short term derogation as a minimum. YW will continue to monitor discharges from Knostrop WwTW outfall in accordance with permit conditions.
8 | Monitoring | Channelled air emissions - Monitoring frequencies and standards | BAT is to monitor channelled emissions to air with at least the frequency given below, and in accordance with EN standards. If EN standards are not available, BAT is to use ISO, national or other international standards that ensure the provision of data of an equivalent scientific quality. | See 'Air emissions tables' tab | No - but will be by August 2022 | No | Odour monitoring programmes specified in Appendix 10 Odour Management Plan. YW proposes to monitor NH3 and H2S from the OCU stack on a 6-monthly basis.
9 | Monitoring | Diffuse emissions - Monitor organic compounds | BAT is to monitor diffuse emissions of organic compounds to air from the regeneration of spent solvents, the decontamination of equipment containing POPs with solvents, and the physico-chemical treatment of solvents for the recovery of their calorific value, at least once per year using one or a combination of the techniques given below. |  | N/A (explain) | NA | Relevant activities are not carried out at this site.
|  |  | a) Measurement |  | N/A (explain) | NA | Relevant activities are not carried out at this site.
|  |  | b) Emissions factors |  | N/A (explain) | NA | Relevant activities are not carried out at this site.
|  |  | c) Mass balance |  | N/A (explain) | NA | Relevant activities are not carried out at this site.
10 | Monitoring | Odour - Monitor emissions Applicability The applicability is restricted to cases where an odour nuisance at sensitive receptors is expected and/or has been substantiated. | BAT is to periodically monitor odour emissions. (The monitoring frequency is determined in the odour management plan (see BAT 12).) |  | Yes | No | Odour monitoring programmes, are established within the Odour Management Plan. See Section V: Appendix 10 Odour Management Plan.
11 | Monitoring | Monitor annual consumption and generation of waste outputs | BAT is to monitor the annual consumption of water, energy and raw materials as well as the annual generation of residues and waste water, with a frequency of at least once per year. |  | Yes | No | Refer to Section II: Technical Description and Section III: Supporting Information, Form C2, Question 3d Management systems (sub-section 'Monitoring') and Form C3, Questions 6a, b, c, d and e
12 | Emissions to air | Odour Management Plan Applicability The applicability is restricted to cases where an odour nuisance at sensitive receptors is expected and/or has been substantiated. | In order to prevent or, where that is not practicable, to reduce odour emissions, BAT is to set up, implement and regularly review an odour management plan, as part of the environmental management system (see BAT 1), that includes all of the following elements: — a protocol containing actions and timelines; — a protocol for conducting odour monitoring as set out in BAT 10; — a protocol for response to identified odour incidents, e.g. complaints; —an odour prevention and reduction programme designed to identify the source(s); to characterise the contributions of the sources; and to implement prevention and/or reduction measures. |  | Yes | No | Refer to Section V: Appendix 10: Odour Management Plan
13 | Emissions to air | Odour reduction techniques | In order to prevent or, where that is not practicable, to reduce odour emissions, BAT is to use one or a combination of the techniques given below. |  | Yes | No | Refer to Section V: Appendix 10: Odour Management Plan
|  |  | a) Minimising residence times |  | Yes | No | Refer to Section V: Appendix 10: Odour Management Plan
|  |  | b) Using chemical treatment |  | Yes | No | Refer to Section V: Appendix 10: Odour Management Plan. Chemical treatment is not routinely used but could be considered in order to respond to an abnormal / significant odour issue.
|  |  | c) Optimising aerobic treatment |  | N/A (explain) | NA | Relevant activities are not carried out at this site.
14 | Emissions to air | Diffuse emission reduction techniques | In order to prevent or, where that is not practicable, to reduce diffuse emissions to air, in particular of dust, organic compounds and odour, BAT is to use an appropriate combination of the techniques given below. Depending on the risk posed by the waste in terms of diffuse emissions to air, BAT 14d is especially relevant.
|  |  | a) Minimising the number of potential diffuse emission sources |  | Yes | No | BAT in place (where applicable to site activities). All significant sources of diffuse emisisons are covered. Refer to Section II: Technical Description, Section III Supporting Information, Form C3, Question 3b General Requirements – LDAR programme, Section V: Appendix 8 Odour Risk Assessment, and Section V: Appendix 10 Odour Management Plan.
|  |  | b) Selection and use of high- integrity equipment |  | Yes | No | Plant is compliant with YW engineering standards and subject to ongoing formal inspection and maintenance regimes.
|  |  | c) Corrosion prevention |  | Yes | No | Plant is compliant with YW engineering standards and subject to ongoing formal inspection and maintenance regimes.
|  |  | d) Containment, collection and treatment of diffuse emissions |  | Other (explain) | Yes | All tanks and vessels that are considered to be significant sources of diffuse emissions are covered, extracted and treated in a two-stage OCU. An impact assessment of diffuse emissions for the remaining, uncovered vessels (including the dewatering feed tank and tanks associated with the liquor treatment plant) has been undertaken (refer to Diffuse Emissions Risk Assessment). Monitoring data indicates that diffuse emissions are low and the risk assessment concludes that no further mitigation is required. Some further monitoring is however proposed for tanks where data was absent and surrogate data has been used in the risk assessment. No containment, collection or treatment is therefore proposed for these vessels although this will be subject to ongoing review as part of the OMP, which includes a commitment to process monitoring and field olfactometry to ensure no residual impacts arise.
|  |  | e) Dampening |  | N/A (explain) | NA | Materials are already wet or liquid
|  |  | f) Maintenance |  | Yes | No | Planned maintenance systems in place. Refer to Section II: Technical Description and Section III: Supporting Information, Form C2, Question 3d Management systems. LDAR in place - refer to Form C3, Question 3b.
|  |  | g) Cleaning of waste treatment and storage areas |  | Yes | No | Regular cleaning is undertaken, where required and appropriate
|  |  | h) Leak detection and repair (LDAR) programme |  | Yes | No | Form C3, Question 3b General Requirements – LDAR programme
15 | Emissions to air | Flare use minimisation techniques | BAT is to use flaring only for safety reasons or for non-routine operating conditions (e.g. start-ups, shutdowns) by using both of the techniques given below.
|  |  | a) correct plant design |  | Yes | No | Refer to Section II: Technical Description (sub-section Biogas Storage and Use)
|  |  | b) Plant management |  | Yes | No | Refer to Section II: Technical Description (sub-section Biogas Storage and Use)
16 | Emissions to air | Flare emissions minimisation techniques | In order to reduce emissions to air from flares when flaring is unavoidable, BAT is to use both of the techniques given below.
|  |  | a) Correct design of flaring devices |  | Yes | No | Refer to Section II: Technical Description (sub-section Biogas Storage and Use)
|  |  | b) Monitoring and recording as part of flare management |  | Yes | No | Refer to Form C3, Question 4 Monitoring, Table C3: 4a-1 and 4a-2 .
17 | Noise and vibrations | Noise management plan Applicability The applicability is restricted to cases where a noise or vibration nuisance at sensitive receptors is expected and/or has been substantiated. | In order to prevent or, where that is not practicable, to reduce noise and vibration emissions, BAT is to set up, implement and regularly review a noise and vibration management plan, as part of the environmental management system (see BAT 1), that includes all of the following elements: |  | N/A (explain) | NA | Noise or vibration nuisance at sensitive receptors is not expected and no substantiated noise and vibration nuisance complaints have been received. Noise and vibration management plan not required. Refer to Section V: Appendix 9 - Noise impact assessment. Complaints handling and response procedures are in place – refer to Section III: Supporting Information, Form C2, Question 3d Management systems.
|  |  | i) a protocol containing appropriate actions and timelines; |  | N/A (explain) | NA | See above
|  |  | ii) a protocol for conducting noise and vibration monitoring; |  | N/A (explain) | NA | See above
|  |  | iii) a protocol for response to identified noise and vibration events, e.g. complaints; |  | N/A (explain) | NA | See above
|  |  | iv) a noise and vibration reduction programme designed to identify the source(s), to measure/estimate noise and vibration exposure, to characterise the contributions of the sources and to implement prevention and/or reduction measures. |  | N/A (explain) | NA | See above
18 | Noise and vibrations | Noise and vibration reduction techniques | In order to prevent or, where that is not practicable, to reduce noise and vibration emissions, BAT is to use one or a combination of the techniques given below. |  | Yes | No | Noise is minimised using a combination of techniques appropriate to the nature of installation activities and the risk of noise nuisance. Refer to Section V: Appendix 9 Noise impact assessment.
|  |  | a) Appropriate location of equipment and buildings |  | Yes | No | See above.
|  |  | b) Operational measures |  | Yes | No | See above
|  |  | c) Low-noise equipment |  | Yes | No | See above
|  |  | d) Noise and vibration control equipment |  | Yes | No | See above
|  |  | e) noise attenuation |  | Yes | No | See above
19 | Emissions to water | Water management techniques | In order to optimise water consumption, to reduce the volume of waste water generated and to prevent or, where that is not practicable, to reduce emissions to soil and water, BAT is to use an appropriate combination of the techniques given below.
|  |  | a) water management |  | Yes | No | Measures are in place to ensure that water is used only where necessary, and preference is given to the use of final treated effluent rather than mains water. Refer to Section III: Supporting Information, Form C3, Question 6d Explain and justify the raw and other materials, other substances and water that you will use.
|  |  | b) water recirculation |  | N/A (explain) | No | Relevant activities are not carried out at this site. Measures are in place to ensure that water is used only where necessary, and preference is given to the use of final treated effluent rather than mains water.
|  |  | c) impermeable surface |  | Yes | No | For details of techniques to minimise accidental/unplanned discharges to the environment from surfacing, storage areas, tanks, vessels, drainage systems etc refer to the Accident Management Plan (Form C2, Q 6-7), Appendix 5: Site Condition Report and Appendix 11: Secondary Containment Risk Assessment.
|  |  | d) Techniques to reduce the likelihood and impact of overflows and failures from tanks and vessels |  | Other (explain) | No | Refer to Secondary Containment Risk Assessment (version 2, as revised 9/6/2022). A secondary containment risk assessment has been undertaken to assess whether existing measures to protect the environment in the event of a failure of containment of primary storage tanks are adequate. This assessment has concluded that further measures are required in order to provide an adequate level of environmental protection in the event of tank overflow or failure. YW will implement the required improvements and therefore no long term derogation is necessary.
|  |  | e) Roofing of waste storage and treatment areas |  | Yes | No | Digested sludge cake is transferred from the centrifuges onto the cake pad. Whilst the drop zone area is not covered by a roof (due to the height of the conveyor used to transfer sludge from the centrifuges), the digested sludge cake is then moved to a roofed cake barn where it is held prior to transfer off site.
|  |  | f) Segregation of water streams |  | Yes | No | In order to reduce pollution risks most rainwater runoff is collected and returned to Knostop WwTW for treatment, in addition to process liquors and cleaning washwater etc. Roofwater runoff is limited due to small number/surface area of buildings within the installation boundary. However, roofwater from two buildings is discharged via soakaway. Refer to Section III: Supporting Information, Form C3, Question 2 Point source emissions to air, water and land.
|  |  | g) Adequate drainage infrastructure |  | Yes | No | All process liquors, cleaning washwater and surface water runoff from areas of the site where there is a risk of contamination (such as the sludge cake drop zone area) are returned to Knostrop WwTW for treatment. Refer to Section III: Supporting Information, Form C3, Question 2 Point source emissions to air, water and land and Figure 4: Drainage Plan.
|  |  | h) Design and maintenance provisions to allow detection and repair of leaks |  | Yes | No | Measures are in place for the protection of land and groundwater during operation of the permit - refer to Appendix 5: Site Condition Report
|  |  | i) Appropriate buffer storage capacity |  | Yes | No | Wastewater is returned for treatment at the co-located Knostrop WwTW where there is adequate buffer storage capacity.
20 | Emissions to water | Water emission reduction techniques | In order to reduce emissions to water, BAT is to treat waste water using an appropriate combination of the techniques given below. | See 'Water emissions tables' tab |  |  | Process liquor, including surface water runoff is directed to Knostrop WwTW for full treatment. Refer to Section II: Technical Description and Section III: Supporting Information, Form C3, Question 2 Point source emissions to air, water and land
|  |  | a) equalisation |  | Yes | No | There is a centrate balance tank located prior to the STF LTP. Wastewater flow from the STF is mixed with UWwTD wastewater (outside of the installation in the wider WwTW), providing adequate balancing of flow and composition.
|  |  | b) neutralisation |  | Yes | No | Sulphuric acid is dosed prior to the LTP in order to provide suitable conditions to optimise bacterial activity. No further neutralisation is required at Knostrop WwTW.
|  |  | c) Physical separation, e.g. screens, sieves, grit separators, grease separators, oil- water separation or primary settlement tanks |  | Yes | No | Sludge screens are located within the STF. UWWTD flow is screened at Knostrop WwTW.
|  |  | d) adsorption |  | N/A (explain) | No | Not applicable - treatment processes in place ensure that discharge permit conditions are met.
|  |  | e) distillation/rectification |  | N/A (explain) | No | Not applicable - treatment processes in place ensure that discharge permit conditions are met.
|  |  | f) precipitation |  | N/A (explain) | No | Not applicable - treatment processes in place ensure that discharge permit conditions are met.
|  |  | g) chemical oxidation |  | N/A (explain) | No | Not applicable - treatment processes in place ensure that discharge permit conditions are met.
|  |  | h) chemical reduction |  | N/A (explain) | No | Not applicable - treatment processes in place ensure that discharge permit conditions are met.
|  |  | i) evaporation |  | N/A (explain) | No | Not applicable - treatment processes in place ensure that discharge permit conditions are met.
|  |  | j) ion exchange |  | N/A (explain) | No | Not applicable - treatment processes in place ensure that discharge permit conditions are met.
|  |  | k) stripping |  | N/A (explain) | No | Not applicable - treatment processes in place ensure that discharge permit conditions are met.
|  |  | l) activated sludge process |  | Yes | No | Undertaken at Knostrop WwTW
|  |  | m) membrane bioreactor |  | N/A (explain) | No | Not applicable - treatment processes in place ensure that discharge permit conditions are met.
|  |  | n) Nitrification/denitrification when the treatment includes a biological treatment |  | Yes | No | Undertaken at the LTP within the STF installation
|  |  | o) coagulation and flocculation |  | N/A (explain) | No | Not applicable - treatment processes in place ensure that discharge permit conditions are met.
|  |  | p) sedimentation |  | Yes | No | Primary settlement tanks at Knostrop WwTW enable solids settlement to occur.
|  |  | q) Filtration (e.g. sand filtration, microfiltration, ultrafiltration) |  | N/A (explain) | No | Not applicable - treatment processes in place ensure that discharge permit conditions are met.
|  |  | r) floatation |  | N/A (explain) | No | Not applicable - treatment processes in place ensure that discharge permit conditions are met.
21 | Emissions from accidents and incidents | Prevention and limitation techniques | In order to prevent or limit the environmental consequences of accidents and incidents, BAT is to use all of the techniques given below, as part of the accident management plan (see BAT 1). |  | Yes | No | Refer to Accident Management Plan Table C2: 6-5.
|  |  | a) protection measures |  | Yes | No | Refer to Accident Management Plan Table C2: 6-5.
|  |  | b) Management of incidental/accidental emissions |  | Yes | No | Refer to Accident Management Plan Table C2: 6-5.
|  |  | c) Incident/accident registration and assessment system |  | Yes | No | Refer to Accident Management Plan Table C2: 6-5.
22 | Material efficiency | Material efficiency Applicability Some applicability limitations derive from the risk of contamination posed by the presence of impurities (e.g. heavy metals, POPs, salts, pathogens) in the waste that substitutes other materials. Another limitation is the compatibility of the waste substituting other materials with the waste input (see BAT 2). | In order to use materials efficiently, BAT is to substitute materials with waste. |  | Yes | No | Opportunities to substitute materials with waste are very limited. However, treated final effluent is used in preference to mains water supply wherever feasible. Refer also to Section III: Supporting Information, Form C3, Question 6e.
23 | Energy efficiency | Energy efficiency techniques | In order to use energy efficiently, BAT is to use both of the techniques given below. |  | Yes | No | Refer to Section III: Supporting Information, Form C3, Question 6a and 6b
|  |  | a) energy efficient plant |  | Yes | No | Refer to Section III: Supporting Information, Form C3, Question 6a and 6b
|  |  | b) energy balance record |  | Yes | No | Refer to Section III: Supporting Information, Form C3, Question 6a and 6b
24 | Reuse of packaging | Reuse of packaging Applicability Some applicability restrictions derive from the risk of contamination of the waste posed by the reused packaging. | In order to reduce the quantity of waste sent for disposal, BAT is to maximise the reuse of packaging, as part of the residues management plan (see BAT 1). |  | Yes | No | Limited opportunities exist as packaging waste arisings are very low. Refer to Section III: Supporting Information, Form C3, Question 6e for further information about residues management
General BAT conclusions for the biological treatment of waste
33 | Overall performance |  | In order to reduce odour emissions and to improve the overall environmental performance, BAT is to select the waste input. |  | Yes | No | Waste is only received from YW WwTW. Refer to Section II: Technical Description and Section III: Supporting Information, Form C2, Question 3d Management systems. Refer also to BAT 2 above.
34 | Emissions to air |  | In order to reduce channelled emissions to air of dust, organic compounds and odorous compounds, including H2S and NH3, BAT is to use one or a combination of the techniques given below. | See 'Air emissions tables' tab | Other (explain) | Yes | Displaced air from most sources on site is extracted and treated via a two-stage OCU (biofilter followed by carbon adsorption scrubber). The OCU has the design capability to meet the BAT emissions limit. The digested sludge cake, dewatering feed tank and liquor treatment plant tanks (balance tank, reactors and settlement tanks) are not currently covered and extracted to an OCU. Odour emissions from digested sludge sources such as the dewatering feed tank are lower and no further abatement is considered necessary (refer to Odour Risk Assessment and Diffuse Emissions Risk Assessment). Monitoring data indicates that odour emissions from sources associated with the liquor treatment plant tanks are also low and no further abatement is deemed necessary (refer to Odour Risk Assessment and Diffuse Emissions Risk Assessment).
|  |  | a) adsorption - see table 6.1 |  | Yes | No | See above
|  |  | b) biofilter - see table 6.1 |  | Yes |  | See above
|  |  | c) fabric filter - see table 6.1 |  | N/A (explain) |  | See above
|  |  | d) thermal oxidation - see table 6.1 |  | N/A (explain) |  | See above
|  |  | e) wet scrubbing - see table 6.1 |  | N/A (explain) |  | See above
35 | Emissions to water and usage |  | In order to reduce the generation of waste water and to reduce water usage, BAT is to use all of the techniques given below.
|  |  | a) segregation of water streams |  | Yes | No | In order to reduce pollution risks most rainwater runoff is collected and returned to Knostop WwTW for treatment, in addition to process liquors and cleaning washwater etc. Roofwater runoff is limited due to small number/surface area of buildings within the installation boundary. However, roofwater from two buildings is discharged via soakaway. Refer to Section III: Supporting Information, Form C3, Question 2 Point source emissions to air, water and land.
|  |  | b) water recirculation |  | Yes | No | Wastewater is minimised within the constraints of existing plant. Treated final effluent is used in preference to mains water supply wherever feasible.
|  |  | c) minimisation of the generation of leachate |  | Yes | No | Digested sludge is dewatered using centrifuges in order to minimise leachate generation from digested sludge cake. Sludge is contained within tanks and pipework at all other times. Digested sludge cake is held within a roofed cake barn prior to removal from site.
BAT conclusions for the aerobic treatment of waste
36 | Overall environmental performance | control key waste and process parameters | In order to reduce emissions to air and to improve the overall environmental performance, BAT is to monitor and/or control the key waste and process parameters. |  | N/A (explain) | NA | Relevant activities are not carried out at this site.
37 | Odour and diffuse emissions to air | reduce diffuse emissions to air of dust, odour and bioaerosols | In order to reduce diffuse emissions to air of dust, odour and bioaerosols from open-air treatment steps, BAT is to use one or both of the techniques given below. |  | N/A (explain) | NA | Relevant activities are not carried out at this site.
|  |  | a) use of semipermeable membrane covers |  | N/A (explain) | NA | Relevant activities are not carried out at this site.
|  |  | b) adaptation f operations to the meteorological conditions |  | N/A (explain) | NA | Relevant activities are not carried out at this site.
BAT conclusions for the anaerobic treatment of waste
38 | Emissions to air | Monitor and control key waste and process parameters | In order to reduce emissions to air and to improve the overall environmental performance, BAT is to monitor and/or control the key waste and process parameters. |  | Other (explain) | Yes | YW carries out an extensive level of process monitoring (Refer to Section II: Technical Description and Section III: Form C3, Question 4a: Monitoring Table C3: 4a-2 Key process monitoring provision). An exercise is currently being undertaken to ensure we have the correct equipment, instrumentation and that staff are appropriately trained to ensure we are conducting the monitoring in line with BAT 38. Whilst it is hoped this will be in place by August 2022, YW would like to request a short term derogation to enable us to get the equipment and procedures in place in order to attain this BAT.
BAT conclusions for the mechanical biological treatment (MBT) of waste
39 | Emissions to air | Segregation and recirculation of waste gas streams | In order to reduce emissions to air, BAT is to use both of the techniques given below. |  | N/A (explain) | NA | Relevant activities are not carried out at this site.
|  |  | a) segregation of the waste gas streams |  | N/A (explain) | NA | Relevant activities are not carried out at this site.
|  |  | b) recirculation of waste gas |  | N/A (explain) | NA | Relevant activities are not carried out at this site.
BAT conclusions for the physico-chemical treatment of solid and/or pasty waste
40 | Monitor waste input | Monitoring of content of wastes during pre-acceptance and acceptance | In order to improve the overall environmental performance, BAT is to monitor the waste input as part of the waste pre-acceptance and acceptance procedures (see BAT 2). |  | N/A (explain) | NA | Relevant activities are not carried out at this site.
41 | Emissions to air | Abatement systems and BAT-AELS | In order to reduce emissions of dust, organic compounds and NH3 to air, BAT is to apply BAT 14d and to use one or a combination of the techniques given below. | See 'Air emissions tables' tab | N/A (explain) | NA | Relevant activities are not carried out at this site.
a) adsorption - see section 6.1
b) biofilter - see section 6.1
c) fabric filter - see section 6.1
d) wet scrubbing - see section 6.1

## Water emission tables
This information only shows monitoring and AELs associated with certain treatments
BAT 7
Monitoring emissions to water
| Substance/parameter | Standard(s) | Waste treatment process | Minimum monitoring frequency (11)(12) | Monitoring associated with
| Chemical oxygen demand (COD) (15) (16) | No EN standard available | All waste treatments except treatment of water-based liquid waste | Once every month | BAT 20
| Arsenic (As), Cadmium (Cd), Chromium (Cr), Copper (Cu), Nickel (Ni), Lead (Pb), Zinc (Zn) (13) (14) | Various EN standards available (e.g. EN ISO 11885, EN ISO 17294-2, EN ISO 15586) | Mechanical bilogical treatment of waste, Physico-chemical treatment of solid and/or pasty waste | Once every month
| Mercury (Hg) (13) (14) | Various EN standards available (i.e. EN ISO 17852, EN ISO 12846) | Mechanical bilogical treatment of waste, Physico-chemical treatment of solid and/or pasty waste | Once every month
| PFOA (13) | No EN standard available | All waste treatments | Once every six months
PFOS (13)
| Total nitrogen (Total N) (16) | EN 12260, EN ISO 11905-1 | Biological treatment of waste | Once every month
| Total organic carbon (TOC) (15) (16) | EN 1484 | All waste treatments except treatment of water-based liquid waste | Once every month
| Total phosphorus (Total P) (16) | Various EN standards available (i.e. EN ISO 15681-1 and -2, EN ISO 6878, EN ISO 11885) | Biological treatment of waste | Once every month
| Total suspended solids (TSS) (16) | EN 872 | All waste treatments except treatment of water-based liquid waste | Once every month
(11) Monitoring frequencies may be reduced if the emission levels are proven to be sufficiently stable.
(12) In the case of batch discharge less frequent than the minimum monitoring frequency, monitoring is carried out once per batch.
(13) The monitoring only applies when the substance concerned is identified as relevant in the waste water inventory mentioned in BAT 3.
(14) In the case of an indirect discharge to a receiving water body, the monitoring frequency may be reduced if the downstream waste water treatment plant abates the pollutants concerned.
(15) Either TOC or COD is monitored. TOC is the preferred option, because its monitoring does not rely on the use of very toxic compounds.
(16) The monitoring applies only in the case of a direct discharge to a receiving water body.
BAT 20
Table 6.1 BAT-associated emission levels (BAT-AELs) for direct discharges to a receiving water body
| Substance/Parameter | BAT-AEL (24) | Waste treatment process to which the BAT-AEL applies
| Total organic carbon (TOC) (25) | 10-60 mg/l | All waste treatments except treatment of water-based liquid waste
| Chemical oxygen demand (COD) (25) | 30-180 mg/l | All waste treatments except treatment of water-based liquid waste
| Total suspended solids (TSS) | 5-60 mg/l | All waste treatments
| Total nitrogen (Total N) | 1-25 mg/l (28) (29) | Biological treatment of waste
| Total phosphorus (Total P) | 0.3-2 mg/l | Biological treatment of waste
|  | 1-3 mg/l (27) | Treatment of water-based liquid waste
| Metals and metalliods (31) |  | Mechanical bilogical treatment of waste, Physico-chemical treatment of solid and/or pasty waste
| Arsenic (expressed as As) | 0.01 - 0.05 mg/l
| Cadmium (expressed as Cd) | 0.01 - 0.05 mg/l
| Chromium (expressed as Cr) | 0.01 - 0.15 mg/l
| Copper (expressed as Cu) | 0.05 - 0.5 mg/l
| Lead (expressed as Pb) | 0.05 - 0.1 mg/l (32)
| Nickel (expressed as Ni) | 0.05 - 0.5 mg/l
| Mercury (expressed as Hg) | 0.5 - 5 ug/l
| Zinc (expressed as Zn) | 0.1 - 1 mg/l (33)
(24) The averaging periods are defined in the General considerations.
(25) Either the BAT-AEL for COD or the BAT-AEL for TOC applies. TOC monitoring is the preferred option because it does not rely on the use of very toxic compounds.
(27) The BAT-AEL may not apply to plants treating drilling muds/cuttings.
(28) The BAT-AEL may not apply when the temperature of the waste water is low (e.g. below 12 °C).
(29) The BAT-AEL may not apply in the case of high chloride concentrations (e.g. above 10 g/l in the waste input).
(31) The BAT-AELs only apply when the substance concerned is identified as relevant in the waste water inventory mentioned in BAT 3.
(32) The upper end of the range is 0,3 mg/l for mechanical treatment in shredders of metal waste.
(33) The upper end of the range is 2 mg/l for mechanical treatment in shredders of metal waste.
Table 6.2 BAT-associated emission levels (BAT-AELs) for indirect discharges to a receiving water body
| Substance/Parameter | BAT-AEL (24) | Waste treatment process to which the BAT-AEL applies
| Metals and metalliods (36) |  | Mechanical bilogical treatment of waste, Physico-chemical treatment of solid and/or pasty waste
| Arsenic (expressed as As) | 0.01 - 0.05 mg/l
| Cadmium (expressed as Cd) | 0.01 - 0.05 mg/l
| Chromium (expressed as Cr) | 0.01 - 0.15 mg/l
| Copper (expressed as Cu) | 0.05 - 0.5 mg/l
| Lead (expressed as Pb) | 0.05 - 0.1 mg/l (37)
| Nickel (expressed as Ni) | 0.05 - 0.5 mg/l
| Mercury (expressed as Hg) | 0.5 - 5 ug/l
| Zinc (expressed as Zn) | 0.1 - 1 mg/l (38)
(36) The BAT-AELs only apply when the substance concerned is identified as relevant in the waste water inventory mentioned in BAT 3.
(37) The upper end of the range is 0,3 mg/l for mechanical treatment in shredders of metal waste.
(38) The upper end of the range is 2 mg/l for mechanical treatment in shredders of metal waste.

## Air emission tables
This information only shows monitoring and AELs associated with certain treatments
BAT 8
Monitoring channelled emissions to air
| Substance/ Parameter | Standard(s) | Waste treatment process | Minimum monitoring frequency (17) | Monitoring associated with
| Dust | EN 13284-1 | Mechanical biological treatment of waste | Once every six months | BAT 34
|  |  | Physico-chemical treatment of solid and/or pasty waste | Once every six months | BAT 41
| H2S | No EN standard available | Biological treatment of waste (20) | Once every six months | BAT 34
| NH3 | No EN standard available | Biological treatment of waste (20) | Once every six months | BAT 34
|  |  | Physico-chemical treatment of solid and/or pasty waste (18) | Once every six months | BAT 41
| Odour concentration | EN 13725 | Biological treatment of waste (21) | Once every six months | BAT 34
| TVOC | EN 12619 | Mechanical biological treatment of waste | Once every six months | BAT 34
|  |  | Physico-chemical treatment of solid and/or pasty waste (18) | Once every six months | BAT 41
(17) Monitoring frequencies may be reduced if the emission levels are proven to be sufficiently stable.
(18) The monitoring only applies when the substance concerned is identified as relevant in the waste gas stream based on the inventory mentioned in BAT 3.
(20) The odour concentration may be monitored instead.
(21) The monitoring of NH3 and H2S can be used as an alternative to the monitoring of the odour concentration.
BAT 34
Table 6.7 BAT-associated emission levels (BAT-AELs) for channelled NH3, odour, dust and TVOC emissions to air from the biological treatment of waste
| Parameter | Unit | BAT-AEL (average over sampling period) | Waste treatment process
| NH3 (41) (42) | mg/Nm3 | 0.3 - 20 | All biological treatments of waste
| Odour concentration (41) (2) | ouE/Nm3 | 200 - 1,000
| Dust | mg/Nm3 | 2 - 5 | Mechanical biological treatments of waste
| TVOC | mg/Nm3 | 5 - 40 (43)
(41) Either the BAT-AEL for NH3 or the BAT-AEL for the odour concentration applies.
(42) This BAT-AEL does not apply to the treatment of waste mainly composed of manure.
(43) The lower end of the range can be achieved by using thermal oxidation.
BAT 41
BAT-associated emission level (BAT-AEL) for channelled emissions of dust to air from the physico-chemical treatment of solid and/or pasty waste
| Parameter | Unit | BAT-AEL (Average over the sampling period)
| Dust | mg/Nm3 | 2 - 5
Associated monitoring given in BAT 8

## Picklists (hidden)
Narrative BATCs | Numeric BATCs | Derogation
Yes | Yes | Yes
No - but will be by August 2022 | No - but will be by August 2022 | No
Other (explain) | Other (explain) | NA
N/A (explain) | N/A (explain)
ADD A NOT APPLIC OPTION | for some