## Process Returns
Tonnage
[10 empty] | Imports | 300000
[10 empty] | Indigenous | 2700000
| Imports |  |  |  | Indigenous | [5 empty] | figures above amended in line with application
| Volume | 300000 |  |  | Volume | 2700000 |  |  |  |  | *centrate considered inconsequential and excluded from calculation
| %DS | 2.5% |  |  | %DS | 1.3%
assume 1:1 for t to m3
Thickener
|  |  | Input Volume | 3000000 |  |  | Thickener Return Liquor |  |  | 1945.2055 | Daily digester throughput cf. 259 in application
|  |  | Input %DS | 1.42% |  |  | Volume | 2290000
|  |  | Target Thickness | 6%
|  |  | Volume to digesters | 710000
Cake |  |  | Digester | [6 empty] | What is the total influent volume at Knostrop WwTW? (M3/d)
Volume | 100000 |  | Feed %DS | 6% | [5 empty] | 4.0312 | 213600 | dry weather flow
%DS | 20% |  | %VS | 75% | [5 empty] | 1.5285 | 563328 | fft i.e. max capacity
|  |  | %VS destruction | 45%
|  |  | Output %DS | 3.975%
|  |  | Output Volume | 1022205.8333
|  |  | Centrifuge |  |  |  | Centrifuge Return Liquor (Via Liquor Treatment Plant)
|  |  | Input Volume | 1022205.8333 |  |  | Volume | 852902.9922
|  |  | Input %DS | 3.975%
|  |  | Target Solids | 24%
|  |  | Cake Volume | 169302.8411
[7 empty] | Total Sum (annum) | 3142902.9922 | M3/yr
[7 empty] | Total per day | 8610.6931 | M3/d

## Cake Pad Run off
Cake pad width | 28 | m
Cake pad Length | 90 | m
Cake pad surface area | 2520 | m2
|  |  | Expected cake pad runoff (annum) | 2520000 | Litres | ~ | 6.9041 | M3/d
Average Rainfall (annum) | 1000 | mm
Source: https://www.metoffice.gov.uk/binaries/content/assets/metofficegovuk/pdf/weather/learn-about/uk-past-events/regional-climates/north-east-england_-climate---met-office.pdf
Source: https://www.metoffice.gov.uk/binaries/content/assets/metofficegovuk/pdf/weather/learn-about/uk-past-events/regional-climates/north-east-england_-climate---met-office.pdf
Highest monthly rainfall (mm) | 92 | mm
Daily rainfall (mm) (averaged) | 3.0667 | mm
|  |  | Estimated cake pad runoff per day (based on highest monthly rainfall data) | 7728 | L/d
Cake pad surface area | 2520 | m2
|  |  | Highest run off (cubic metres per day) | 7.728 | M3/d
+
|  |  | Process returns | 8610.6931 | M3/d
=
|  |  | Sum worst case cake pad run off and process returns | 8618.4211 | M3/d

## Application response Figures
3a What is the daily dry weather flow? | 8610.6931 | cubic metres | i.e. figure for liquor returns only shown on K15
3b What is the maximum volume of effluent you will discharge in a day? | 8618.4211 | cubic metres | i.e. process returns (q3a above) plus highest monthly rainfall runoff from cake pad.
3c What is the maximum rate of discharge? | 0.09975 | litres a second | i.e. answer to 3b above divided by (24*60*60). Guidance states that this should be based on 1 in 30 year storm event.
3dWhat is the maximum volume of non‐rainfall dependent effluent you will discharge in a day? | 8610.6931 | cubic metres | i.e. same as 3a
3e What is the maximum rate of rainfall dependent discharge? | 0.09975 | litres a second | i.e. same as 3c