## Sheet1
Noise source corrections to be applied to Linmere SoundPlan source sound power levels
Octave band centre frequency, Hz
Description | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Comments
Louvres with 600mm attenuator | -6 | -9 | -14 | -22 | -36 | -28 | -21 | -15 | applied to 6-Phase - Main Building-Louvre East and 12-Phase - Main Building-Louvre North sources
Louvres with 1800mm attenuator | -12 | -20 | -34 | -50 | -50 | -50 | -49 | -39 | applied to 6-Phase - Main Building-Louvre West and 12-Phase - Main Building-Louvre South sources
Extract fan (Silent-Aire) chute with 1000mm attenuator | 4 | 0 | -13 | -26 | -20 | -14 | -12 | -14 | applied to all EF Chute sources
Extract fan casing (Silent-Aire) | -5 | -11 | -17 | -26 | -28 | -33 | -39 | -44 | applied to all EF Breakout or EF Façade sources
Generator exhaust silencer | -8 | -9 | -12 | -22 | -27 | -27 | -21 | -15 | applied to all Generator Flue sources
Generator cooling air discharge outlet 900mm attenuator | -7 | -13 | -19 | -27 | -41 | -41 | -30 | -22 | applied to all Generator Discharge sources