## Plant Noise Levels
Item | Manufacturer's Lw data | Manufacturer's Lp data | Derived Lw | Quantity | Modelled height | Directivity | Operating time
External
Combined boiler/CHP exhaust stack | 85 dBA | - | - | 1 |  | omni
Odour control unit | 96 dBA | - | - | 1 |  | hemispherical
CHP enclosure | - | 59 dBA at 10m | 91 dBA | 1 |  | hemispherical
Gas cooling unit chiller | 86 dBA | - | - | 1 |  | hemispherical
Gas coling unit compressor | - | 78 dBA at 1m | 96 dBA | 1 |  | hemispherical
Air fan gas holder | - | 70 dBA at 1m | 85 dBA | 2 |  | hemispherical
Gas Upgrading Unit recompression booster | - | 78 dBA at 1m | 93 dBA | 1 |  | hemispherical
GUU Drycooler | - | 68 dBA at 10m | 99 dBA | 1 |  | hemispherical
GUU Glycol chiller | - | 55 dBA at 10m | 87 dBA | 1 |  | hemispherical
Agitator | - | 56 dBA at 2m | 75 dBA | 3 |  | hemispherical
Biogas compressor | - | 93 dBA at 1m | 110 dBA | 1 |  | hemispherical
OCU Stack at 19m above ground | 65 dBA | - | - | 1 |  | omni
Within Reception Building
Compulsory Mixer | - | 70 dBA at 1m | 85 dBA | 3 | n/a see 'level in building' tab |  | 33%
GUU Glycol pump | - | 70 dBA at 1m | 85 dBA | 1 |  |  | 100%
Slurry pump | - | 80 dBA at 1m | 95 dBA | 5 |  |  | 100%
Vogelsang pump | - | 78 dBA at 1m | 93 dBA | 1 |  |  | 100%
Wangen pump | - | 70 dBA at 1m | 85 dBA | 2 |  |  | 50%
Feed unit floor | - | 79 dBA at 1m | 94 dBA | 1 |  |  | 100%
Feed unit pump | 100 dBA | - | - | 1 |  |  | 33%
Depackaging unit | 83 dBA | - | - | 1 |  |  | 80%

## Noise Emitting buildings
Corner Grid References - New Plant Building
Corner | X | Y
1
2
3
4
For plant data within building please see previous tab
Building on site providing screening

## Level in building
Item | How many? | On time info | Lp/Lw | Dist | dBA | Derived Lw | Corrected for number of plant | Corrected for time
GUU Glycol pump | 1 | 100% | Lp | 1 | 70 | 85 | 85 | 85
Compulsory Mixer | 3 | 33% | Lp | 1 | 70 | 85 | 89.7712 | 84.9564
Feed unit floor | 1 | 100% | Lp | 1 | 79 | 94 | 94 | 94
Feed unit pump | 1 | 33% | Lw | - | 100 | 100 | 100 | 95.1851
Depackaging unit | 1 | 80% | Lw | - | 83 | 83 | 83 | 82.0309
Telehandler | 1 | 50% | Lw | - | 115 | 115 | 115 | 111.9897
Slurry pump | 5 | 100% | Lp | 1 | 80 | 95 | 101.9897 | 101.9897
Wangen pump | 2 | 50% | Lp | 1 | 70 | 85 | 88.0103 | 85
Vogelsang pump | 1 | 100% | Lp | 1 | 78 | 93 | 93 | 93
[6 empty] | Cumulative Sound Power in Building |  | 112.6 | dBLw

## Noise trans via facade
Calculation Notes
Can be used as surface sound power due to minimal distance 'from wall to receive'
Calculation based on a nominal 25 dB internal to external level difference; traditional built constructions as proposed expected to far exceed this
Calculation based on the roof as the weakest point
Therefore sound power of 72 dBA has been applied to each wall and the roof within the noise model as a worst case

## Receptors
Address | Grid Ref X | Grid Ref Y | Assumed storeys | Sensitivity
Spitfire Road | 566582 | 155502 | 2 | Residential
Beech Road | 565737 | 154865 | 2 | Residential
Ashree Farm | 566802 | 156726 | 2 | Residential
Orwell Spike | 567172 | 156351 | 2 | Residential
Seven Mile Lane | 564360 | 155762 | 2 | Residential
Kentfield Farm | 565865 | 156743 | 2 | Residential