# SR2026 number 1: new and existing, low risk, mobile medium combustion plant which is a boiler

The Environmental Permitting (England & Wales) Regulations 2016

## Introductory note

This introductory note does not form a part of these standard rules.

When referred to in an environmental permit, these rules will allow the operator to deploy one or more new or existing mobile medium combustion plant (MCP). The MCP must be a boiler providing steam or hot water only, for a specified duration in England and Wales, where the hire company’s principal place of business is in England. Deployment may be in an Air Quality Management Area (AQMA).

The limits of the permitted activity are that:

- all mobile medium combustion plant shall operate with a net rated thermal input equal to or greater than 1 MWth and less than 20 MWth individually or aggregated

- natural gas and gas oil or a gas oil substitute may be used as a fuel. Gas oil may also be used as a back-up fuel for natural gas deployments for up to 10% of operational hours of the deployment

- all mobile medium combustion plant must meet the minimum distances criteria to a protected habitat set out in these standard rules. The required distance will depend on the thermal capacity, fuel type, achievable emissions and release height.

- deployment of mobile medium combustion plant to increase or replace operational combustion capacity at a regulated facility is prohibited. It may be deployed for the purpose of a statutory inspection of a stationary boiler or in an emergency.

Words and expressions used in this introductory note and these standard rules shall have the meanings given in section 4.4, as appropriate.

End of introductory note

Rules

## 1. Management

### 1.1 General management

1.1.1 The operator shall manage and operate the activities:

(a) in accordance with a written management system that identifies and minimises risks of pollution, so far as is reasonably practicable, including those risks arising from operations, maintenance, accidents, incidents, non-conformances and those drawn to the attention of the operator as a result of complaints; and

(b) using sufficient competent persons and resources.

1.1.2 Records demonstrating compliance with rule 1.1.1 shall be maintained.

1.1.3 Any person having duties that are or may be affected by the matters set out in these standard rules or the permit shall have convenient access to a copy of the permit and the rules.

## 2. Operations

### 2.1 Permitted activities

2.1.1 The operator is only authorised to carry out the activities specified in table 2.1.

#### Table 2.1

| Activity reference | Description of specified activity | Limits of specified activity |
| --- | --- | --- |
| New and existing mobile MCP which are boilers for the production of steam and/or hot water. | The operation of new and existing mobile MCP, which are boilers, operated with a net rated thermal input greater than or equal to 1 MWth and less than 20 MWth individually or aggregated. | The only fuel that shall be used by the MCP shall be natural gas, gas oil or gas oil substitute as agreed in writing with the Environment Agency. Gas oil may also be used as a backup fuel for natural gas deployments for up to 10% of operational hours of the deployment All mobile MCP deployments must meet the minimum distance requirements from protected habitats criteria specified in these standard rules, including any additional distances where capacity is aggregated, based on thermal capacity, fuel type, achievable emissions, and release height for each deployment. Mobile MCP may also be deployed to a regulated facility for the purposes of statutory inspection or an emergency but must not be used to increase operational combustion capacity. |

### 2.2 Deployment

2.2.1 The operator may deploy mobile medium combustion plant specified in Appendix A of this permit to a location which meets the criteria specified in Table 2.2, 2.3 and 2.4, providing the operator can meet the emission limit values specified in either Table 3.1, 3.2 or 3.3.

2.2.2 The operator may deploy mobile medium combustion plant covered by this permit to a location which doesn’t meet the criteria in Tables 2.2, 2.3 or 2.4, where the operator uses an approved screening tool and method and the results confirm the emissions will have an insignificant impact on protected habitats.

2.2.3 No deployment of a mobile medium combustion plant shall occur for longer than 12 months.

2.2.4 For continuous deployment of a mobile medium combustion plant over 11 months repeat deployments at the same location shall only be permitted after a period of 9 months has elapsed between deployments.

2.2.5  The MCP shall be operated at the grid reference location specified for it in the deployment.

2.2.6 Rated thermal capacity of a deployment can be aggregated by using more than one mobile medium combustion plant subject to;

(a)	where two mobile medium combustion plant or any size shall use the screening distances in Column A in Tables 2.2, 2.3 and 2.4;

(b)	where more than two mobile medium combustion plant shall use the screening distances in Column B in Tables 2.2, 2.3 and 2.4;

(c)	no more than seven medium mobile combustion plant may be used to aggregate capacity.

#### Table 2.2 Mobile medium combustion plant with a net rated thermal capacity of greater than or equal to 1MWth and less than 20MWth, individually or aggregated, fired on natural gas, meeting emission limits given in Table 3.1

| Deployment Period | Net rated thermal input of mobile MCP deployed in MWth | Stack height in metres | Minimum protective distance from MCP to a protected habitat in metres (1-2 MCP) COLUMN A | Minimum protective distance from MCP to a protected habitat in metres (3-7 MCP) COLUMN B |
| --- | --- | --- | --- | --- |
| Up to 1 month | 1 | ≥3 | 0 | 0 |
|  | >1 - ≤2 | ≥3 | 50 | 50 |
|  |  | ≥5 | 0 | 0 |
|  | ≤4 | ≥3 | 75 | 75 |
|  |  | ≥5 | 50 | 50 |
|  |  | ≥7 | 0 | 0 |
|  | ≤7 | ≥3 | 75 | 150 |
|  |  | ≥5 | 50 | 125 |
|  |  | ≥7 | 0 | 75 |
|  | ≤12 | ≥3 | 100 | 175 |
|  |  | ≥5 | 75 | 150 |
|  |  | ≥7 | 0 | 75 |
|  | ≤14 | ≥3 | 125 | 200 |
|  |  | ≥5 | 100 | 175 |
|  |  | ≥7 | 50 | 125 |
|  | ≤20 | ≥3 | 150 | 225 |
|  |  | ≥5 | 125 | 200 |
| Up to 3 months | 1 | ≥3 | 75 | 75 |
|  |  | ≥7 | 50 | 50 |
|  | ≤2 | ≥3 | 100 | 100 |
|  |  | ≥7 | 75 | 75 |
|  | ≤3 | ≥3 | 125 | 125 |
|  |  | ≥5 | 100 | 100 |
|  |  | ≥7 | 75 | 75 |
|  | ≤4 | ≥3 | 125 | 200 |
|  |  | ≥7 | 100 | 175 |
|  | ≤5 | ≥3 | 150 | 225 |
|  |  | ≥5 | 125 | 200 |
|  | ≤7 | ≥3 | 150 | 250 |
|  |  | ≥7 | 125 | 225 |
|  | ≤10 | ≥3 | 200 | 300 |
|  |  | ≥5 | 175 | 275 |
|  | ≤12 | ≥3 | 225 | 325 |
|  |  | ≥5 | 200 | 300 |
|  |  | ≥7 | 175 | 275 |
|  | ≤14 | ≥3 | 250 | 350 |
|  |  | ≥7 | 225 | 325 |
|  | ≤20 | ≥3 | 300 | 400 |
|  |  | ≥5 | 275 | 375 |
| Up to 6 months | 1 | ≥3 | 100 | 100 |
|  | ≤2 | ≥3 | 150 | 150 |
|  |  | ≥7 | 125 | 125 |
|  | ≤3 | ≥3 | 175 | 175 |
|  |  | ≥7 | 150 | 150 |
|  | ≤4 | ≥3 | 200 | 300 |
|  |  | ≥5 | 175 | 275 |
|  | ≤5 | ≥3 | 225 | 325 |
|  |  | ≥5 | 200 | 300 |
|  | ≤7 | ≥3 | 250 | 400 |
|  |  | ≥7 | 225 | 375 |
|  | ≤10 | ≥3 | 300 | 450 |
|  |  | ≥5 | 275 | 425 |
|  | ≤12 | ≥3 | 350 | 500 |
|  |  | ≥5 | 300 | 450 |
|  | ≤14 | ≥3 | 400 | 550 |
|  |  | ≥7 | 350 | 500 |
|  | ≤20 | ≥3 | 450 | 600 |
| Up to 12 months | 1 | ≥3 | 150 | 150 |
|  | ≤2 | ≥3 | 225 | 225 |
|  |  | ≥5 | 200 | 200 |
|  | ≤3 | ≥3 | 250 | 250 |
|  | ≤4 | ≥3 | 300 | 450 |
|  |  | ≥7 | 275 | 425 |
|  | ≤5 | ≥3 | 350 | 500 |
|  |  | ≥7 | 300 | 450 |
|  | ≤7 | ≥3 | 400 | 600 |
|  |  | ≥7 | 350 | 550 |
|  | ≤10 | ≥3 | 450 | 650 |
|  | ≤12 | ≥3 | 500 | 700 |
|  |  | ≥7 | 450 | 650 |
|  | ≤14 | ≥3 | 600 | 800 |
|  | ≤20 | ≥3 | 700 | 900 |

#### Table 2.3 Mobile medium combustion plant with a net rated thermal capacity of greater than or equal to 1MWth and less than 20MWth, individually or aggregated, fired on gas oil or gas oil substitute, or natural gas, meeting emission limits given in Table 3.2

| Deployment Period | Net rated thermal input of mobile MCP deployed in MWth | Stack height in metres | Minimum protective distance from MCP to a protected habitat in metres (1-2 MCP) COLUMN A | Minimum protective distance from MCP to a protected habitat in metres (3-7 MCP) COLUMN B |
| --- | --- | --- | --- | --- |
| Up to 1 month | 1 | ≥3 | 75 | 75 |
|  |  | ≥5 | 50 | 50 |
|  |  | ≥7 | 0 | 0 |
|  | ≤2 | ≥3 | 75 | 75 |
|  |  | ≥7 | 50 | 50 |
|  | ≤3 | ≥3 | 100 | 100 |
|  |  | ≥5 | 75 | 75 |
|  |  | ≥7 | 50 | 50 |
|  | ≤4 | ≥3 | 100 | 175 |
|  |  | ≥7 | 50 | 125 |
|  | ≤5 | ≥3 | 125 | 200 |
|  |  | ≥5 | 100 | 175 |
|  |  | ≥7 | 50 | 125 |
|  | ≤7 | ≥3 | 150 | 225 |
|  |  | ≥5 | 100 | 175 |
|  |  | ≥7 | 50 | 125 |
|  | ≤10 | ≥3 | 150 | 225 |
|  |  | ≥5 | 125 | 200 |
|  | ≤12 | ≥3 | 175 | 250 |
|  |  | ≥5 | 150 | 225 |
|  |  | ≥7 | 125 | 200 |
|  | ≤14 | ≥3 | 200 | 275 |
|  |  | ≥5 | 175 | 250 |
|  | ≤20 | ≥3 | 225 | 300 |
|  |  | ≥7 | 200 | 275 |
| Up to 3 months | 1 | ≥3 | 100 | 100 |
|  | ≤2 | ≥3 | 150 | 150 |
|  |  | ≥7 | 125 | 125 |
|  | ≤3 | ≥3 | 175 | 175 |
|  |  | ≥7 | 150 | 150 |
|  | ≤4 | ≥3 | 200 | 275 |
|  |  | ≥5 | 175 | 250 |
|  | ≤5 | ≥3 | 225 | 300 |
|  |  | ≥5 | 200 | 275 |
|  | ≤7 | ≥3 | 250 | 350 |
|  |  | ≥7 | 225 | 325 |
|  | ≤10 | ≥3 | 300 | 400 |
|  |  | ≥5 | 275 | 375 |
|  | ≤12 | ≥3 | 350 | 450 |
|  |  | ≥5 | 300 | 400 |
|  | ≤14 | ≥3 | 400 | 500 |
|  |  | ≥7 | 350 | 450 |
|  | ≤20 | ≥3 | 450 | 550 |
| Up to 6 months | 1 | ≥3 | 150 | 150 |
|  | ≤2 | ≥3 | 225 | 225 |
|  |  | ≥5 | 200 | 200 |
|  | ≤3 | ≥3 | 250 | 250 |
|  | ≤4 | ≥3 | 300 | 400 |
|  |  | ≥7 | 275 | 375 |
|  | ≤5 | ≥3 | 350 | 450 |
|  |  | ≥7 | 300 | 400 |
|  | ≤7 | ≥3 | 400 | 550 |
|  |  | ≥7 | 350 | 500 |
|  | ≤10 | ≥3 | 450 | 600 |
|  | ≤12 | ≥3 | 500 | 650 |
|  |  | ≥7 | 450 | 600 |
|  | ≤14 | ≥3 | 600 | 750 |
|  | ≤20 | ≥3 | 700 | 850 |
| Up to 12 months | 1 | ≥3 | 250 | 250 |
|  |  | ≥5 | 225 | 225 |
|  | ≤2 | ≥3 | 350 | 350 |
|  |  | ≥7 | 300 | 300 |
|  | ≤3 | ≥3 | 400 | 400 |
|  | ≤4 | ≥3 | 450 | 600 |
|  | ≤5 | ≥3 | 500 | 650 |
|  | ≤7 | ≥3 | 600 | 800 |
|  | ≤10 | ≥3 | 700 | 900 |
|  | ≤12 | ≥3 | 800 | 1000 |
|  |  | ≥5 | 750 | 950 |
|  | ≤14 | ≥3 | 950 | 1150 |
|  |  | ≥7 | 900 | 1100 |
|  | ≤20 | ≥3 | 1200 | 1400 |
|  |  | ≥5 | 1100 | 1300 |

#### Table 2.4 Mobile medium combustion plant with a net rated thermal capacity of greater than or equal to 1MWth and less than or equal to 5MWth, individually or aggregated, fired on natural gas, meeting emission limits in Table 3.3

| Deployment Period | Net rated thermal input of mobile MCP deployed in MWth | Stack height in metres | Minimum protective distance from MCP to a protected habitat in metres (1-2 MCP) COLUMN A | Minimum protective distance from MCP to a protected habitat in metres (3-7 MCP) COLUMN B |
| --- | --- | --- | --- | --- |
| Up to 1 month | 1 | ≥3 | 75 | 75 |
|  |  | ≥7 | 0 | 0 |
|  | ≤2 | ≥3 | 100 | 100 |
|  |  | ≥5 | 75 | 75 |
|  |  | ≥7 | 50 | 50 |
|  | ≤3 | ≥3 | 100 | 100 |
|  |  | ≥7 | 75 | 75 |
|  | ≤4 | ≥3 | 125 | 200 |
|  |  | ≥5 | 100 | 175 |
|  |  | ≥7 | 75 | 150 |
|  | ≤5 | ≥3 | 125 | 200 |
|  |  | ≥7 | 100 | 175 |
| Up to 3 months | 1 | ≥3 | 125 | 125 |
|  |  | ≥7 | 100 | 100 |
|  | ≤2 | ≥3 | 175 | 175 |
|  |  | ≥5 | 150 | 150 |
|  | ≤3 | ≥3 | 200 | 200 |
|  |  | ≥7 | 175 | 175 |
|  | ≤4 | ≥3 | 225 | 300 |
|  |  | ≥7 | 200 | 275 |
|  | ≤5 | ≥3 | 250 | 325 |
|  |  | ≥7 | 225 | 300 |
| Up to 6 months | 1 | ≥3 | 175 | 275 |
|  | ≤2 | ≥3 | 250 | 350 |
|  |  | ≥7 | 225 | 325 |
|  | ≤3 | ≥3 | 300 | 400 |
|  |  | ≥7 | 275 | 375 |
|  | ≤4 | ≥3 | 350 | 450 |
|  | ≤5 | ≥3 | 400 | 500 |
|  |  | ≥7 | 350 | 450 |
| Up to 12 months | 1 | ≥3 | 275 | 275 |
|  |  | ≥7 | 250 | 250 |
|  | ≤2 | ≥3 | 400 | 400 |
|  |  | ≥7 | 350 | 350 |
|  | ≤3 | ≥3 | 450 | 450 |
|  | ≤4 | ≥3 | 550 | 700 |
|  |  | ≥7 | 500 | 650 |
|  | ≤5 | ≥3 | 600 | 750 |

### 2.3 Operating techniques

2.3.1 The activities shall be operated using the techniques and, in the manner, described, as follows;

(a) each MCP must be operated in accordance with its manufacturer’s instructions and records must be made and retained to demonstrate this.

(b) periods of start-up and shut down of each MCP should be kept as short as possible.

(c) there must be no persistent emission of ‘dark smoke’ as defined in section 3(1) of the Clean Air Act 1993.

(d) the stack must be vertical and unimpeded by cowls or caps.

## 3. Emissions and monitoring

### 3.1 Emissions to air

3.1.1 The point source emissions to air shall not exceed the applicable emission limit values given in tables 3.1, 3.2 and 3.3.

#### Table 3.1 emission limit value requirements for new or new existing mobile medium combustion plant

| Pollutant | Emission limit value in mg/Nm³ Natural gas | Emission limit value in mg/Nm³ Gas oil or gas oil substitute |
| --- | --- | --- |
| Sulphur dioxide (SO₂) (mg/Nm³) | Not applicable | Not applicable |
| Oxides of nitrogen (NO and NO₂ expressed as NO₂) (mg/Nm³) | 100 | 200 |
| Carbon monoxide (CO) (mg/Nm³) | No limit | No limit |

#### Table 3.2 emission limit value requirements for existing mobile medium combustion plant greater than 5MWth firing natural gas or gas oil, or gas oil substitute

| Pollutant | Emission limit value in mg/Nm³ |
| --- | --- |
| Oxides of nitrogen (NO and NO₂ expressed as NO₂) (mg/Nm³) | 200 |
| Carbon monoxide (CO) (mg/Nm³) | No limit |

Table 3.3 emission limit value requirements for existing mobile medium combustion plant greater than or equal to 1MWth but less than or equal to 5MWth

| Pollutant | Emission limit value in mg/Nm³ Natural gas | Emission limit value in mg/Nm³ Gas oil or gas oil substitute as agreed |
| --- | --- | --- |
| Oxides of nitrogen (NO and NO₂ expressed as NO₂) (mg/Nm³) | 250 | 200 |
| Carbon monoxide (CO) (mg/Nm³) | No limit | No limit |

### 3.2 Monitoring

3.2.1 The operator shall, unless otherwise agreed in writing by the Environment Agency, undertake emissions monitoring for the applicable pollutants specified in tables 3.1, 3.2 and 3.3 prior to each deployment.

3.2.5 No monitoring is required for dual fuel mobile MCP during operation on back up gas oil or gas oil substitute

3.2.6 The operator shall, if notified in writing by the Environment Agency, undertake additional monitoring of any MCP for the pollutants specified in tables 3.1, 3.2 and 3.3.

3.2.7 The emissions monitoring shall be carried out in accordance with the guidance ‘monitoring stack emissions: low risk MCPs and specified generators’ or using monitoring equipment, techniques, personnel and organisations with MCERTS certification or MCERTS accreditation (as appropriate), unless otherwise agreed in writing by the Environment Agency.

3.2.8 The operator shall maintain records of all monitoring required by these standard rules including records of the taking and analysis of samples, instrument measurements (periodic and continual), calibrations, examinations, tests and surveys and any assessment or evaluation made on the basis of such data.

3.2.9 Monitoring results must be converted to standard reference conditions for temperature, pressure and the relevant oxygen content, namely the concentration of substances in dry air to a temperature of 273,15K, to a pressure of 101,3 kPa and with an oxygen content of 3%.

## 4. Information

### 4.1 Records

4.1.1 All records required to be made by these standard rules shall:

(a) be legible;

(b) be made as soon as reasonably practicable;

(c) if amended, be amended in such a way that the original and any subsequent amendments remain legible, or are capable of retrieval; and be retained, unless otherwise agreed in writing by the Environment Agency, for at least 6 years from the date when the records were made.

4.1.2 The operator shall maintain convenient access, in either electronic or hard copy, to the records, plans and management system required to be maintained by these rules.

4.1.3 The operator shall maintain records of all deployments including, location, duration of deployment, distance to protected habitats, fuel used, actual thermal capacity and thermal capacity utilised, stack height, the results of any screening under condition 2.2.2 prior to deployment, and whether each deployment is to a regulated facility.

4.1.4 The operator shall maintain a record of any events of non-compliance and the measures taken to ensure compliance is restored in the shortest possible time.

### 4.2 Reporting

4.2.1 The operator shall send all reports and notifications required by these standard rules to the Environment Agency using the contact details supplied in writing by the Environment Agency.

4.2.2 Within one month from the end of the year the operator shall provide a report to the Environment Agency on deployments made during the year using the form made available for that purpose the information specified on the form relating to those deployments.

### 4.3 Notifications

4.3.1 In the event:

(a) of a breach of any of these standard rules the operator must immediately—

i. inform the Environment Agency; and

ii. take the measures necessary to ensure that compliance is restored within the shortest possible time.

(b) of a breach of any of these standard rules which causes a significant degradation of local air quality, the operator must immediately suspend the operation of the activities or the relevant part of them until compliance with the rules has been restored.

4.3.2 Where the operator is notified by the Environment Agency under rule 3.2.6, to undertake monitoring at frequencies not otherwise specified in tables 3.1 and 3.2, the operator shall provide, at least 14 days prior to the monitoring being carried out, details of when the monitoring is to take place.

4.3.3 Any information provided under rule 4.3.1 shall be confirmed in writing within 24 hours.

4.3.4 The Environment Agency shall be notified within 14 days of the occurrence of the following matters, except where such disclosure is prohibited by Stock Exchange rules:

Where the operator is a registered company:

(a) any change in the operator’s trading name, registered name or registered office address; and

(b) any steps taken with a view to the operator going into administration, entering into a company voluntary arrangement or being wound up.

Where the operator is a corporate body other than a registered company:

(c) any change in the operator’s name or address; and

(d) any steps taken with a view to the dissolution of the operator.

In any other case:

(e) the death of any of the named operators (where the operator consists of more than one named individual).

(f) any change in the operator’s name(s) or address(es); and any steps taken with a view to the operator, or any one of them, going into bankruptcy, entering into a composition or arrangement with creditors, or, in the case of them being in a partnership, dissolving the partnership.

### 4.4 Interpretation

4.4.1 In these standard rules the expressions listed in 4.4.1 shall have the meanings given.

‘accident’ means an accident that may result in pollution.

‘activities’ means the operation of the MCP specified in Appendix A.

‘Appendix A’ means Appendix A as attached to the permit.

“approved screening tool” means the Simple Calculation of Atmospheric Impact Limits (SCAIL) tool produced by the UK Centre for Ecology and Hydrology.

‘EP Regulations’ means The Environmental Permitting (England and Wales) Regulations 2016 SI No.1154 and words and expressions used in these rules or the permit which are also used in the Regulations have the same meanings as in those Regulations.

‘existing MCP’ means MCP with a net rated thermal input equal to or greater than 1MWth and less than 20MWth which was put into operation before 20 December 2018.

‘First put into operation’ means the date when fuel is first combusted in the MCP. This can be during initial on-site commissioning but does not include conformity testing at the place of manufacture of the plant.

‘Gas oil’ is as defined in article 3 (19) of the Directive 2015/2193/EU of the European Parliament and of the Council on the limitation of emissions of certain pollutants into the air from medium combustion plants.

‘Gas oil substitutes’ includes hydrotreated vegetable oil and other liquid fuels approved as being equivalent to gas oil by the Environment Agency, as published in our Medium combustion plant (MCP): comply with emission limit values guidance.

`insignificant impact` means where the process contribution from the deployment is calculated to be less than 4% by an approved screening tool

‘MCP’ means medium combustion plant

“MCERTS” means the Environment Agency’s Monitoring Certification Scheme.

‘Mobile MCP’ means a medium combustion plant that is designed to move or be moved whether on roads or other land

‘monitoring stack emissions, low risk MCPs and specified generators’ refers to the guidance with that title published on GOV.UK and last updated on 12 July 2022, or any subsequent version which makes only editorial changes.

‘new MCP’ means a MCP with a net rated thermal input equal to or greater than 1MWth and less than 20MWth which was put into operation on or after the 20 December 2018.

‘operating hours’ means the time, expressed in hours, during which a MCP is operating and discharging emissions into the air, excluding start-up and shut-down periods.

‘protected habitat’ means Special Areas of Conservation (SAC), Special Protection Areas (SPA), Ramsar Sites, Marine Conservation Zones (MCZ) and Sites of Special Scientific Interest (SSSI).

‘regulated facility` has the meaning given in regulation 8(1) of the Environmental Permitting Regulations 2016.

‘year’ means calendar year ending 31 December.

4.4.2 In these standard rules:

(a) references to reports and notifications mean written reports and notifications, except where reference is made to notification being made immediately, in which case it may be provided by telephone.

(b) references to concentrations of substances in emissions to air set out in tables 3.1, 3.2 and 3.3 are expressed at a temperature of 273.15 K, a pressure of 101.3 kPa and after correction for the water vapour content of the waste gases and at a standardised O₂ content of 6% for medium combustion plants using solid fuels, 3% for medium combustion plants, other than engines and gas turbines, using liquid and gaseous fuels and 15% for engines and gas turbines.

End of standard rules.

## Record of changes

| Version | Date | Change |
| --- | --- | --- |
| 1.0 Draft | 2026 | Published for SRP consultation 08 June 2026 |