## Sheet1
Pure DC Environmental Permit - Operational Risk Assessment |  |  |  | Reference: | https://www.gov.uk/guidance/risk-assessments-for-your-environmental-permit
Hazard | Process | Receptor | Pathway | Risk Management Techniques | Probability of Exposure | Consequence | Overall Risk After Management Techniques
Ground contamination | Containment failure of fuel storage bunker | Ground | Infiltration through damaged concrete hardstanding | Integrated double-bunded tanks to be used Automated leak detection system installed in secondary containment chamber Remote monitoring of tank levels, with linked alarm notifiying out of specification changes to levels Daily visial inspection of tank external integrity Appropriate training to staff operatives re use of spill kits, and reporting / post incident learning. Documented processes | Remote | Extreme | Low Risk
Contamination of ground, and or water bodies; odour | Spill (onsite) from vehicle of third party contractor when deliering fuel (vehicle movement) | Ground/soils Groundwater Surface water | Infiltration through damaged concrete hardstanding | Use of drip trays Appropriately stocked spill kits to be stored in accessible location near to fill points Appropriate training to staff operatives re use of spill kits, and reporting / post incident learning. Documented processes Routine visual inspection of gound integrity, and other relevant infrastucture | Unlikely | Moderate | Low Risk
Contamination of ground, and or water bodies; odour | Spill (onsite) from vehicle of third party contractor when deliering fuel (decanting fuel) | Ground/soils Groundwater Surface water | Infiltration through damaged concrete hardstanding | Use of drip trays Appropriately stocked spill kits to be stored in accessible location near to fill points Appropriate training to staff operatives re use of spill kits, and reporting / post incident learning. Documented processes Routine visual inspection of gound integrity, and other relevant infrastucture | Unlikely | Moderate | Low Risk
Litter | Windblown litter from storage areas into receiving environment | Nearby habitats (terrestrial and aquatic) | Windbourne | All waste will be stored within enclosed storage areas that can be closed when being accessed. Documented waste management processes | Unlikely | Minor | No Risk
Prolonged emissions of atmospheric pollutants | Standby power generators operate for prolonged periods (either due to operational requirement - power outage - or routine test regime) | Nearby sensitive ecological habitats Nearby human health receptors | Direct atmospheric emission from genset exhaust vent | Atmospheric emissions regulated under Enviornmnetal Permit. Contractual requirement limits standby power generator operating duration (<48hrs continual operation) Documented operational controls implemented to minimise emissions (including process specification and design; routine servicing and maintenance) Routine test regime structured to minimise cumulative impact of emissions Approproate training for staff | Unlikely | Moderate | Low Risk
Noise | Noise generated by: startup and operation of genset(s) Audible alarms | Nearby human receptors Wildlife in and around Brent Reservoir SSSI and elsewhere | Windbourne | Acoustic baffles around perimeter of building roof, enclosing stack. Fans enclosed within structure affording accoustic suppression. Limited use of external alarms (security and safety systems only; operational alarms internal only) | Possible | Moderate | Moderate Risk
Visible dark smoke | Cold start of standby generators and or sudden changes in load demand resulting in elevated emissions of particulate material | Nearby human receptors | Direct atmospheric emission from genset exhaust vent | Engine start-up sequence to be automated and process controlled to minimise conditions resulting in formation of dark smoke. Documented operational controls (including routine service and maintenance) | Possible | Moderate | Moderate Risk
Note on F4: Microsoft Office User: Remote, Unlikely, Possible, Likely
Note on G4: Microsoft Office User: Minor, Moderate, Major, Extreme

## Sheet2
|  |  | Consequence |  |  |  | Score = Probability x Consequence
|  |  | Minor | Moderate | Major | Extreme
|  |  | 1 | 2 | 3 | 4 |  | Risk Description
Probability | Remote | 1 | 1 | 2 | 3 | 4 | 1 | No Risk
| Unlikely | 2 | 2 | 4 | 6 | 8 | 2 | No Risk
| Possible | 3 | 3 | 6 | 9 | 12 | 3 | Low Risk
| Likely | 4 | 4 | 8 | 12 | 16 | 4 | Low Risk
[7 empty] | 6 | Moderate Risk
[7 empty] | 8 | Moderate Risk
[7 empty] | 9 | High Risk
[7 empty] | 12 | High Risk
[7 empty] | 16 | High Risk