- Purpose and Scope

This Environmental Risk Assessment (ERA) has been prepared to meet the Environment Agency (EA) guidance “Risk assessments for your environmental permit – GOV.UK”. The ERA identifies and evaluates all potential environmental risks arising from permitted activities at the Inspired Global Cuisine Limited (IGC) Oldham facility, considering:

- All potential emissions into the air, water and land

- Normal, abnormal and accident conditions

- Human receptors and environmental (habitat) receptors

- Existing and proposed mitigation and control measures

This ERA supports the Environmental Permit application and demonstrates that risks are reduced to as low as reasonably practicable (ALARP).

- Site Overview

IGC Oldham is a frozen Soups, Sauces, ready‑meal manufacturing and storage facility involving cooking, chilling, freezing, assembly, cold storage and dispatch operations. Key infrastructure includes:

- Cooking kettles and sauce preparation areas

- Two natural gas steam boilers (MCP <7.5 MW each)

- External ammonia refrigeration plant (total charge <650 kg)

- Trade effluent system with sediment and grease management

- Surface water drainage with interceptors, penstocks and attenuation

- Waste storage and handling areas

- External yard and vehicle movements

- Risk Assessment Methodology

The ERA follows the EA Source–Pathway–Receptor methodology:

- Identify potential sources of emissions or pollutants

- Identify pathways by which pollutants could reach receptors

- Identify receptors, including:

  - Human receptors

  - Environmental and habitat receptors

- Assess

  - Likelihood of release

  - Consequence of impact

- Identify control measures and assess residual risk

Risk assessment qualitatively as Low/Medium/High before and after impact

- Receptor

Human Receptors

- On‑site employees and contractors

- Visitors and drivers

- Nearest residential properties surrounding the site

- Members of the public using nearby transport routes

Environmental and Habitat Receptors

Habitat receptors have been identified and assessed in line with Environment Agency screening distances and modelling methodology set out in the updated Air Quality Assessment prepared by SLR Consulting Limited (SLR Project No. 440.v13945.00001, Revision 03, January 2026).

In accordance with EA guidance, statutory and non-statutory ecological sites within:

10 km (Special Areas of Conservation (SAC), Special Protection Areas (SPA), Ramsar sites); and  
2 km (Sites of Special Scientific Interest (SSSI), Local Wildlife Sites (LWS), National Nature Reserves (NNR) and Local Nature Reserves (LNR))

were identified using the MAGIC online resource.

The following designated habitat sites fall within the relevant screening distances of the installation:

- Rochdale Canal Site of Special Scientific Interest (SSSI) and Special Area of Conservation (SAC)

- Hunt Lane Local Wildlife Site (LWS)

- River Irk Marsh LWS

- Rochdale Canal – Lock at Scowcroft Farm to Stott’s Lane LWS

- Rochdale Canal – Scowcroft to Warland LWS

- Scowcroft Reservoir LWS

The Air Quality Assessment defined eighteen discrete ecological receptor points (ECO 1 to ECO 18) across the SAC/SSSI and all five Local Wildlife Sites in order to represent worst-case exposure locations.

These receptors were assessed for:

- Short-term and long-term nitrogen dioxide (NO₂) concentrations

- Nutrient nitrogen deposition

- Nitrogen-derived acid deposition

The assessment applied conservative assumptions in accordance with EA guidance, including:

- Use of APIS site-specific critical loads

- 100% conversion of NOx to NO₂ for long-term impacts

- EA-recommended deposition velocities

- Five years of meteorological data

Modelling results demonstrate that for all assessed designated habitat sites:

- Process contributions to NO₂ are below EA screening thresholds; and

- Nutrient nitrogen and acid deposition rates are well below the relevant critical loads.

On this basis, significant effects to the Rochdale Canal SAC/SSSI and all five Local Wildlife Sites can be screened out, and no further Stage 2 or Stage 3 habitat assessment is required for emissions to air.

Aquatic ecology associated with the Rochdale Canal, downstream surface waters, groundwater, soils and the sewer network remain relevant receptors for emissions to water and accident scenarios assessed elsewhere in this Environmental Risk Assessment.

Habitat receptors have been identified and assessed in line with the methodology and screening distances set out in the SLR Consulting Limited Air Quality Assessment (SLR Project No. 440.v13945.00001, Revision 02, dated 20 November 2025), prepared to support the Environmental Permit application.

The following environmental and habitat receptors have been identified:

- Surface Water and Aquatic Habitat: Rochdale Canal

- Statutory Designated Site: Rochdale Canal Site of Special Scientific Interest (SSSI) and Special Area of Conservation (SAC)

- Sensitive Feature: Luronium natans (Floating Water-plantain)

- Sewer network and downstream sewage treatment works

- Groundwater (non-principal aquifer – no direct abstraction on site)

- Soil and ground beneath the site

The Rochdale Canal SSSI/SAC is the only statutory designated habitat site located within 2 km and 10 km of the installation, as confirmed via MAGIC and detailed ecological screening undertaken as part of the Air Quality Assessment. No additional European or nationally designated habitat sites fall within the relevant EA screening distances for emissions to air.

A number of discrete ecological receptor points (ECO 1 to ECO 10) along the Rochdale Canal SSSI/SAC have been modelled in the Air Quality Assessment to represent a robust worst-case evaluation of potential impacts. These receptor points have been used to assess:

- Short-term and long-term nitrogen dioxide (NO₂) concentrations

- Nutrient nitrogen deposition

- Nitrogen-derived acid deposition

The assessment applied conservative assumptions in accordance with EA guidance, including:

- Use of the lowest relevant critical loads from APIS

- 100% conversion of NOx to NO₂ for long-term impacts

- EA-recommended deposition velocities

On this basis, the Rochdale Canal SSSI/SAC is considered the critical habitat receptor for the purposes of this Environmental Risk Assessment.

- Aquatic ecology associated with the Rochdale Canal

No European designated sites (SAC, SPA, Ramsar) are present within the immediate zone of influence. A habitat screening approach has therefore been applied.

- Emission Source and Pathways

Emissions to Air

| Source | Emission | Pathway | Receptors | Controls | Residual Risk |
| --- | --- | --- | --- | --- | --- |
| Gas boilers | NOx, CO | Atmospheric dispersion | Local residents, staff | MCP-compliant burners, stack design, maintenance | Low |
| Cooking processes | Odour, steam | Atmospheric dispersion | Local residents | Extraction, process control, OMP | Low |
| Ammonia plant (accidental) | Ammonia gas | Air dispersion | Staff, public | External plant, detection, alarms, emergency plan | Low |
| Emergency generators (temporary) | Combustion gases | Air dispersion | Staff | Infrequent use, maintained equipment by 3rd party, only on site when required | Low |

Emissions to Water

| Source | Emission | Pathway | Receptors | Controls | Residual Risk |
| --- | --- | --- | --- | --- | --- |
| Trade effluent | Organic load, fats | Sewer → STW → watercourse | Wince Brook NGR SD 89248 04298 | Consent limits, grease traps, monitoring | Low |
| Yard runoff | Oils, silt | Surface water drains → attenuation | Wince Brook NGR SD 89248 04298 | Interceptors, penstocks, inspection | Low |
| Firewater runoff | Contaminated water | Overland flow / drainage | Wince Brook NGR SD 89248 04298 | Firewater containment, shut‑off valves | Low |
| Chemical spill | Cleaning chemicals | Drainage or ground | Surface water | Bunding, COSHH storage, spill kits | Low |

Emissions to Land

| Source | Emission | Pathway | Receptors | Controls | Residual Risk |
| --- | --- | --- | --- | --- | --- |
| Chemical storage | Liquids | Ground infiltration | Soil, groundwater | Bunded storage, sealed surfaces and bulk chemicals stored inside the building | Low |
| Waste storage | Leachate | Ground | Soil | Sealed containers, frequent removal | Low |
| Ammonia plant oils | Oils | Ground | Soil | Secondary containment, inspections | Low |

Noise and Odour

| Source | Impact | Pathway | Receptors | Controls | Residual Risk |
| --- | --- | --- | --- | --- | --- |
| Plant & machinery | Noise | Airborne | Residents | Acoustic design, Noise Attenuation Barriers & Maintenance | Low |
| Cooking activities | Odour | Airborne | Residents | Extraction, BAT-aligned controls | Low |
| Yard activity | Noise | Airborne | Residents | Operating hours, vehicle controls, Acoustic design, Noise Attenuation Barriers maintenance | Low |

- Accident and Abnormal Scenarios

The following scenarios have been assessed:

- Ammonia release from refrigeration plant

- Fire and contaminated firewater runoff

- Major chemical spill

- Drainage system failure

- Power failure affecting control systems

All scenarios are managed via:

- Ammonia Emergency Response Plan

- Surface Water & Drainage Incident Response Procedure

- Fire Prevention and Emergency Plans

- Staff training and drills

Residual risks are assessed as Low following mitigation.

- BAT and Supporting Assessments

This ERA is supported by the following documents:

- EHS IMS 9.1.4.1 – BAT Gap Analysis Register

- H1 Air and H1 Water Risk Assessments

- Odour Management Plan

- Surface Water Management and Emergency Response Plan

- Ammonia Emergency Release Plan

- Air Quality Assessment prepared by SLR Consulting Limited (SLR Project No. 440.v13945.00001, Revision 03, January 2026).

BAT conclusions for the Food and Drink sector have been applied to ensure emissions are prevented or minimised at source.