- Purpose and Scope

This H1 Emissions to Water Risk Assessment has been prepared in accordance with: - Risk assessments for your environmental permit – GOV.UK - Surface water pollution risk assessment for your environmental permit – GOV.UK - EA H1 guidance (source–pathway–receptor methodology)

The assessment covers indirect discharges via sewer, together with surface water pollution risks arising from normal operations, abnormal events and accident scenarios.

- Site Drainage and Discharge Summary

- On-site drainage: The installation operates separate foul/trade effluent and surface water drainage systems within the site boundary.

- Surface water: Surface water from roofs and yards is routed via interceptors and attenuation ponds prior to discharge off-site.

- Point of combination: Attenuated surface water connects to the foul/trade effluent drainage at manhole S33a, constructed on an existing sewer stub.

- Downstream drainage: From S33a onwards, the drainage system operates as a combined sewer.

- Discharge classification: All flows leave the site as an indirect discharge to sewer, conveyed to Oldham WwTW for treatment prior to final effluent discharge to Wince Brook. (NGR SD 89248 04298)

- Receptors

Primary Receptors

- Public sewer network

- Sewage Treatment Works (STW)

Secondary / Downstream Receptors

- Downstream controlled waters following STW discharge

- Wince Brook (identified as a sensitive surface water receptor within the wider catchment)

Other Environmental Receptors

- Soil and made ground

- Groundwater (non‑principal aquifer; no abstractions on site)

- Sources of Potential Water Pollution

- Trade effluent from food production and washdown

- Fats, oils and grease (FOG)

- Cleaning chemicals (diluted)

- Yard runoff (silt, oils)

- Firewater runoff

- Accidental chemical or oil spills

- Source – Pathway – Receptor Risk assessment (Indirect Discharge)

Normal Operations – Trade Effluent

| Source | Hazard | Pathway | Receptor | Controls | Residual Risk |
| --- | --- | --- | --- | --- | --- |
| Process effluent | Organic load, FOG | Sewer | STW | Trade effluent consent, flow limits, grease traps, monitoring | Low |
| Washdown | Detergents (diluted) | Sewer | STW | Approved chemicals, COSHH, dilution controls | Low |

Abnormal and Accidental Scenarios

| Scenario | Hazard | Pathway | Receptor | Controls | Residual Risk |
| --- | --- | --- | --- | --- | --- |
| Grease trap failure | FOG overload | Sewer | STW | Routine inspection, maintenance, alarms | Low |
| Chemical spill to drain | Cleaning chemicals | Sewer | STW | Bunded storage, drain protection, spill kits | Low |
| Firewater runoff | Contaminated water | Surface drains | STW | Penstocks, firewater containment plan | Low |
| Interceptor failure | Oils/silt | Surface water | STW | Maintenance, inspection regime | Low |

- Surface Water Pollution Risk Assessment

A surface water pollution risk assessment has been undertaken in line with EA guidance. Key controls include:

- Separate foul and surface water drainage systems

- Interceptors on yard drainage

- Penstock valves to isolate surface water in an emergency

- Attenuation systems to control discharge rate

- Surface water emergency response procedures

These measures prevent uncontrolled releases to surface water and protect downstream receptors, including Wince Brook.

- Mitigation and Management Measures

- Trade effluent consent compliance and monitoring

- Planned maintenance of drainage, interceptors and grease traps

- Approved chemical management and COSHH controls

- Spill prevention and response equipment

- Staff training and emergency response drills

- Conclusion

This H1 Emissions to Water Risk Assessment demonstrates that:

- All process effluent is discharged indirectly to sewer under consent

- Robust engineering and management controls are in place

- Surface water pollution risks are effectively managed

- Residual risk to controlled waters, including the Wince Brook, is Low

The installation is therefore not expected to cause pollution of surface water or harm to the water environment.