## Tracker
DS Installation Permit Duly Made Actions Responses no later than 20/02/2024
Action # | Topic | Requirement | Action | Attachment | Responsible | Status
1 | Payment of enhanced pre-application fees | Fee (£850) for enhanced pre-application advice (reference EPR/HP3728SN/P001) has not yet been paid. If paid already provide a copy of the bank transaction details for the payment and highlight the details that relate to the pre-application fee. We can then cross reference the payment with our records. | Send Kirstie evidence of payment for enhanced pre-application advice (reference EPR/HP3728SN/P001) | Yes | SP
2 | Missing documents/items Air emissions | Application refers to, ‘H1_Moderna_VOC Air Emissions FINAL 13.12.23’. Please provide a copy of the document. | Send Kirstie document ‘H1_Moderna_VOC Air Emissions FINAL 13.12.23’ | Yes | SP
3 | Missing documents/items Water emissions |  | Send Kirstie document Partly redacted ‘H1_Moderna_water | Yes | SP
4 | Missing documents/items Boundary plan | Dedicated installation boundary plan, suitable for inclusion in the permit. Provide installation boundary plan prepared in accordance with application form Part B2 Guidance Section 5. | Request update from BN and send Kirstie a plan or plans for the site to include Date and a reference Drawn accurately to a defined scale Outline of the site must be clearly marked Include any local features must be legible at A4 size, drawn to scale and include a scale bar. | Yes | SP/BN
5 | Application Form Part B3. | The declaration in Part B3 Appendix 1, question 13 must be made by an authorised signatory (as was also the case for the declaration in application form Part F1). | Nic Chornet signature and resubmit application form Part B3. | Yes | SP
6 | Missing documents/items Form B6 | A groundwater point source activity can include discharges to ground via infiltration systems. These will be point source discharges and Form B6 will have to be filled in NOT form B7. Application form part B6 must be submitted because our installation includes a point source emission to sewer. | Provide a completed version of application form Part B6. | Yes as follows: Trade Effluent to Sewer Discharge Form Part B6 Surface Water Discharge Form Part B6 Moderna Discharge Supporting Infomation v1.0 200224 TH H1_Moderna_Water Emissions FINAL 14.12.23 | SP
7 | BAT status of backup diesel engines Refer to Supplementary combustion sector (Part A installations) basic pre-application advice sheet section titled ‘Emergency standby diesel generators’ | Application indicates that the proposed backup engines are not compliant with Best Available Techniques (BAT) with regard to emissions optimisation, stating that ‘the standard achieved is expected to be of the order of 3g’ NOx rather than the 2g NOx stated in the guidance, and without secondary abatement. Therefore: | Conduct dispersion modelling for pollutants of concern Nox and PM10. | - | SP | Provide justification for use of non 2g standard generators to KL by 12 Mar24
8 |  | a. Provide the reasoning for selecting the proposed engines, justifying why it is acceptable to deviate from BAT. It is unlikely that we would accept the cost of BAT compliant engines as justification for the selection of non-BAT engines. | Review EDG specification and ERM assessment and proposed plan | -
9 |  | b. Provide manufacturer’s specification sheets that detail the expected NOx emission concentrations from the engines. | Provide manufacturer’s specification sheet | -
10 |  | c. Confirm whether the dispersion of flue gases is optimised through vertical stacks with no caps and cowls impediments. (Best dispersion from vertical stack) | Confirm what modifications are required (exhaust flues) to achieve dispersion following dispersion modelling | -
11 |  | d. No air emissions monitoring has been proposed in the application. However, in accordance with the ‘less than 500 operating hours per year exemption’ detailed in our guidance the engines will need to be monitored every 1,500 operating hours or every 5 years, whichever comes first. Our guidance on Monitoring stack emissions: low risk MCPs and specified generators. would apply. Confirm that the engines will be monitored in accordance with our guidance. | Response Yes engines will be monitored in accordance with guidance, every 1,500 operating hours or every 5 years, whichever comes first | No
12 | Other 7. Table 8.1 of the application Supporting Information Document lists: | inorganic salts’ as a raw material. Please provide chemical names for all inorganic salts used. |  |  | JJL
13 | Other 7. Table 8.1 of the application Supporting Information Document lists: | ‘SAM powder’. Explain what this is, with chemical name if relevant. |  |  | JJL
14 | Operating hours | Confirm intended operating hours of the site. Will the site ever operate at night? Will the generators ever be tested at night? What are the likely sources of noise from the site at night? | 8.) Confirm Operating hours 8.1. Please confirm the intended operating hours of the site. 24/7, 10 months per year 8.2 Will the site ever operate at night? YES (worst case) 8.3 Will the generators ever be tested at night? NO 8.4 What are the likely sources of noise from the site at night? - Chiller, Heat pumps, Transformers |  | JJL
15 | Additional fee for habitats assessment. | This is not required because there are no statutory conservation sites within relevant screening distances of the installation. I will therefore arrange for the fee to be refunded (£779). separate to the requirement for additional fee previously mentioned in point 1 above because the payment was made under a different reference number (i.e. EPR/TP3822SV/A001). | (Kirstie Lythgo) | -
16 | Commercial confidentiality assessment | Kirstie to complete now once application received in full. Kirstie may need to request and agree an extension of time with you to agree confidentiality. This is in accordance with EA procedures. | Review requirement for any redaction of responses and provide redacted as well as unredacted versions as appropriate. Note: Emissions data is default entry on public register | Yes | SP/JJL