## Long Term Inputs
Input Data
Emission Point | Substance | Emission Concentration (mg/m3) | Total flow (m3/s) | Effective height of release (m) | Release Rate (g/s)
A1 (Fume hood exhaust) | Hydrochloric Acid, 6 mol/L | 0.001 | 0.41111 | 0 | 4.1111e-07
| Glacial Acetic Acid | 0.93 | 0.41111 | 0 | 0.00038233
| 100% Ethanol | 0.3 | 0.41111 | 0 | 0.00012333
A2 (QC lab) | Acetonitrile | 0.42 | 1.6439 | 0 | 0.00069043
| Formic Acid | 0.01 | 1.6439 | 0 | 1.6439e-05
| Acetic Acid | 0.04 | 1.6439 | 0 | 6.5756e-05
| Methanol | 0.11 | 1.6439 | 0 | 0.00018083
| IPA | 0.42 | 1.6439 | 0 | 0.00069043
| Ethanol | 0.42 | 1.6439 | 0 | 0.00069043
| 1,1,1,3,3,3-Hexafluro-2-propanol (HFIP) | 0.01 | 1.6439 | 0 | 1.6439e-05
| Hydrochloric Acid, 1 mol/L | 0.01 | 1.6439 | 0 | 1.6439e-05
| Tetrahydrofuran | 0.24 | 1.6439 | 0 | 0.00039453
| N,N-Diisopropylethylamine (DIEA) | 0.002 | 1.6439 | 0 | 3.2878e-06
| Chloroform | 0.02 | 1.6439 | 0 | 3.2878e-05
| Hydrogen peroxide 30% | 0.01 | 1.6439 | 0 | 1.6439e-05
| Phenol, Chloroform, Isoamyl Alcohol | 0.01 | 1.6439 | 0 | 1.6439e-05
Assumptions
Effective height based on stack above building being 3.5 m high, building height 12.7 m as per EA guidance (https://www.gov.uk/guidance/air-emissions-risk-assessment-for-your-environmental-permit#pc-dispersion-factor)
Concentrations based on 16 hours operating per day max 240 days per year

## Long Term Test 1&2
Input Data
| Release Rate g/s |  | Total Release Rate g/s | Annual Dispersion Factor (ug/m3 / g/s)) | PC to air (Annual) (ug/m3) | Long Term EAL (ug/m3) | Comments | PC < 1% of long term EAL?
Substance | A1 | A2
Acetonitrile |  | 0.00069043 | 0.00069043 | 148 | 0.10218 | 680 | EAL | Yes
Formic Acid |  | 1.6439e-05 | 1.6439e-05 | 148 | 0.002433 | 96 | https://assets.publishing.service.gov.uk/media/5f510e86d3bf7f329285a027/Derivation_of_new_EALs_to_air.pdf AND https://www.hse.gov.uk/pubns/priced/eh40.pdf, 9600ug/m3 8hr WEL, divide by 100 as per EA H1 Annex F | Yes
Acetic Acid | 0.00038233 | 6.5756e-05 | 0.00044809 | 148 | 0.066317 | 250 | EAL | Yes
Methanol |  | 0.00018083 | 0.00018083 | 148 | 0.026763 | 2660 | EAL | Yes
IPA (2-propanol) |  | 0.00069043 | 0.00069043 | 148 | 0.10218 | 9990 | EAL | Yes
Ethanol | 0.00012333 | 0.00069043 | 0.00081377 | 148 | 0.12044 | 19200 | EH40 Workplace Exposure Limits (https://www.hse.gov.uk/pubns/priced/eh40.pdf) 1920000, divided by 100 as per EA H1 Annex F | Yes
1,1,1,3,3,3-Hexafluro-2-propanol (HFIP) |  | 1.6439e-05 | 1.6439e-05 | 148 | 0.002433 | 5 | no short term tox data found, used benzene as proxy | Yes
Hydrochloric Acid | 4.1111e-07 | 1.6439e-05 | 1.685e-05 | 148 | 0.0024938 | n/a | no long term EAL
Tetrahydrofuran |  | 0.00039453 | 0.00039453 | 148 | 0.058391 | 3000 | EAL | Yes
N,N-Diisopropylethylamine (DIEA) |  | 3.2878e-06 | 3.2878e-06 | 148 | 0.00048659 | 5 | benzene as proxy | Yes
Chloroform |  | 3.2878e-05 | 3.2878e-05 | 148 | 0.0048659 | n/a | no long term EAL
Hydrogen peroxide |  | 1.6439e-05 | 1.6439e-05 | 148 | 0.002433 | 14 | https://assets.publishing.service.gov.uk/media/5f510e86d3bf7f329285a027/Derivation_of_new_EALs_to_air.pdf AND https://www.hse.gov.uk/pubns/priced/eh40.pdf, 1400ug/m3 8hr WEL, divide by 100 as per EA H1 Annex F | Yes
Phenol, Chloroform, Isoamyl Alcohol |  | 1.6439e-05 | 1.6439e-05 | 148 | 0.002433 | 3.66 | https://assets.publishing.service.gov.uk/media/5f510e86d3bf7f329285a027/Derivation_of_new_EALs_to_air.pdf AND https://www.hse.gov.uk/pubns/priced/eh40.pdf, Phenol EAL = 200 ug/m3 EAL chloroform = n/a no long term EAL WEL isoamyl alcohol (aka 3-Methylbutan-1-ol) = 366ug/m3, divide by 100 as per EA H1 Annex F = 3.66 ug/m3 use most stringent as EAL = 3.66 ug/m3 | Yes
Dispersion factors taken from EA guidance based on 0 m effective height (https://www.gov.uk/guidance/air-emissions-risk-assessment-for-your-environmental-permit#pc-dispersion-factor)

## Short Term Inputs
Input Data
Emission Point | Substance | Emission Concentration (mg/m3) | Total flow (m3/s) | Effective height of release (m) | Release Rate (g/s)
A1 (Fume Hood Exhaust) | Hydrochloric Acid, 6 mol/L | 0.02 | 0.41111 | 0 | 8.2222e-06
| Glacial Acetic Acid | 14.88 | 0.41111 | 0 | 0.0061173
| 100% Ethanol | 4.77 | 0.41111 | 0 | 0.001961
A2 (QC Lab) | Acetonitrile | 6.7293 | 1.6439 | 0 | 0.011062
| Formic Acid | 0.204 | 1.6439 | 0 | 0.00033536
| Acetic Acid | 0.70231 | 1.6439 | 0 | 0.0011545
| Methanol | 1.6952 | 1.6439 | 0 | 0.0027867
| IPA | 6.7293 | 1.6439 | 0 | 0.011062
| Ethanol | 6.755 | 1.6439 | 0 | 0.011104
| 1,1,1,3,3,3-Hexafluro-2-propanol (HFIP) | 0.12842 | 1.6439 | 0 | 0.00021111
| Hydrochloric Acid | 0.098992 | 1.6439 | 0 | 0.00016273
| Tetrahydrofuran | 3.8056 | 1.6439 | 0 | 0.0062559
| N,N-Diisopropylethylamine (DIEA) | 0.039704 | 1.6439 | 0 | 6.5269e-05
| Chloroform | 0.39864 | 1.6439 | 0 | 0.00065532
| Hydrogen peroxide 30% | 0.089093 | 1.6439 | 0 | 0.00014646
| Phenol, Chloroform, Isoamyl Alcohol | 0.17123 | 1.6439 | 0 | 0.00028148
Assumptions
Effective Height based on stack above building being 3.5 m high, building height 12.7 m as per EA guidance (https://www.gov.uk/guidance/air-emissions-risk-assessment-for-your-environmental-permit#pc-dispersion-factor)
Concentrations based on 1 hour operating per day max 240 days per year

## Short Term Test 1&2
Input Data | [7 empty] | Test 1
| Release Rate g/s |  | Total Release Rate g/s | Hourly Dispersion Factor (ug/m3 / g/s)) | PC to air (hourly) (ug/m3) | Short Term EAL (ug/m3) | Comments | PC < 10% of short term EAL?
Substance | A1 | A2
Acetonitrile |  | 0.011062 | 0.011062 | 3900 | 43.1427 | 10200 | EAL | Yes
Formic Acid |  | 0.00033536 | 0.00033536 | 3900 | 1.3079 | n/a | https://assets.publishing.service.gov.uk/media/5f510e86d3bf7f329285a027/Derivation_of_new_EALs_to_air.pdf AND https://www.hse.gov.uk/pubns/priced/eh40.pdf, no short term exposure limit
Acetic Acid | 0.0061173 | 0.0011545 | 0.0072718 | 3900 | 28.3602 | 3700 | EAL | Yes
Methanol |  | 0.0027867 | 0.0027867 | 3900 | 10.868 | 33300 | EAL | Yes
IPA (2-propanol) |  | 0.011062 | 0.011062 | 3900 | 43.1427 | 125000 | EAL | Yes
Ethanol | 0.001961 | 0.011104 | 0.013065 | 3900 | 50.9552 | 1920000 | EH40 Workplace Exposure Limits (https://www.hse.gov.uk/pubns/priced/eh40.pdf) | Yes
1,1,1,3,3,3-Hexafluro-2-propanol (HFIP) |  | 0.00021111 | 0.00021111 | 3900 | 0.82333 | 14.03 | msds (fishersci.com), LC50 4h = 1974ppm, assume 1/1000000 safety factor = 14.03 ug/m3 | Yes
Hydrochloric Acid | 8.2222e-06 | 0.00016273 | 0.00017095 | 3900 | 0.66672 | 750 | EAL | Yes
Tetrahydrofuran |  | 0.0062559 | 0.0062559 | 3900 | 24.3981 | 59900 | EAL | Yes
N,N-Diisopropylethylamine (DIEA) |  | 6.5269e-05 | 6.5269e-05 | 3900 | 0.25455 | 5 | Treated as 100% benzene | Yes
Chloroform |  | 0.00065532 | 0.00065532 | 3900 | 1.5079 | 100 | EAL - 24hr mean | Yes
Hydrogen peroxide |  | 0.00014646 | 0.00014646 | 3900 | 0.57119 | 280 | https://assets.publishing.service.gov.uk/media/5f510e86d3bf7f329285a027/Derivation_of_new_EALs_to_air.pdf AND https://www.hse.gov.uk/pubns/priced/eh40.pdf, STEL = 2800ug/m3, divide by 10 as per EA H1 Annex F | Yes
Phenol, Chloroform, Isoamyl Alcohol |  | 0.00028148 | 0.00028148 | 3900 | 1.0978 | 45.8 | https://assets.publishing.service.gov.uk/media/5f510e86d3bf7f329285a027/Derivation_of_new_EALs_to_air.pdf AND https://www.hse.gov.uk/pubns/priced/eh40.pdf, Phenol EAL = 3900 ug/m3 EAL chloroform = 100 ug/m3 STEL isamyl alcohol (aka 3-Methylbutan-1-ol) = 458ug/m3, divide by 10 as per EA H1 Annex F = 45.8 ug/m3 use most stringent as EAL = 45.8 ug/m3 | Yes
Dispersion factors taken from EA guidance based on 0 m effective height (https://www.gov.uk/guidance/air-emissions-risk-assessment-for-your-environmental-permit#pc-dispersion-factor)
Background concentrations conservatively based on half EAL for benzene as no background data
Multiplied by 0.59 to covert to 24 hour average as 24 short term EAL used as per EA gudance on averaging periods (https://www.gov.uk/guidance/air-emissions-risk-assessment-for-your-environmental-permit#pc-dispersion-factor)