## Concentrations
Inputs
| Raw Material | Consumption of raw material (kg/year) | Raw material discharged to wastewater (%) | Hazardous Component (based on SDSs) | Composition (wt%) | Hazardous Component discharged (kg/year) | Component discharge rate (mg/year) | Annual wastewater flowrate (t/a) | Annual wastewater flow rate (l/year) | Annual average conc (mg/l)
Cleaning & Disinfection | CIP 100 |  | 100 | Potassium Hydroxide | 30 | 0 | 0 | 7268 | 7268000 | 99.0644
|  |  |  | Tetrasodium (EDTA) | 5 | 0 | 0 | 7268 | 7268000 | 16.5107
| CIP 200 |  | 100 | Phosphoric Acid | 60 | 0 | 0 | 7268 | 7268000 | 198.1288
|  |  |  | Citric Acid | 7 | 0 | 0 | 7268 | 7268000 | 23.115
Manufacturing, incl Buffer Prep and Chromato-graphy Column Packing | Dithiothreitol |  | 100 | DTT | 100 | 0 | 0 | 7268 | 7268000 | 5.7788
| Alkylpolyamine |  | 100 | 4-Azaoctamethylenediamine | 100 | 0 | 0 | 7268 | 7268000 | 0.11007
| EDTA |  | 100 | Disodium dihydrogen ethylenediaminetetraacetate dihydrate | 100 | 0 | 0 | 7268 | 7268000 | 93.2856
| Sodium Hydroxide Pellets |  | 100 | Sodium Hydroxide | 100 | 0 | 0 | 7268 | 7268000 | 76.087
| Sodium Hydroxide (10 mol/L) |  | 100 | Sodium Hydroxide | 30 | 0 | 0 | 7268 | 7268000 | 7.9252
| Hydrochloric Acid (6 mol/L) |  | 100 | Hydrochloric Acid | 40 | 0 | 0 | 7268 | 7268000 | 0.013759
| Ethanol |  | 100 | Ethanol | 100 | 0 | 0 | 7268 | 7268000 | 3.1095
Effluent waste water treatment | Sulphuric Acid |  | 100 | Sulphuric Acid | 59.14 | 0 | 0 | 7268 | 7268000 | 16.2741
| Sodium Hydroxide (50%) |  | 100 | Sodium Hydroxide | 52 | 0 | 0 | 7268 | 7268000 | 14.3093

## Combined Concentrations
| Cleaning and Disinfection | Manufacturing | Effluent Waste Water Treatment | Total quantity | Total Concentration
| kg/a | kg/a | kg/a | kg/a | ug/l
Potassium Hydroxide |  |  |  | 720 | 99064.3919
Tetrasodium (EDTA) |  |  |  | 798 | 109796.3676
Phosphoric Acid |  |  |  | 1440 | 198128.7837
Citric Acid |  |  |  | 168 | 23115.0248
DTT |  |  |  | 42 | 5778.7562
4-Azaoctamethylenediamine |  |  |  | 0.8 | 110.0715
Sodium Hydroxide |  |  |  | 714.6 | 98321.4089
Hydrochloric Acid |  |  |  | 0.1 | 13.7589
Ethanol |  |  |  | 22.6 | 3109.5212
Sulphuric Acid |  |  |  | 118.28 | 16274.0782

## H1 Test
|  | 20500 | [15 empty] | H1 Screening Tests
Input Data | [17 empty] | Test 1 |  | Test 2 |  | Test 3 |  | Test 4
Substance | Release Concentration (ug/l) (AA) | Release Concentration (ug/l) (MAC) | Discharge volume (m3/s) (average) | Discharge volume (m3/s) (max) | 95% Exceedance river flow (m3/s) | Effluent Flow Rate x Release Concentration (Average) (ug/s) | Effluent Flow Rate x Release Concentration (Max) (ug/s) | Effluent Flow Rate + River Flow Rate (m3/s) | PC (AA) (ug/l) | PC (MAC) (ug/l) | Background Concentration (ug/l) | RFR<x10 EFR? | PEC (AA) | PEC (MAC) | Freshwater EQS (ug/l) (Long term/AA) | Freshwater EQS (ug/l) (Short term/MAC) | Comments/Source (EQS or other) | Test 1 (Substance <10% of AA EQS?) | Test 1 (Substance <10% of MAC EQS?) | Test 2 (Substance < 4% of AA EQS) | Test 2 (Substance < 4% of MAC EQS) | Test 3 (BC - PEC <10% of AA EQS) | Test 3 (BC - PEC <10% of MAC EQS) | Test 4 (PEC < AA EQS) | Test 4 (PEC < MAC EQS)
Potassium Hydroxide | 99064.3919 | 99064.3919 | 0 | 0 | 3.3 | 0 | 0 | 3.3 | 0 | 0 |  |  |  |  | N/A | 80000 | Short term value taken from LC50 toxicity to fish from SDS |  | Fail |  | Pass
Tetrasodium (EDTA) | 109796.3676 | 109796.3676 | 0 | 0 | 3.3 | 0 | 0 | 3.3 | 0 | 0 |  |  |  |  | 400 | 4000 | Freshwater EQS | Fail | Fail | Pass | Pass
Phosphoric Acid | 198128.7837 | 198128.7837 | 0 | 0 | 3.3 | 0 | 0 | 3.3 | 0 | 0 |  |  |  |  | N/A | 3500 | Short term value taken from LC50 toxicity to fish from SDS |  | Fail |  | Pass | #VALUE! | Pass | Pass | Pass
Citric Acid | 23115.0248 | 23115.0248 | 0 | 0 | 3.3 | 0 | 0 | 3.3 | 0 | 0 |  |  |  |  | N/A | 1516000 | Short term value taken from LC50 toxicity to fish from SDS |  | Pass
DTT | 5778.7562 | 5778.7562 | 0 | 0 | 3.3 | 0 | 0 | 3.3 | 0 | 0 |  |  |  |  | N/A | 34800 | Short term value taken from EC50 invertebrates from ECHA. https://echa.europa.eu/registration-dossier/-/registered-dossier/31622/6/2/1 |  | Fail |  | Pass
4-Azaoctamethylenediamine | 110.0715 | 110.0715 | 0 | 0 | 3.3 | 0 | 0 | 3.3 | 0 | 0 |  |  |  |  | N/A | N/A | No EQS/alternative data available
Sodium Hydroxide | 98321.4089 | 98321.4089 | 0 | 0 | 3.3 | 0 | 0 | 3.3 | 0 | 0 |  |  |  |  | N/A | 45400 | Short term value taken from LC50 toxicity to fish from SDS |  | Fail |  | Pass
Hydrochloric Acid | 13.7589 | 13.7589 | 0 | 0 | 3.3 | 0 | 0 | 3.3 | 0 | 0 |  |  |  |  | N/A | 20500 | Short term value taken from LC50 fishes ECHA. No long term value available. https://echa.europa.eu/registration-dossier/-/registered-dossier/15859/6/2/2 |  | Pass
Ethanol | 3109.5212 | 3109.5212 | 0 | 0 | 3.3 | 0 | 0 | 3.3 | 0 | 0 |  |  |  |  | N/A | 15300000 | Short term value taken from EC50 toxicity to fish from SDS |  | Pass
Sulphuric Acid | 16274.0782 | 16274.0782 | 0 | 0 | 3.3 | 0 | 0 | 3.3 | 0 | 0 |  |  |  |  | N/A | 28000 | Short term value taken from LC50 toxicity to fish from ECHA. https://echa.europa.eu/information-on-chemicals/registered-substances/-/disreg/substance/100.028.763 |  | Fail |  | Pass
River flow from: | NRFA Station Mean Flow Data for 39002 - Thames at Days Weir (ceh.ac.uk)
Note on M3: Taraka Rhodes: Estimated data taken from raw water sampling in dock