Title	Odour Assessment Report
Site	SPALDING WRC
Purpose of report	Waste Permit Application

Project Personnel and Contacts
ROLE		NAME	LOCATION
Client		Nathan Ward	Spalding WRC, West Marsh Road, Spalding, Lincolnshire / Spalding, PE11 3UL
Author		Omid Shafibeik / (Senior Modeller)	Thorpe Wood House, / Peterborough, PE3 6WT
Checked by / Version Control		Kate Rider / (Strategic Waste Planner)	Lancaster House, / Huntingdon, PE29 6XU
VERSION	DATE	BY AMENDMENT REASON

CONTENTS
1. Executive summary
2. Introductions
  1. Existing Wastewater Treatment Processes
    1. Consent and Current compliance
  2. Odour Assessment Modelling
  3. Odour Survey and Emissions Data
3. Atmospheric Modelling method
  1. Modelling method
  2. Meteorological data
  3. AERMOD
    1. Control Options
    2. Sources and emissions input
    3. Receptors Network
4. Dispersion Modelling Results
5. Conclusions
6. Recommendations

1	Executive summary
Spalding Water Recycling Centre (WRC) has been identified for emergency sludge cake storage because it has a large concreted area, and leachate from the sludge cake cannot seep into the ground and can be safely treated on site.
Odour models are required as part of waste permit applications for all of Anglian Water’s (AW) Sludge Treatment Centres (STC).
Spalding Water Recycling Centre (WRC) already has a two-waste operation permits under Environmental Permitting Regulations (EPR) but requires a permit variation under IED.
Anglian Water Services (AWS) are applying for a Bespoke Permit for the STC waste activity due to the a Environment Agency (EA) decision has been made that biosolid storage facilities at Water Recycling Centre (WRCs) and STCs should be permitted under the Environmental Permitting Regulations.
AW needs to demonstrate that the STCs have minimal impact at the permit boundary and comply to H4.
The STC odour sources plus 4000 tonnes of sludge cake (50% raw and 50% advanced treated) stored on the large concrete area on the north side of the site were modelled with three years of meteorological data. A model run was completed with each year of meteorological data to determine the odour impacts from Spalding STC on the surrounding area.
With the meteorological year that produced the worst-case scenario, the effects of odour dispersion were also examined considering all sludge cake storage area with;
- Storing 100% of area with raw sludge cake (figure 10).
- Storing 100% of area with advanced digested sludge cake (figure 11).
- Storing sheeted sludge cake (covered by synthetic plastic sheet to prevent odour release shown in figure 12).

An odour impact assessment using AERMOD (9.9.0) was undertaken to determine the odour exposure levels across the areas surrounding the STC.
The modelling methods used are based on assessment techniques that are presented within guidance published by the EA, DEFRA, and the Institute of Air Quality Management (IAQM).
An odour concentration of 1.5 Odour Units Per Cubic Metre (OU/m3) has been taken as the benchmark level at which nuisance and potential loss of amenity would be anticipated. This assessment criterion for the protection of public nuisance/amenity is in line the EA H4 Planning Guidance, including septic effluent and sludge in amongst a range of substances categorised as most offensive and for which a low detection threshold should be taken into consideration.
The odour emission rates used for the modelling study were based on the olfactometric samples collected and analysed for sludge cake from similar odour sources at AW different STCs and Hydrogen Sulphide survey carried out by H&M Environmental consultants on 22/06/2021.
Certified processed meteorological data (2017-2019) from Wittering meteorological station, representative of Spalding WRC was obtained from Atmospheric Dispersion Modelling Ltd (ADM Ltd) for the modelling study.
The atmospheric dispersion model AERMOD was used to predict the dispersion of odour from the STC, utilising meteorological data and the odour sources details.
The modelling showed that the odour from the STC with sludge cake storage extend beyond the water recycling centre (WRC) boundary and affect nearby sensitive receptors around the site.
To reduce the odour to acceptable levels, sheeting should be provided over the stored sludge cake.

2	Introduction
Spalding WRC is located to the north Spalding town, next to the river Welland. The WRC coordinates are given in Figure 1. The site approximate centre point is at X=560342 E, Y=322145 N.

Figure 1: Spalding WRC-Coordinates
The site address is as follows:
Spalding WRC (Site short code =SPALST)
Spalding WRC, West Marsh Road, Spalding, Lincolnshire, Spalding, PE11 3UL
Grid reference: TF 2617425127

The WRC location map and the area occupied by the STC for EA permitting are given in figure 2.

Figure 2: Spalding WRC location map and STC, EA permitting area.
The WRC site boundary is shown in red, and the EA permit area boundaries are shown in green. Figure 2 also gives details for advanced digested sludge cake cake storage areas.
## 2.1 The Existing Wastewater Treatment Processes
Spalding WRC and STC is located Spalding Sludge Treatment Centre, West Marsh Lane, Spalding, Lincolnshire, PE11 3UL (NGR: TF 26174 25127).

The sludge from primary settlement tanks is periodically withdrawn and into a concrete gallery under the old redundant sludge storage tanks. From the gallery sludge is pumped to the strain press for screening. The screenings are stored in 8 cubic yard skip under the strain press and is removed to landfill.
Screened sludge is stored in the primary sludge storage tank. From this tank sludge is pumped to the Gravity Belt Thickener (GBT) to be thickened.

The thickened sludge is stored in the covered thickened sludge storage tank and is periodically removed off site.

There is also a large, concreted area (143m x45m) that has been identified for emergency sludge cake storage. For storage of sludge cake hard standing area is required to prevent leachate from the sludge cake to seep into the ground and to be safely treated on site.

## 2.2 Odour assessment and modelling
Investigative modelling study was carried out to assess odour impacts from Spalding WRC on the surrounding area.
## 2.3 Odour Survey and emissions data
AWS developed an odour dispersion model for Spalding WRC in 2014. Over the years the model has been updated to include the latest developments and operating regime of the treatment plant.
The odour emission rates used for sludge cake are based on actual olfactometric samples taken and analysed by specialised odour contractors in an accredited odour laboratory. Some samples were collected by H&M Environmental Ltd, and some were collected by Silsoe Odours. All samples were analysed in Silsoe Odours olfactometry laboratory.
Olfactometry is a sensory measurements that employs the human nose as the odour detector and hence relate to the effect of odours as experienced by humans. The most common sensory measurement is threshold olfactometry which measures the odour concentration in terms of dilution required to reduce an odorous compound until its threshold concentration.
The other emission rates are based actual hydrogen sulphide survey carried out by H&M Environmental on 22/06/2021 and AW previous experiences from other site and emissions recommended by Water Research Council (WRc). The emission rates for covered odour sources have been reduced by 70% according to research and recommendations by WRc.
The purpose of this emissions data is to support conclusions to be drawn on prevailing odour risk and to provide source data for the odour dispersion modelling.
# 3 Atmospheric Dispersion Modelling
Atmospheric dispersion modelling is the mathematical simulation of how air pollutants disperse in ambient atmosphere. It is solved by computer programmes that use mathematical equations and algorithms which simulate the pollutants dispersion. The dispersion models are used to estimate or to predict the downwind concentration of air pollutants emitted from sources such as wastewater treatment plants, industrial plants, and vehicular traffic.
Atmospheric dispersion modelling is a well-documented and recognised technique to predict the dispersion of malodours. Modelling was undertaken using the AERMOD computer programme (release version 9.9.0).
AERMOD is recognised by the Environment Agency, UK Met Office, and the US Environmental Protection Agency. AERMOD uses meteorological data, terrain data and emission data as input to predict the dispersion of odours.
## 3.1 Modelling Method
Six steps were followed in the modelling of odour dispersed from Spalding STC.
1. Certified pre-processed meteorological data was purchased from an independent source (Atmospheric Dispersion Modelling) for the WRC.
2. Terrain data was processed for use in the model.
3. Source emission data used were based on actual WRC olfactometric samples taken and analysed in specialised laboratory over the past years.
4. The processed Met data, process units, sources emission data were all inputted into the AERMOD model.
5. The AERMOD model was compiled and ran.
6. Results from AERMOD are processed by the graphical post-processor. This gives a graphical representation of the odour dispersal on a map of the affected area. These are presented in Section 4 of this report.
Graphical representations of the resultant odour dispersal models over a map of Spalding are presented in Section 4.

## 3.2 Meteorological Data
Meteorology is fundamental for the dispersion of pollutants because it is the primary factor determining the diluting effect of the atmosphere. It is extremely important that the correct meteorological data is used for the modelling study.
Certified meteorological data (2017-2019) from Wittering meteorological station representative of Spalding WRC was purchased from ADM Ltd for the modelling study. ADM Ltd are an independent, accredited source that provide a range of services to industry, developers, consultancies, and government organisations. These services cover the full spectrum of air quality and odour, project management and provision of dispersion modelling software together with terrain and meteorological data.
AERMOD requires the input of data that include hourly averaged values for wind speed and direction, cloud cover, ambient temperature, solar radiation, the amount of atmospheric turbulence, the height of mixing layer and other parameters.
Longitude and latitude of both Spalding WRC and of the meteorological station are given in Table 1.
Table 1: Longitude and latitude of WRC and Meteorological Station.
Location	Latitude	Longitude
Spalding WRC	52.808N	-0.129E
Wittering Met Station	52.671N	0.483W

Wind roses from Wittering station for years 2017-2019 are presented in figures 3 to 5.

Figure 3: 2017 wind rose for Wittering Meteorological Station

Figure 4: 2018 wind rose for Wittering Meteorological Station

### Figure 5: 2019 wind rose for Wittering Meteorological Station
The wind roses indicate the frequency of occurrence of wind from different directions for the number of wind speed ranges.
These wind roses indicate that the prevailing wind direction is blowing from a south westerly direction directing the odours towards a north easterly direction for majority of the time.
During calm days with no wind and low temperatures dispersion is very poor and odours tend to concentrate close to the source.
## 3.3 AERMOD
This section details the control options; source inputs and receptor networks used in the models.
Gaussian plume air dispersion model: AERMOD version 9.9.0 was used for the modelling work. The AERMOD atmospheric dispersion modelling system is a steady-state plume model that incorporates air dispersion based on planetary boundary layer turbulence structure and scaling concept, including treatment of both surface and elevated sources, and both simple and complex terrain.

### 3.3.1 Control Options
The key parameters for the control options of the model are detailed in Table 2 below. The values for dispersion options and averaging time are standard defaults. The rural coefficient is applicable to this location.
#### Table 2: Control Option Parameters
SETTING	VALUE
Dispersion Options	Regulatory Default
Dispersion Coefficient	Rural
Pollutant Averaging time	1 hr
Flagpole Receptors	zero

### 3.3.2 Sources and Emissions Input
Figure 6 gives details of the buildings, covered tanks, and the Odour Control Units and corresponding emission rates within the permit area.

Figure 6: Spalding STC south section – Details of all buildings, covered tanks, odour control units and odour sources within the permitting area.

The buildings are not odour sources. They have been included in the odour model to incorporate the effects of building downwash.
Building downwash occurs as the wind flows over and around buildings and impacts the dispersion of pollution from nearby stacks.
The advanced treated sludge cake emission rate is from olfactometric samples collected by H&M Environmental and analysed by Silsoe Odours from Cotton valley WRC and Whitlingham WRC.
The emission rate for the outlet stack of Gravity Belt Thickener was estimated from onsite H2S measurements on 26/05/2021.
The Primary sludge holding tank and the thickened sludge holding tank are completely covered. According to Water Research Council findings, for the odour sources such as theses covers provide a 70% reduction in odour emission rate.
Water Research Council (WRc) suggest an odour emission rate of 40 ou/m2/sec for an open sludge holding tank with 70% reduction for covers. Therefore, an odour emission rate of 12 ou/m2/sec was used for this tank.
WRc suggest an odour emission rate of 8 ou/m2/sec for an open thickened sludge holding tank with 70% reduction for covers. Therefore, an odour emission rate of 2.4 ou/m2/sec was used for this tank.
All other emission rates are based on the hydrogen sulphide survey carried out by H&M Environmental at Spalding WRC on 22/06/2021.

### 3.3.3 Receptor Network
A uniform polar grid with 30 rings at 50m spacing with 45 radials at 8-degree intervals, extending to 1500m from the centre of STC (X= 526174 E, Y= 325127 N), was placed over the map of the area as a receptors network providing 1350 receptors in and around the STC.
The odour contour maps were generated by orienting the map on the STC centre with a zoom radius of 700m.

## 4.0 Dispersion Modelling Results
The model was run using three meteorological years (2017-2019) considering 4000 tonnes (area= 51m x 51m with working height of 1.5m) of sludge stored on the concrete area at the north side of the treatment plant as shown in figure 2 to test the variability of the odour concentration results among the different years. The sludge storage area consisted of 2000 tonnes of advanced treated sludge and 2000 tonnes of raw sludge.
The effect of storing:
- 4000 tonnes of advanced treated sludge cake,
- 4000 tonnes of raw sludge cake,
- Covering all the stored sludge cake with synthetic plastic cover to eliminate the odour from this source.
were also examined separately with the meteorological year that gave the worst-case scenario.
The 98th percentile of hourly mean odour concentrations has been calculated. Contour lines for odour concentrations of 1.5, 3, 5, and 10 OUE/m3 have been included for all the scenarios. The significance of these odour concentrations is explained below:
- 1 OUE/m3 is the level of odour detection under laboratory conditions.
- 3 OUE/m3 is the level of odour detection in open environment. Complaints are unlikely to occur and exposure below this level are unlikely to constitute significant pollution.
- 5 OUE/m3 is when odour becomes detectable & recognisable. Complaints may occur and depending on the sensitivity of the locality and nature of the odour.
- 10 OUE/m3 is when odour becomes distinct and intrusive. Complaints are highly likely and odour exposure at these levels represents an actionable nuisance.
The odour contour maps for three model runs are shown in figures 7 to 9.

Figure 7: Spalding WRC 98%ile hourly means odour contour map (year 2017).
Zoom radius 700m.

The 98th percentile of hourly mean odour concentrations calculated using 2017 meteorological data show that the 1.5 OUE/m3 contour isopleth extends 577m in north westerly direction and encompasses an area of 242295m2 approximately.

Figure 8: Spalding STC 98%ile hourly means odour contour map (year 2018).
Zoom radius 700m.

The 98th percentile of hourly means odour concentrations calculated using 2018 meteorological data show that the 1.5 OUE/m3 contour isopleth extends 538m in a north westerly direction and encompasses an area of 302820m2 approximately.

Figure 9: Spalding STC 98%ile hourly means odour contour map (year 2019).
Zoom radius 700m.

The 98th percentile of hourly mean odour concentrations calculated using 2019 meteorological data show that the 1.5 OUE/m3 contour isopleth extends 502m in a north westerly direction and encompasses an area of 271483m2 approximately.
The model run with 2018 meteorological data gave the worst-case scenario as the area encompassed under the 1.5 OU/m3 was 25% and 12% larger than modelled years with meteorological data for 2017 and 2019, respectively.
As it can be seen from these contour maps the odour from the STC extend beyond the WRC boundary and affect nearby sensitive receptors around the site.
As 2018 meteorological produced the worst-case scenario, the effects of storage of all 4000 tonnes of raw sludge cake and advanced treated sludge cake were also examined separately, and the results are given in figure 10 and 11.

Figure 10: Spalding STC 98%ile hourly means odour contour map (year 2018) – Storage of
4000 tonnes of raw sludge cake - Zoom radius 700m.

The 98th percentile of hourly mean odour concentrations calculated using 2018 meteorological data and storing only raw sludge cake show that the 1.5 OUE/m3 contour isopleth extends 614m in a north westerly direction and encompasses an area of 395120m2 approximately.
This shows if all the sludge cake storage area was dedicated to storing of raw sludge cake, it would increase the distance and area encompassed by the 1.5 OUE/m3 contour by 14% and 30% compared with storing both advance treated and raw sludge cake.

Figure 11: Spalding STC 98%ile hourly means odour contour map (year 2018) – Storage of
4000 tonnes of advanced digested sludge cake - Zoom radius 700m.

The 98th percentile of hourly mean odour concentrations calculated using 2018 meteorological data and storing only advanced digested sludge cake show that the 1.5 OUE/m3 contour isopleth extends 414m in a north westerly direction and encompasses an area of 173443m2 approximately.
This shows if all the sludge cake storage area was dedicated to storing of advance treated sludge cake, it would decrease the distance and area encompassed by the 1.5 OUE/m3 contour by 23% and 43% compared with storing both advance treated and raw sludge cake.
The effect of covering all the stored sludge cake with synthetic plastic cover to eliminate the odour release from this source was examined and the results are given in figure 12.

Figure 12: Spalding STC 98%ile hourly means odour contour map (year 2018) – Sheeted sludge cake storage - Zoom radius 100m.

The 98th percentile of hourly mean odour concentrations calculated using 2018 meteorological data and storing only advanced digested sludge cake show that the 1.5 OUE/m3 contour isopleth extends 205m in a north westerly direction and encompasses an area of 33332m2 approximately.
This shows if all the sludge cake storage area was sheeted, it would decrease the distance and area encompassed by the 1.5 OUE/m3 contour by 62% and 89% compared with storing both advance treated and raw sludge cake that are open to atmosphere.
This suggests that if all sludge cake stored was sheeted, then although the 1.5 OUE/m3 contour slightly extends beyond the site boundary, no sensitive receptors would be affected.

6.0	Conclusions
This modelling study evaluates the risk of amenity loss to areas around Spalding STC.

An odour concentration of 1.5 OU/m3 has been taken as the benchmark level at which nuisance and potential loss of amenity would be anticipated. This assessment criterion for the protection of public nuisance/amenity is in line the Environment Agency (EA) H4 Planning Guidance, including septic effluent and sludge in amongst a range of substances categorised as most offensive and for which a low detection threshold should be taken into consideration.
Open storage of sludge cake will result in the 1.5 OU/m3 contour to extend beyond the site boundary and effects sensitive receptors around the WRC boundary.
However, if all sludge cake stored was sheeted, then although the 1.5 OUE/m3 contour slightly extends beyond the site boundary, and no sensitive receptors would be affected.
7.0	Recommendations
Possible mitigation measures could include;

- Sheeting should be used as soon as practical after raw sludge cake is tipped or after stockpile is opened for removal off site.
- Strict enforcement that trucks bringing raw cake to site are to be sheeted. Sheets should only be removed as soon as practical prior to tipping; trucks should be re-sheeted even when empty leaving sites. This should be re-enforced throughout the site team and RES operations managers.
- AW has identified a need to review and implement a more transparent and robust complaints monitoring and actions process. This is to increase the site’s visibility of complaints. AW are proactively starting a review of the current process so action and an improved system can be put in place.
- Limiting activities under certain weather conditions e.g., when wind direction is towards sensitive receptors.
- It would be beneficial to continue with frequent boundary monitoring.