## Sheet1
ENERGY EFFICIENCY CONTROLS IN PLACE AT BAKKAVOR SPALDING
Energy Efficiency Controls @ Bk, Spalding | Technique In Use (Yes / No) | Technique Details (Brief Explanation) | Area In Use (Input All site or Specific Area(s)) | Key | LIST
- burner regulation and control; | YES | 1. Improve efficiency of steam generation in boilers : Burner controls and condensate recovery upgrade carried out for Boiler 3 as this is the primary boiler for the site. Reverse osmosis on boiler water feed to Boiler 3 (less blowdown required). 2. MOTORS : Boiler economiser considered but burner upgrade deemed more appropriate and achieves the same goal. | Building A | Building A : Deli Buidling B : Soups & Sauces Building C : R&D, Finance Building D : Central Engineering Building E : MyHR Building F : SDC (Logistics) Building G : Cerebus ETP : Effluent Treatment Plant | YES
- cogeneration; | NO | Cogeneration techniques are not currently used on site. | N/A |  | NO
- energy-efficient motors; | YES | Motor management policy : Where new equipment is purchased, those with VSDs are preferred where this is available. This is set out in the electrical specification used by the site. | Sitewide
- heat recovery with heat exchangers and/or heat pumps (including mechanical vapour recompression); | YES | 1. Heat exchangers in place for Boiler systems. Heated water is returned to the boiler at 85oC in order to reduce Thermal Input Loads. 2. Reduce usage of steam/hot water : Improvements in condensate return to provide warm and treated water back to the boiler. All hot water in Soups is produced from steam heat exchangers (instead of gas fired boilers). | Boilers : Buildings A, B & G
- minimising blowdown from the boiler; | YES | Improve efficiency of steam generation in boilers : Burner controls and condensate recovery upgrade carried out for Boiler 3 as this is the primary boiler for the site. Reverse osmosis on boiler water feed to Boiler 3 (less blowdown required). | Boilers : Buildings A, B & G
- optimising steam distribution systems; | YES | 1. Insulation on Steam Valves & Flanges. 2. Steam trap survey and repair : The site owns a steam trap monitor, and carry out regular surveys. Repairs carried out as required. 3. Oven/cooking efficiency : Steam injection for some cooking processes which provides an efficient method for some foods. 4. Reduction usage of steam/hot water : Improvements in condensate return to provide warm and treated water back to the boiler. All hot water in Soups and Factory 1 is produced from steam heat exchangers (instead of gas fired boilers). 5. Improve efficiency of steam generation in boilers : Burner controls and condensate recovery upgrade carried out for Boiler 3 as this is the primary boiler for the site. Reverse osmosis on boiler water feed to Boiler 3 (less blowdown required). | Boilers : Buildings A, B & G
- preheating feed water (including the use of economisers); | YES | Heat exchangers in place for Boiler systems. Heated water is returned to the boiler at 85oC in order to reduce Thermal Input Loads | Boilers : Buildings A, B & G
- process control systems; | YES | 1. Temperature Measurement : Storage and processing vessels, transfer lines etc. 2. Pressure measurement : Indirect control of other parameters e.g. flow / level 3. Level measurement : Storage and reaction vessels 4. Flow measurement : Transfer lines, steam supply, CIP 5. Flow control : Constant flow valves, flow regulators a) Constant flow valves, flow regulators : Servo driven pumps on water lines so pressure can be adjusted to control flow rate. Compressed air systems have regulators to control flow. * Further description is available in Section 2.1 of 2019 BAT Draft Assessment. | Buildings A, B, F & G
- reducing compressed air system leaks; | YES | Compressed Air Reduction Initiative on site - report, detect & fix process. | All site
- reducing heat losses by insulation; | YES | Insualtion lagging present on Piping systems. Lagging is replaced as required. | All site
- variable speed drives; | YES | 1. Motor management policy : Where new equipment is purchased, those with VSDs are preferred where this is available. This is set out in the electrical specification used by the site. 2. Variable speed air compressors : VSDs (2 out of 3 at Cerberus, Deli, and Soups/Sauces & Salads). These are sequenced, with the 3rd running as back up if required. | Buildings A, B & G
- multiple-effect evaporation; | NO | No Evaporation processes are carried out n the site. | N/A
Electicity sub metering | YES | Sub-metering is in place across all the factories and data is captured via Carbon Desktop | Buildings A, B , C and G
Power factor correction improvements (cost saving only) | YES | This has been applied to all of the substations on site. | All site
Switch-off campaign | NO | Switch off campaigns have been rolled out at the site in past years. The use of Carbon Desktop had focussed attention on this issue; in addition, motion sensitive lighting is being rolled out. To be reviewed for re-roll out in 2022. | All site
Lighting upgrades to LED | YES | LED lighting has been installed in parts of the site and further roll out is ongoing. An energy saving spreadsheet has been produced, including yard and other external areas and some internal areas; specifying the likely payback period to replace existing lighting with LEDs. A separate lighting audit has been carried under the H&S management system and has identified the need for upgrades. Where upgrades are required, the lighting will be LED. Currently a large project in place to replace all the lighting system for Building G (Cerebus) (as of Q3 2021). | All site
Air Leak Detection and Repair | YES | An external party has been engaged to carry out a survey to identify any required repairs. | Building G
Refrigeration optimisation | YES | Cerberus, SDC, and Deli has been fully optimised, through the implementation of ammonia based refrigeration system. | Building A and G and SDC
Clean refrigeration evaporators | YES | Hygiene department clean these under the site PPM. An electrical system is used to do a regular defrost cycle on each ceiling mounted evaporators. | Buildings A, B, and G
Adiabatic cooling on refrigeration condensers | YES | The spiral condensers in soups have adiabatic cooling as do the condensers in the Deli. | Buildings A and B
Refrigeration heat recovery | YES | Heat recovery system on the new Blugenium system installed for heat recovery for the glycol return - the heat is used for production and welfare uses within Building A. | Building A
Improved insulation (chilled systems) | YES | Maintenance of chilled systems is managed by a third party; insulation requirements are led by legislation and met by the third party. Where pipework/other is replaced, insulation is also replaced. | Buidlings A, B, Cand G
Door policy (closing doors) | YES | This is high priority, particularly given the nature of the business. Air locks present on doors to external yards. For internal doors some are on sensors to automatically close these; others are manual however signage is considered paramount to ensure chilled areas are kept so. | All site
Increase server room temperature | YES | Server rooms are fitted with air conditioning; this is set at an appropriate temperature as per best practice. | All site
Timers on electric radiators | YES | Any new electrical radiators fitted at the site do include timers. | All site
Gas sub-metering, monitoring and targeting | YES | There are 7 gas sub-meters across the site. These are reported and trended using Carbon Desktop. | All site
Oven/cooking efficiency | YES | Steam injection for some cooking processes which provides an efficient method for some foods. | Buidlings A, B, Cand G