ODOUR MANAGEMENT PLAN (OMP)

1.	INTRODUCTION										2

1.1 	Site Description										2

1.2	Maintenance and review of the OMP								2

1.3	Relevant sector guidance on which this OMP is based						3

1.4	Version Control										3

2. 	RECEPTORS											4

2.1 	Receptor List and Map										4

2.2	Wind Rose and Source of Weather Data							5

3.	SOURCES OF ODOUR AND SITE PROCESSES							7

3.1	Odorous Materials Entering and Leaving Site							7

3.2	Odorous Materials										8

3.3 	Overview of odorous processes and emissions						10

4.	CONTROL MEASURES AND PROCESS MONITORING						13

4.1 	APPROPRIATE MEASURES AND BEST AVAILABLE TECHNIQUES (BAT)					13

5.	ODOUR REPORTING										17

5.1	COMPLAINTS REPORTING										17

5.2	COMMUNITY ENGAGEMENT									17

5.3	PRO-ACTIVE ODOUR MONITORING									17

5.4	REACTIVE ODOUR MONITORING									17

6.	ABNORMAL EVENTS										18

APPENDIX 1 OFF SITE ODOUR MONITORING RECORD							19

Davidstow Creamery, Camelford Cornwall, PL32 9XW

Environmental Permit number:  BN6137IK

# Who this Plan is for

This Odour Management Plan (OMP) has been prepared by Dairy Crest Limited (trading as Saputo Dairy UK) (hereafter referred to as “SDUK”) to support the Davidstow Creamery and Water Processing Facility (“WPF”) teams in:

- monitoring and contingencies to control and minimise odour pollution during normal and abnormal operation,

- preventing unacceptable off-site odour pollution as described by the Environmental Permit BN6137IK, and

- undertaking odour surveys and responding to external complaints.

This OMP will be communicated directly to those SDUK employees involved in managing odour emissions, undertaking off-site odour surveys and responding to complaints.

# 1.	Introduction

### 1.1 	Site Description

In summary, SDUK’s Davidstow facility comprises:

- a Creamery receiving milk, on a daily basis, which it pasteurises and processes into cheese.  Whey from the cheese making process is used to manufacture whey cream, demineralised whey powder and whey protein concentrate.  Lactose powder is processed to produce galacto-oligosaccharide (GOS), a prebiotic syrup, and

- A Water Processing Facility (WPF) which receives process waste water from the Creamery and employs physico-chemical, biological and membrane processes to treat water for subsequent discharge to the River Inny (in accordance with the Permit conditions) or reuse within the Creamery.

The Creamery and WPF operate for approximately 358 days per year, 24 hours per day (other than an annual maintenance shut down around October/ November).   Operation is relatively consistent during the year with some variation in site throughput associated with peak milk volume receipts referred to as the ‘spring flush’.

Davidstow Creamery is located in a predominantly rural location; the nearest villages to the site are Trewassa, Davidstow and Tremail with other smaller residential areas such as Treworra nearby. The land use surrounding the Creamery and WPF is predominantly rural and agricultural, with a low population density.  There is potential for seasonal and/or intermittent odour releases from local farming practices and a fallen stock facility located to the south of the Creamery.

### 1.2	Maintenance and Review of the OMP

The Davidstow Environment and Sustainability Manager is responsible for developing, maintaining and updating the OMP.    Reviews of the OMP are typically undertaken on an annual basis or following significant change on site that has the potential to affect odour emissions sources and/or control of emissions.

The OMP forms part of Davidstow’s Environmental Management System (EMS) and is filed under EMS/ Davidstow/ 8.1 Operational Control.

The Creamery and Water Processing Facility (WPF) Operations Managers (supported by the Environment and Sustainability Manager) are responsible for training relevant people in their teams.

All personnel undertaking off-site odour surveys will be trained in completion of the odour survey reporting form shown in Appendix 1.

### 1.3	Relevant Sector Guidance on which this OMP is based

- Environment Agency’s Technical Guidance Note H4 ‘Odour Management’

- EA’s Environment Agency Odour Management Plan Template Final V2 05/05/21

### 1.4	Version Control

| Rev | Purpose for Revision | Authorised By | Submitted to EA | Owner |
| --- | --- | --- | --- | --- |
| 5 | Clarification of EA questions. Changes from previous version in blue font | C Appleton | Jan 2024 | M Bardell |
| 4 | Routine update and adoption of EA template for OMPs Updated with EA comments during determination of application for Permit Variation | C Appleton | Dec 2023 | G Jones |
| 3 | Routine update | S Cook | 2021 | S Magor |
| 2 | New format with olfactometry results | M Youds | 2018 | M Bardell |
| 1 | First issue | M Bardell | 2016 | AMP |

# 2. 	Receptors

### 2.1 	Receptor List and Map

As described in Section 3, the principal sources of odour are within the WPF. The location of each receptor is described relative to the WPF.

| Ref. | Receptor Type | Direction from WPF | Approx Distance to Site Boundary (m) | Sensitivity to odour - Low (e.g. footpath/road) - Medium (e.g. industrial/ workplace) - High (e.g. housing / pub / hotel etc.) |
| --- | --- | --- | --- | --- |
| 1 | Residential properties on Blacka Lane local to Creamery (north) | W | 1,000 | High |
| 2 | Trewassa –residential properties & maintenance workshop | NW | 300 | High |
| 3 | Treworra – residential properties | E | 500 | High |
| 4 | Tremail - residential properties | E | 2,000 | High |
| 5 | Airfield | S | 1,500 | High |
| 6 | Inny Vale – residential & holiday properties | ENE | 1,500 | High |
| 7 | Air Museum | W | 1,500 | Medium |
| 8 | St Kitts Farm – residential and commercial | W | 2,000 | High |
| 9 | Fallen Stock Yard – commercial | ESE | 1,500 | Low |
| 10 | Davidstow Church & The Pines (residential) | N | 1,000 | High |
| 11 | Residential properties – Pendragon House, Trehane House and Bungalow | NW | 2,000 | High |
| 12 | Barnpark Farm | WSW | 500 | Medium |
| 13 | Residential properties on Blacka Lane local to Creamery (south) | WSW | 1,500 | High |

### 2.2	Wind Rose and Source of Weather Data

Meteorological data has been obtained from Cardinham weather station near Bodmin to the south of Davidstow and the receptors identified in section 2.  A wind rose is shown below for 2019 which is representative of all years of data assessed.

A meteorological station recording wind speed and direction as part of the Envirosuite monitoring system is located at the WPF and is used to assess off site impacts and during complaint investigation.

The prevailing winds within the region are from the west-southwest, west and northwest, with a secondary component from the southeast and relatively minor frequency of winds from the south and southwest.

The majority of odour complaints relating to SDUK’s operations have been received from residents in Trewassa to the northwest of the WPF and Treworra to the east-northeast, hence the wind frequencies from the southeast and west-southwest are typically responsible for transporting any odours from the WPF to the sensitive properties.

Location of receptors shown in the table above

# 3.	Sources of Odour and Site Processes

### 3.1	Odorous Materials Entering and Leaving Site

The raw materials delivered to and received at the Creamery and WPF (including untreated fresh waste water) are of inherently low odour potential.

Sources of odour arise when ingredients, by-products, process waste water or waste generated during the operation of the Creamery or WPF degrade.   Degradation typically results from (i) storage and handling of materials under oxygen deficient conditions (ii) when materials are allowed to acidify which increases the potential for formation of hydrogen sulphide (H2S) and/ or (iii) excessive retention time of such materials in tanks.

Although of low odour, some inputs to waste water processing can exacerbate the potential for odour formation e.g. the use of sulphuric acid which adds to the sulphur content of process waste water containing dairy effluent (which contains a small amount of sulphur).

Chemical analysis of odourous emissions undertaken by specialists annually from 2018 to 2021 has shown that H2S is the principal odourous compound present at the WPF and to a much lesser extent other reduced sulphur species such as Dimethyl Sulphide (DMS) and Dimethyl-disulphide (DMDS).  Traces of other organic compounds such as aldehydes and ketones are typically present at lower concentrations compared to their odour detection thresholds and they are generally considered to have less offensive odour characteristics.

H2S occurs when the dissolved sulphur present in waste water is reduced under oxygen depleted conditions to other sulphur compounds.

In addition to keeping waste water aerated, pH plays an important role in keeping any H2S present in solution as emissions of H2S vapours increases sharply under neutral or acidic conditions of pH <8.

Section 3.2 identifies the different types of potentially odourous materials on site.

Extensive olfactomeric assessments of odour emissions at the WPF were conducted in 2017 to define and quantify an inventory of the main sources of odour.  This was further updated by assessments carried out in 2020, 2021, 2022 and 2023 by a specialist consultant.

These olfactometry assessments entail sampling of odourous air from typically 18 point (e.g. OCU) and area sources (e.g. open tank surfaces, DAFs, sludge pit) at the WPF as well as the Creamery (calcium Phosphate Plant and Lagoon).  Odourous air samples are presented to an independent odour panel comprising specialists who follow a defined process to quantify the magnitude of the concentration of the odour in each sample.   This data is combined with the size of the odour source (e.g. surface area of a tank) in order to quantity an odour emission rate measured in odour units per second, OuE/sec.

The outcome of the olfactometry assessments have been used in assigning low, medium or high risk as detailed below.

Section 3.3 identifies the processes associated with the use of potentially odourous materials, their locations and potential to contribute to offsite odour emissions.

### 3.2	Odorous Materials

| Odorous and Potentially Odorous Material | Odour Potential High / Medium / Low Risk | Maximum quantity on site at any given day | Maximum time held on site (hours or days) | Location of odorous materials on site | Additional Comments |
| --- | --- | --- | --- | --- | --- |
| Out of specification or surplus whey | Medium | 300 tonnes in a covered, extracted and abated storage lagoon at the Creamery | 7 days | Creamery | Rated medium risk if excessive residence time and hot weather |
| Untreated process waste water from Calcium Phosphate (CaP) plant | Low | 450 tonnes in CaP Balance Tank | 3 days | Creamery | Low as typical residence time is <1 day |
| CaP Cake | Low | 20 tonnes | Inventory of cake press/ belt and cake trailers awaiting export | Creamery | Low as trailers are routinely exchanged & accumulations routinely (daily) removed from belt press & conveyor |
| Untreated process waste water - Balance Tank 1 (BT1) & Divert Tank) | High | 2,500 tonnes | Typically 1-2 days (residence time in BT1 and Divert Tank) Removal of ‘fresh’ and mostly dilute waste water from BT1 is periodically undertaken to maintain liquid level in BT1. This employs a road tanker mainly filled from the liquid head in the tank. This effluent is typically dilute and has not had time to degrade by a and therefore has a lower potential to cause offsite odour emissions. | WPF - BT1 and Divert Tank | Rated as high risk if stored under adverse conditions of pH <8 or low dissolved oxygen (DO <0.5 mg/l as measured by daily manual readings) |
| Part treated process waste water – Balance Tank 2 (BT2), Anoxic Tank 2 (AN2) and Anoxic Tank 3 (AN3) | Medium | 3,000 tonnes | Typically 1-2 days (residence time in BT2, AN2 and AN3) | WPF – BT2 and AN2 and AN3 | Rated as high risk if stored under adverse conditions of low pH or low DO of <0.5 mg/l as measured by daily manual readings |
| Part treated process waste water Aeration Tank 3 (AT3) | Medium | 3,000 tonnes | Typically 1-2 days (residence time in AT3) | WPF – AT3 | Low under normal operating conditions. High if contents stored under adverse conditions of low DO of typically <3 mg/l as measured by on-line continuous telemetry of the circulating activated sludge mass |
| WPF Sludge | High | Inventory of sludge pits and 2x 8 tonne sludge trailers located within the closed Centrifuge building (other than during trailer exchange) | Sludge trailers removed daily | WPF | Sludge is inherently odourous |
| Waste cheese curds | Low | 1 tonne | 1-2 weeks between collections | WPF | Rated as low risk due to low inventory unless retained on site for excessive time during hot weather |

### 3.3 	Overview of Odorous Processes and Emissions

| Ref | Building | Type of Process | Type of Emission Point | Odour Potential | Additional Comments |
| --- | --- | --- | --- | --- | --- |
| WPF | Inlet well | Untreated process waste water/ open well | Area | Low | Inlet well is of small surface area and receives fresh waste water so rated low |
|  | DAF units 1-3 | Partially treated waste water/ open units within buildings (DAF1&2) and externally (DAF3) | Area | Medium |  |
|  | Balance Tank 2 | Partially treated waste water / open tank | Area | High |  |
|  | Anoxic Tanks 1-3 | Partially treated waste water / open tanks | Area | Medium |  |
|  | Aeration Tanks 1A, 1B, 2 & 3 | Aerated waste water / open tanks | Area | Low (AT1A,B and 2) Medium (AT3) |  |
|  | RAS / WAS Chambers | Sludge / open wells | Area | Low |  |
|  | Bottom sludge pit | Sludge / open chamber | Area | Low |  |
|  | Top sludge pit | Sludge / open pit | Area | Low |  |
|  | Sludge conveyor | Dewatered sludge / agitation | Area | Medium |  |
|  | Sludge trailer | Dewatered sludge / open trailer | Area | Medium |  |
|  | Odour Control Unit | Treated emissions / vertical stack | Point | High | OCU serves BT1 and Divert Tank |
|  | Cheese curd waste bins | Waste storage | Point | Low |  |
| Creamery | Open top buffer tank | Partially treated waste water / open tanks | Area | Medium |  |
|  | Flocculation tank | Partially treated waste water / open tanks | Area | Low |  |
|  | Sludge conveyor | Dewatered sludge / agitation | Area | Low |  |
|  | Sludge cake trailer | Dewatered sludge / open trailer | Area | Low | CaP sludge cake has a very low odour |
|  | Odour Control Unit | Treated emissions / vertical stack | Point | Low | OCU serves covered storage lagoon |

Site Plan Showing Location of Odourous Process Locations – WPF

Site Plan Showing Location of Odourous Process Locations – Creamery

# 4.	Control Measures and Process Monitoring

### 4.1 	Appropriate Measures and Best Available Techniques (BAT)

| Odorous and potentially odorous process/material | Control Measures (Appropriate Measure / BAT) | Monitoring frequency | Monitoring procedure and optimum process parameters | Trigger level | Action taken if outside optimum process parameters |
| --- | --- | --- | --- | --- | --- |
| Out of specification or surplus whey | - Use of covered contingency storage lagoon to hold high strength waste ingredients and by-products awaiting either subsequent processing at the WPF or export from site by road tanker - Single stage OCU serving covered lagoon Note 1 | Continuous Annual | Manual inventory checks and retention time minimised Quarterly ‘health check’ of condition of OCU serving the lagoon Note 5 | 300 tonnes Retention > 1week >1 ppm H2S | Export via road tanker Replace OCU media if depleted with H2S emissions >1 mg/Nm3 |
| Untreated process waste water – CaP Plant | - Residence time of Demin effluent in CaP Balance Tank minimised at <1 day during normal operation | Continuous | Monitoring of tank level and residence time | >3 days in summer | Export via road tanker |
| CaP Cake | - Maintaining process condition of CaP Plant for effective precipitation and flocculation - Automated dosing of sulphuric acid to minimise residual sulphur level in waste water received by the WPF - Housekeeping of CaP Plant to remove residual cake - Routine exchange of cake trailer | Continuous Continuous Daily Daily | pH dosing and polymer feed rate (visual check of floc) pH of flocculation tank Standard Operating Procedure Trailer level automatically detected and auto trailer changeover | Poor floc pH >4 Residual solids Trailers full | Tankering Tankering Manual clean Exchange trailer |
| Untreated process waste water - WPF | - Short interval control of Creamery operations - Use of Unplanned Event Reporting (UER) form to manage and communicate unplanned discharges of ingredients, by-products and products to drain | Daily Continuous | Unplanned losses to drain minimised or communicated to WPF using UER form | Unplanned Event | Higher strength effluent routed to lagoon, Divert Tank and/ or tankering |
|  | - Monitoring of Dissolved Oxygen (DO) Levels in reception tanks provided by aeration air supplied to BT1 via 4x external mounted Landia blower/ mixers spaced approximately equally around the circumference of the tank. - Desludging of BT1 and Divert tanks | Continuous Annual | >0.5 mg/l DO Sludge accumulation | <0.5 mg/l DO Poor DO | Increase aeration rate Remove sludge |
|  | - Automatic diversion of high strength effluent from BT1 to the Divert Tank using pH, COD and/or turbidity (being commissioned in summer 2023) - Automated dosing of caustic to BT1 to maintain pH >8 (being commissioned in 2023) | Continuous Continuous | Daily COD load <12 tonnes Daily lab analysis of COD of influents Visual checks of WPF inlet well pH >8 Note 4 | COD load >13 tonnes/ day pH <8 | Higher strength effluent routed to Divert Tank and/ or tankering. Manual diversion if automated system fails Manual addition of caustic |
|  | - Covered and extracted WPF reception tanks BT1 and Divert Tank | Periodic integrity test e.g. smoke Annual | Maintain slight negative pressure Preventative maintenance of extraction fan | Visual detection of fugitive emissions from the cover of BT1 during smoke testing | Remedial works to tank cover/ duct work to minimise fugitive emissions and maintain negative pressure in both tanks. |
|  | - Monitoring of H2S levels in BT1 and Divert tank headspace - Multi-stage Odour Control Unit (OCU), extract fan and exhaust stack (wet/ dry (Diox) / dry (Triox))Note2. - Monitoring of H2S levels in OCU exhaust | Continuous Quarterly Continuous | <10 ppm H2S measured by on-line instrument and verified via manual measurement Quarterly ‘health check’ of condition of OCU serving BT1 and Divert Note 5 < 1 ppm H2S measured by on-line instrument and verified via manual measurement | >10 ppm H2S >1 ppm H2S in exhaust | Increase pH to >8 via manual additional of caustic Reduce COD load by rebalancing flow/ load across the various treatment stages of the WPF Dosing of Diox Max direct to BT1 and/ or additional dosing of Diox Max to wet scrubber stage Replace dry OCU media on initial detection of deterioration if detected during quarterly OCU ‘health check’ |
| Part treated process waste water – BT2 and AN2,AN3 | - Short interval control of WPF operations - Covered and extracted WPF buffer tank BT2 and AN2 and AN3 (due for completion in spring 2024) - OCU serving BT2, AN2 and AN3 (due for completion in spring 2024) Note 3 | Daily Continuous Continuous | Daily review of key WPF metrics (process parameters and lab results) Maintain slight negative pressure < 1 ppm H2S in exhaust Quarterly ‘health check’ of condition of OCU serving BT2 and Anoxics Note 5 | >1 ppm H2S | Increase aeration Replace dry OCU media on initial detection of deterioration if detected during quarterly OCU ‘health check’ |
| Part treated process waste water – AT3 | - Maintain Mixed Liquor Suspended Solids (MLSS) through COD feed rate and sludge wasting - Aeration of AT3 via jet mix system and DO - Maintain low Ammoniacal Nitrogen (Amm-N) Levels | Daily Continuous Daily | Daily lab analysis of MLSS >2-3 mg/l DO <1.0 mg/l Amm-N | MLSS >15,000 mg/l <2 mg/l DO >3 mg Amm-N | Reduce feed, increase sludge wasting Increase aeration Add nitrifying bacteria |
| WPF Sludge | - Sludge centrifuges located inside closed container - Sludge conveyor and trailers located inside closed building with roller door only opened for exchange of trailer - Frequent exchange of trailers - Sludge building housekeeping to prevent sludge accumulation - Sludge pit inventory minimised and periodically de-sludged to remove any stagnant material at the base of the tank | Continuous Continuous Daily Daily Annual | Doors closed except during trailer exchange taking typically 5-10 minutes No overfilling of trailers Minimise solids outside of trailers Twice yearly removal of any solids accumulation | Doors open other than for trailer exchange | Close doors Exchange trailer Manual clean Twice yearly de-sludging |
| Cheese Curd Waste | - Frequent emptying of covered bins | Scheduled collections | Visual checks on inventory of bins to prevent overfill | Bins full or scheduled collection time exceeded | Empty bins |
| Notes on Odour Control Units (OCUs) or ‘Scrubbers’ Note 1 – Lagoon OCU Comprises a single stage dry chemical bed installed with proprietary chemical media called Triox and Diox (which remove reduced sulphur species including H2S as well as other odourous compounds) and is served by an induced draught fan. The fan continuously extracts air from the headspace of the lagoon via multiple connection points on the covered lagoon which is routed to the scrubber via a common header. Treated air exiting the fan is discharged to atmosphere via a stack adjacent to the scrubber. Note 2 – Divert/ BT1 Scrubber OCU Comprises 3 stages: - Stage 1 Wet Scrubber: A wet scrubber removes gaseous pollutants from the gas stream via mass transfer to a liquid solvent. The scrubber chamber is packed with pall rings and it incorporates a scrubber liquor distribution system. An automated dosing system adds odour suppressant (Diox-Max) to the recirculating scrubber liquor. If required the wet scrubber is replenished with potable water to supplement condensation in the air extracted from BT1/ Divert tank with the liquid level being monitored via a sight glass. The proprietary odour abatement chemical Di-Ox 5000 is added either manually or via a variable speed pumped dosing system from an IBC stored on a portable bund adjacent to the scrubber. - Stage 2 Dry Scrubber #1: A dry scrubber removes pollutants from the waste gas stream by retention on a solid surface. The dry scrubber comprises a chamber filled with 8 m3 of AWT’s proprietary ‘Tri-Ox’ adsorbent which selectively removes hydrogen sulphide. - Stage 3 Dry scrubber #2: The chamber contains three layers of different adsorbent materials; 5.5 m3 ‘Di-Ox’ (bottom layer) targeting hydrogen sulphide, mercaptans and organic amines, 1.0 m3 ‘ADS-C’ (middle layer) for neutralisation of acid gases such as hydrogen sulphide, mercaptans and organic sulphides, including reduced sulphur compounds e.g. DMS / DMDS and 1.5 m3 ‘Ecosorb’ (top layer) which is a high activity, extruded activated carbon. An extract fan pulls air through the wet scrubber and head space of the wet and two dry scrubbers. The treated air is released to atmosphere via a vent stack which discharges at a height of approximately 1 m above the height of BT1 at an efflux velocity of 15 m/s. Valves in the extraction ductwork enable the extracted air flow to be balanced between BT1 and Divert in order to maintain a slight negative pressure in each tank. The combined 3 stage (wet/dry/dry) OCU serving BT1 has a minimum residence time of approx. 22 seconds at maximum extraction fan flow rate. The absence of fugitive emissions from tank cover and ductwork can be confirmed by smoke test during routine surveys Note 3 – BT2/ AN2/ AN3 OCU (due for completion in spring 2024) Comprises 2x two stage dry/ dry chemical beds operating in parallel each installed with proprietary chemical media called Tri-Ox (1st stage) and a multi-component Di-Ox/ ADS-C and Ecosorb (2nd stage) which remove reduced sulphur species including H2S as well as other odourous compounds. The dry chemical beds are served by an induced draught fan discharging via a 4.25m exhaust stack with an efflux velocity of 15 m/s. This has been sized to provide adequate dispersion (being remote from nearby structures that could be detrimental to dispersion) whilst minimising the potential for treated air exiting the stack to add to off-site noise levels. Valves in the extraction ductwork enable the extracted air flow to be balanced between BT2 and Anoxic pits in order to maintain a slight negative pressure in each tank/ pit. The two parallel 2x 2 stage have a minimum residence time of 24 seconds which has specified by the equipment provider to ensure sufficient contact time with the dry chemical media for abatement of odourous compounds. BT2 is of sectional cast concrete and hence less vulnerable to under/ over pressure than a hermetically sealed steel structure. The BT2 cover is not hermetically sealed and relies on a small degree of air ingress from around the large circumference in to the headspace of the tank which operates at negative pressure. The absence of fugitive emissions can be confirmed by smoke test during commissioning (consistent with performance guarantees) and routine surveys. Note 4 – Potential adverse effects of higher pH When the pH of wastewater exceeds 8 and alkaline conditions are introduced, there is an increased potential for the release of ammonia gas (NH3). Ammonia exists in two forms in water: unionized (NH3) and ionized (NH4+), and the ratio between these forms is highly pH dependent. At higher pH levels, a greater proportion of ammonia exists in its volatile, uncharged form (NH3), which can be released into the air, contributing to odours. However both periodic chemical speciation analysis and routine scrubber health checks have not shown nitrogen containing compounds to be routinely present in extracted air. Consequently, H2S is considered the most significant contributor to potential odours. Note 5 – Scrubber ‘Health Checks’ The effectiveness of the scrubbers is monitored by the technology provider (AWT) on a quarterly basis by measuring H2S concentrations (as well as VOCs, mercaptans and amines) in the scrubber inlet and outlet (and between stages where relevant) and periodically during olfactometry assessment. The H2S concentration in the treated air is also checked daily by the WPF Operations team. The dry chemical media is replaced if showing signs of deterioration. |  |  |  |  |  |

# 5.	Odour Reporting

### 5.1	Complaints Reporting

Complaint reports are received either:

- via email and/ or call from the Environment Agency’s National Incident Recording System (NIRS) team if the complaint has been raised with the EA, and/ or

- via phone call or email to Davidstow Site Security, Creamery or WPF Operations managers.

All complaints are recorded in a Complaint Log by the Environment and Sustainability Manager. Details of the nature of the external complaint are recorded as well as time/ date, location, level and description of the character reported by the complainant.

The Complaint Log forms part of Davidstow’s Environmental Management System (EMS) and is retained under EMS/ Sites/ Davidstow/ 9.1 Performance Evaluation/ 8. Complaint Log.

### 5.2	Community Engagement

Community Liaison meetings are held with representatives of the local community (members of Davidstow Parish Council) and the Environment Agency on a typically monthly basis or as agreed with the local community.    Meetings are documented and actions/notes shared with participants.

SDUK attendees typically comprise the Davidstow Site Director, WPF Operations Manager, Environmental Management and Project Management.

Community representatives (and other members of the community) are invited to provide feedback on odour emissions directly to SDUK via email/security gate house between meetings in addition to any reports sent to the EA.

Where possible, SDUK will proactively advise Community representatives of abnormal operational conditions that have the potential to increase odour emissions so that they can advise the wider community.

### 5.3	Pro-active Odour Monitoring

SDUK undertakes the following periodic pro-active monitoring of odour emissions:

- On-site - Periodic (typically annual) olfactomeric assessment of emissions from principal sources at the WPF and Creamery.   Olfactometric assessment is periodically supplemented with chemical speciation of principal sources.  Monitoring is undertaken by a specialist odour consultancy e.g. Olfasense

- Off-site - Community surveys by Creamery personnel (typically operations managers or their deputies and members of the Davidstow environment team).  Results of off-site monitoring are recorded using form F.EV.05 shown in Appendix 1.   Surveys can include the use of portable equipment to measure H2S concentrations at low levels (ppb).  Survey results are recorded as part of the Complaint Log referred to in section 5.1 above.

- Use of remote, fixed monitoring equipment at locations previously known to be affected by periodic increases in odour emissions i.e. Trewassa and Treworra.  Current or recent historic measured ground level concentrations of H2S (as well as ammonia) can be accessed remotely using a web-based system referred to as Envirosuite.

### 5.4	Reactive Odour Monitoring

Reactive odour monitoring follows the same process as described for pro-active monitoring above.

When complaints are received from the NIRS team in a timely fashion and/ or directly from the local community to enable a meaningful investigation, a community survey is undertaken and recorded using form F.EV.05 shown in Appendix 1.

# 6.	Abnormal Events

Operating experience and risk assessments have shown the following abnormal events to have the potential to materially affect odour emissions from the WPF.

| Abnormal Event | Recovery Steps |
| --- | --- |
| Unplanned discharge of ingredient, by-product or finished product to drain typically as a result of Creamery equipment breakdown or unplanned event | Material is routed either to the covered, extracted and abated contingency lagoon located at the Creamery or the Divert Tank at the WPF. In addition, material can be exported directly from storage tanks at the Creamery e.g. storage tank T417 |
| Increased waste water load at WPF | Export of surplus via road tanker Increase pH in BT1 through manual addition of caustic to supplement caustic dosed via the automated pH control system (being commissioned in summer 2023) Manual dosing of a proprietary odour suppressant (typically ‘Diox Max’ an aqueous solution of stabilised chlorine dioxide) added to BT1 in controlled doses of typically 1,000 litres over a 12 hour shift, depending on plant conditions |
| Failure of WPF aeration equipment | Replace with spares which are retained on site Obtain rental blower(s) from retained contractor |
| Failure of WPF equipment e.g. DAFs reducing forward flow through WPF increasing inventory/ residence time in BT1 and Divert Tank | Amend production schedule of Creamery if possible to reduce waste water volume e.g. cleaning schedule Export via road tanker |
| Increased ammonia in aeration circuits | Reduce feed, increase DO, add nitrifying bacteria, control Mixed Liquor Suspended Solids (MLSS) via sludge wasting rate |
| Power cut | Manual diversion to contingency storage lagoon at Creamery and/ or Divert Tank Export via road tanker |

# Appendix 1 Off Site Odour Monitoring Record

| Completed By |  |  |  |  |
| --- | --- | --- | --- | --- |
| Date: | Time | 09:00 15:00 OTHER: |  |  |
| Wind direction |  | Weather/Other |  |  |
| Location | Odour (any H2S?) | Character of odour | Intensity level | Noise |
| 1 Site |  |  |  |  |
| 2 Trewassa |  |  |  |  |
| 3 Treworra |  |  |  |  |
| 4 Tremail |  |  |  |  |
| 5 Airfield |  |  |  |  |
| Other notes, people met, comments |  |  |  |  |
| Observations at other locations on drive |  |  |  |  |

Location map is at the end of the document.

| 1 Site | Any main site observations |
| --- | --- |
| 2 Trewassa | At field gate beside workshop |
| 3 Treworra | You can go up the lane saying “Treworra Barton/Belle tents”. Can park in the turning spot beside farm gate/Belle tents. Can also walk along the lane to next farm gate, closer to plant. |
| 4 Tremail | Field gate – higher part of hamlet |
| 5 Airfield | Any observations as the route is taken |

INTENSITY – for good or bad odours

|  | What is that like? |
| --- | --- |
| 0 No odour | Clear fresh air or rain/wind |
| 1 Very faint odour | Smell something taking deep breath or not constant (even cut grass or faint sewage types) |
| 2 Faint odour | Imagine bbq smoke 2 or 3 gardens away, you’re aware but it is not bothering you. |
| 3 Detect odour | Arrive and notice it when you get out of the car, and it is constant. |
| 4 Strong odour | It is an obvious smell, persistant – like fresh paint in a closed up house. |
| 5 Intense odour | You’ll notice it in the car and constant, perhaps quite unpleasant as you stand at the location. Doesn’t lessen while there. |
| 6 Extremely strong odour | Strong enough it may make you wretch, cover your mouth and probably move away quickly |

CHARACTERISTICS – description examples

| Character of Odour | What is that like? |
| --- | --- |
| Healthy sewage treatment plant | Like fresh garden compost, a bit earthy, soil after rain |
| Unpleasant | Should be evident – anything you wouldn’t want to be around yourself. Sat having a cuppa – would you want to keep smelling it? |
| Sulphur like/eggy | Indicates high hydrogen sulphide almost certainly from our plant. IMPORTANT – please report back to the WPF team. |
| Sewage | Blocked drains, septic tank |
| Anoxic | Bottom of a pond black sticky anoxic sludge, smells unpleasant but not like eggy smell |
| Fishy | Rotting fish, blood fish & bone manure |
| Gone off milk/cheesy | Should make sense |
| Sweet | Calcium phosphate is sometimes like this |
| Acrid | Acidic, drain unblocker |
| Smokey | Woodsmoke, bbq, field burn off |
| Metallic | Burnt brake pads, angle grinding |
| Silage | Sweet, grass smell |
| Manure, agricultural | Stronger muck smell either from animal yard or spreading (not expecting you to say which unless you see the operation) |
| Others | Anything else you smell good or bad: Paint, vomit, blossom, wild garlic, garbage (bottom of a dirty wheelie bin) |

Tremail

Odour intensity (1-6):

H₂S Levels:

Character of odour:

Noise:

Comments:

Questions and Answers

Q – Why are we doing this?

A – To better understand day to day what odours our operations are making.  To experience what our neighbours do. So we can pick up things swiftly to improve/fix.

Q – Am I looking for just “bad” odours from just us or anywhere?

A – Any odours good or bad in these locations will help us build a picture of impacts and see if they are related to wind directions and operations.

Q – Should I speak with the local community?

A – It would of course be courteous to introduce yourself or say hello if they are there during these trips.  Any feedback is helpful.  Often impacted neighbours near industrial operations wish to be heard.  It’s all helpful.

Q – Do I have to explain the WPF operations, especially if it is smelly?

A – No you don’t.  But if it is bad, please say you will pass the information on to the WPF Operations Manager for investigation.

If it is strong and from the WPF sewage, acidic, eggy – please report directly to the WPF team

Chemical Speciation.

Periodic assessments undertaken by specialist odour consultants has at times also entailed ‘chemical speciation’ to determine the components of odourous air.  Samples of odourous air are transferred onto Tenax-based adsorption tubes and subsequently analysed by Gas Chromatography Mass Spectroscopy (GC-MS) to determine which specific odorous chemical compounds are present at each location. The analysis suite includes aromatic and aliphatic VOCs, nitrogen, sulphur and chlorine containing species. Measured concentrations of individual compounds are then compared to published Odour Threshold Values (OTVs) for each compound.

Potential adverse effects of higher pH

When the pH of wastewater exceeds 8 and alkaline conditions are introduced, there is an increased potential for the release of ammonia gas (NH3). Ammonia exists in two forms in water: unionized (NH3) and ionized (NH4+), and the ratio between these forms is highly pH dependent. At higher pH levels, a greater proportion of ammonia exists in its volatile, uncharged form (NH3), which can be released into the air, contributing to odours.  However both periodic chemical speciation analysis and routine scrubber health checks have not shown nitrogen containing compounds to be routinely present in extracted air.  Consequently, H2S is considered the most significant contributor to potential odours.