## Containment
| EPR/BN6137IK | Dairy Crest Limited | Davidstow Creamery |  | 0
Containment
| Guidance on containment is available on our website: |  |  | gov.uk: leaks from containers | Also refer to the CIRIA C736 guidance doc "Containment systems for the prevention of pollution"
Row No. | Tank name or reference | Contents | Tank capacity (litres) | Location | Tank Material of Construction | Bund Reference | Is tank bunded? | Is bund shared with other tanks? If so, which? | Capacity of bund (litres) | LxWxH to delete | Bund capacity as % of tank capacity | Material of construction of bund | Does bund have a drain point? | Do any pipes penetrate bund wall? | Please give details of any tank overfill protection measures in place | Where does surfaced area outside bund drain to? | Where is the tanker fill point and how are drips captured? | What leak detection is provided (if any)? | When was the last bund integrity test carried out? | What maintenance measures (inc inspection) are in place for the tank and bund? | Outline how the bund is emptied | Provide any other information relating to the tank and bund here, eg details of any tertiary containment: | DOC REF for supporting info
CREAMERY
1 | Citric acid IBC | Citric acid | 1000 | Area behind energy centre close to HCl scrubber | Plastic | Acid bund 1 | Yes | Yes with sulphuric acid IBC 1 | 1100 | 3.32m x 0.43m x 1.25m | 110% | Plastic | No | No | None. Full IBCs delivered to site. | Drainage via the surface water drainage system | Full IBCs are delivered to site. Empty IBC replaced in situ. | Visual inspection | Unknown | Environmental Walk Days/ Night Shifts. Maintenance schedule of the tanks and bund unknown. | Pumped out | The number of IBCs stored here may vary
2 | Organic peroxide IBC | Organic peroxide | 1000 | Area behind energy centre close to HCl scrubber | Plastic | Acid bund 3 | Yes | Yes with sulphuric acid IBC 3 | 1100 | 3.32m x 0.43m x 1.25m | 110% | Plastic | No | No | None. Full IBCs delivered to site. | Drainage via the surface water drainage system | Full IBCs are delivered to site. Empty IBC replaced in situ. | Visual inspection | Unknown | Environmental Walk Days/ Night Shifts. Maintenance schedule of the tanks and bund unknown. | Pumped out | The number of IBCs stored here may vary
3 | Sulphuric acid IBC 1 | Sulphuric acid 50% | 1000 | Area behind energy centre close to HCl scrubber | Plastic | Acid bund 1 | Yes | Yes with citric acid IBC | 1100 | 3.32m x 0.43m x 1.25m | 110% | Plastic | No | No | None. Full IBCs delivered to site. | Drainage via the surface water drainage system | Full IBCs are delivered to site. Empty IBC replaced in situ. | Visual inspection | Unknown | Environmental Walk Days/ Night Shifts. Maintenance schedule of the tanks and bund unknown. | Pumped out | The number of IBCs stored here may vary
4 | Sulphuric acid IBC 2 | Sulphuric acid 50% | 1000 | Area behind energy centre close to HCl scrubber | Plastic | Acid bund 2 | Yes | No | 1100 | 3.32m x 0.43m x 1.25m | 110% | Plastic | No | No | None. Full IBCs delivered to site. | Drainage via the surface water drainage system | Full IBCs are delivered to site. Empty IBC replaced in situ. | Visual inspection | Unknown | Environmental Walk Days/ Night Shifts. Maintenance schedule of the tanks and bund unknown. | Pumped out | The number of IBCs stored here may vary
5 | Sulphuric acid IBC 3 | Sulphuric acid 50% | 1000 | Area behind energy centre close to HCl scrubber | Plastic | Acid bund 3 | Yes | Yes with organic peroxide IBC | 1100 | 3.32m x 0.43m x 1.25m | 110% | Plastic | No | No | None. Full IBCs delivered to site. | Drainage via the surface water drainage system | Full IBCs are delivered to site. Empty IBC replaced in situ. | Visual inspection | Unknown | Environmental Walk Days/ Night Shifts. Maintenance schedule of the tanks and bund unknown. | Pumped out | The number of IBCs stored here may vary
6 | Sulphuric acid IBC 4 | Sulphuric acid 50% | 1000 | Area behind energy centre close to HCl scrubber | Plastic | Acid bund 4 | Yes | Yes with sulphuric acid IBC 5 | 1100 | 3.32m x 0.43m x 1.25m | 110% | Plastic | No | No | None. Full IBCs delivered to site. | Drainage via the surface water drainage system | Full IBCs are delivered to site. Empty IBC replaced in situ. | Visual inspection | Unknown | Environmental Walk Days/ Night Shifts. Maintenance schedule of the tanks and bund unknown. | Pumped out | The number of IBCs stored here may vary
7 | Sulphuric acid IBC 5 | Sulphuric acid 50% | 1000 | Area behind energy centre close to HCl scrubber | Plastic | Acid bund 4 | Yes | Yes with sulphuric acid IBC 4 | 1100 | 3.32m x 0.43m x 1.25m | 110% | Plastic | No | No | None. Full IBCs delivered to site. | Drainage via the surface water drainage system | Full IBCs are delivered to site. Empty IBC replaced in situ. | Visual inspection | Unknown | Environmental Walk Days/ Night Shifts. Maintenance schedule of the tanks and bund unknown. | Pumped out | The number of IBCs stored here may vary
8 | Ultrasil 125 IBC | Utrasil 125 | 1000 | Back of pasteurising room | Plastic | Ultrasil 125 bund | Yes | No | 1100 | 1.6m x 1.3m x 0.7m | 110% | Plastic | No | No | None. Full IBCs delivered to site. | Drainage via the surface water drainage system | Full IBCs are delivered to site. Empty IBC replaced in situ. | Visual inspection | Unknown | Environmental Walk Days/ Night Shifts. Maintenance schedule of the tanks and bund unknown. | Pumped out | Bund covered by IBC storage. Rainwater unable to get into the bund.
9 | Ultrasil 67 IBC | Ultrasil 67 | 1000 | Back of pasteurising room | Plastic | Ultrasil 67 bund | Yes | No | 1100 | 1.6m x 1.3m x 0.7m | 110% | Plastic | No | No | None. Full IBCs delivered to site. | Drainage via the surface water drainage system | Full IBCs are delivered to site. Empty IBC replaced in situ. | Visual inspection | Unknown | Environmental Walk Days/ Night Shifts. Maintenance schedule of the tanks and bund unknown. | Pumped out | Bund covered by IBC storage. Rainwater unable to get into the bund.
10 | Ultrasil 69 IBC | Ultrasil 69 | 1000 | Back of pasteurising room | Plastic | Ultrasil 69 bund | Yes | No | 1100 | 1.6m x 1.3m x 0.7m | 110% | Plastic | No | No | None. Full IBCs delivered to site. | Drainage via the surface water drainage system | Full IBCs are delivered to site. Empty IBC replaced in situ. | Visual inspection | Unknown | Environmental Walk Days/ Night Shifts. Maintenance schedule of the tanks and bund unknown. | Pumped out | Bund covered by IBC storage. Rainwater unable to get into the bund.
11 | Ultrasil 78 IBC | Ultrasil 78 | 1000 | Back of pasteurising room | Plastic | Ultrasil 78 bund | Yes | No | 1100 | 1.6m x 1.3m x 0.7m | 110% | Plastic | No | No | None. Full IBCs delivered to site. | Drainage via the surface water drainage system | Full IBCs are delivered to site. Empty IBC replaced in situ. | Visual inspection | Unknown | Environmental Walk Days/ Night Shifts. Maintenance schedule of the tanks and bund unknown. | Pumped out | Bund covered by IBC storage. Rainwater unable to get into the bund.
12 | HCL Scrubber | Caustic 1.1 - 1.5 % | Unknown | Behind cheese packing | Plastic | Caustic bund | Yes | No | 6676 | N/A | #VALUE! | Concrete | Yes | No | Overflow pipe if caustic level gets too high. | Drainage via the surface water drainage system | The scrubber is filled via internal pipework, no drip capturing methods. | Visual inspection and monitoring via level instrumentation. | Unknown | Environmental Walk Days/ Night Shifts | Pumped out
13 | Deaeration chamber | Used as a Hotwell now filled with water | Unknwon | Boiler Area | Stainless Steel | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Unknown | Drainage via the surface water drainage system | N/A | Visual inspection | N/A | Unknown | N/A
14 | Deaeration chamber 2 | Steam | Unknown | Boiler Area | Stainless Steel | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Unknown | Drainage via the surface water drainage system | N/A | Visual inspection | N/A | Unknown | N/A
15 | Kerosene Tank 1 | Kerosene | 130000 | Boiler area | TBC | Kerosene Bund | Yes | Yes | 213750 | 15m x 7.5m x 1.90m | 164.4% | Concrete (block work) | No | No | Pumped out if spills using sump pump | Drainage via the surface water drainage system | Fill point external within delivery area. Drips captured in a pernament drip tray. | Visual inspection. Extent of instrumentation unknown. | Unknown | Unknown | Blind bund. Contents pumped out.
16 | Kerosene Tank 2 | Kerosene | 130000 | Boiler area | TBC | Kerosene Bund | Yes | Yes | 213750 | 15m x 7.5m x 1.90m | 164.4% | Concrete (block work) | No | No | Pumped out if spills using sump pump | Drainage via the surface water drainage system | Fill point external within delivery area. Drips captured in a pernament drip tray. | Visual inspection. Extent of instrumentation unknown. | Unknown | Unknown | Blind bund. Contents pumped out.
17 | Wood Pellet Pit | Wood pellets | Unknown | Boiler Area | Unknown | N/A | No - solids | N/A | N/A | N/A | N/A | N/A | N/A | N/A | None | Drainage via the surface water drainage system | N/A | Visual inspection. | N/A | Unknown | N/A
18 | Wood Pellet Silo | Wood pellets | 100 tonnes | Boiler Area | TBC (Assumed steel) | N/A | No - solids | N/A | N/A | N/A | N/A | N/A | N/A | N/A | None | Filled with wood pellets so no fluid present. Any fluid in the area is drained via the surface water drain and transferred to the WPF. | Pellets offloaded into a hopper and then transferred into the silos. Solid material, drip capture not applicable. | Visual inspection. Extent of instrumentation unknown. | N/A | Unknown | Unknown
19 | Wood Pellet Silo 2 | Wood pellets | 100 tonnes | Boiler Area | TBC (Assumed steel) | N/A | No - solids | N/A | N/A | N/A | N/A | N/A | N/A | N/A | None | Filled with wood pellets so no fluid prescent. Any fluid in the area is drained via the surface water drain and transferred to the WPF | Pellets offloaded into a hopper and then transferred into the silos. Solid material, drip capture not applicable. | Visual inspection. Extent of instrumentation unknown. | N/A | Unknown | Unknown
20 | Bulk chemical delivery area | Tanker delivery area for Caustic and Nitric Acid | N/A | Bulk Chemicals | N/A | Bulk chemical delivery bund | N/A | N/A | 7500 | 12.95m x 4.82m x 0.12m | N/A | Concrete | Yes | No | None | Drainage via the surface water drain and transferred to the WPF | Any spills from chemical delivery vehicles are contained within this bund. | None | Unknown | Environmental walk | Free drain to red drain (WPF)
21 | Tank 71 | Nitric Acid 35% | 30000 | Bulk Chemicals | Stainless Steel | Bulk chemical bund | Yes | Yes, small dwarf wall between 71 and 72 | 31698.75 | 1.07m x 7.5m x 3.95m | 105.7% | Concrete | Yes | No | Level monitoring | Drainage via the surface water drain and transferred to the WPF | Bulk Chemical off loading, drip tray, hosed to WPF drain | Level monitoring/transmitters/daily use. Visual inspection (walk over) | Unknown | Environmental Walk Days / Nights shifts. Maintenance schedule unknown. | Overpump from sump to red drain (WPF) or removal by contractor.
22 | Tank 72 | Caustic 47% | 30000 | Bulk Chemicals | Stainless Steel | Bulk chemical bund | Yes | Yes, small dwarf wall between 71 and 72 | 31698.75 | 1.07m x 7.5m x 3.95m | 105.7% | Concrete | Yes | No | Level monitoring | Drainage via the surface water drain and transferred to the WPF | Bulk Chemical off loading, drip tray, hosed to WPF drain | Level monitoring/transmitters/daily use. Visual inspection (walk over) | Unknown | Environmental Walk Days / Nights shifts. Maintenance schedule unknown. | Overpump from sump to red drain (WPF) or removal by contractor.
23 | Butter Tank 1 (Redundant) | Butter | 14000 | Butter room | Stainless Steel | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Redundant | Drained within the Butter Room and then transferred to WPF | Redundant | Redundant | N/A | Redundant | N/A | Butter is no longer being produced at Davidstow
24 | Butter Tank 2 (redundant) | Butter | 14000 | Butter room | Stainless Steel | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Redundant | Drained within the Butter Room and then transferred to WPF | Redundant | Redundant | N/A | Redundant | N/A | Butter is no longer being produced at Davidstow
25 | Cream Tank 1 | Cream | 14000 | Butter room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation. Extent of control unknown. | Drained within the Butter Room and then transferred to WPF | Filled from Tank 415 by closed pipework. Any leaks along this pipework will be captured by drainage within the respective room and and transferred to the WPF | Level monitoring. Visual inspection during site walk around. | N/A | Full maintenance schedules and inspections in place, details unknown | N/A
26 | Cream Tank 2 | Cream | 14000 | Butter room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation. Extent of control unknown. | Drained within the Butter Room and then transferred to WPF | Filled from Tank 415 by closed pipework. Any leaks along this pipework will be captured by drainage within the respective room and and transferred to the WPF | Level monitoring. Visual inspection during site walk around. | N/A | Full maintenance schedules and inspections in place, details unknown | N/A
27 | P3 Triquart AM 25 l drums | P3 Triquart AM | 25 | Cheese Room | Plastic | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A. 25 L containers are manually changed over when empty. | Drained within the Cheese Room and transferred to the WPF | N/A. Full containers delivered to site. Empty containers replaced in situ. | Visual only. | N/A | None | Free drain via red drainage system to WPF.
28 | Polix Chlorant 25 l drums | Polix Chlorant | 25 | Cheese Room | Plastic | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A. 25 L containers are manually changed over when empty. | Drained within the Cheese Room and transferred to the WPF | N/A. Full containers delivered to site. Empty containers replaced in situ. | Visual only. | N/A | None | Free drain via red drainage system to WPF.
29 | Pripan 25 l drums | Pripan | 25 | Cheese Room | Plastic | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A. 25 L containers are manually changed over when empty. | Drained within the Cheese Room and transferred to the WPF | N/A. Full containers delivered to site. Empty containers replaced in situ. | Visual only. | N/A | None | N/A
30 | T521 Whey tank | Whey | TBC | Cheese Room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation. Extent of control unknown. | Drained within the Cheese Room and transferred to the WPF | N/A | Visual inspection. | N/A | N/A | N/A
31 | T531 Whey Tank | Whey | TBC | Cheese Room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation. Extent of control unknown. | Drained within the Cheese Room and transferred to the WPF | N/A | Visual inspection. | N/A | N/A | N/A
32 | Tank 400 | Whey | 12000 | Cheese Room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation. Extent of control unknown. | Drained within the Cheese Room and transferred to the WPF | All filled from whey clarification tanks. Leakages will be drained to WPF. | Level instrumentation. Visual inspection. | N/A | Full maintenance schedules and inspections in place. Full maintenance schedule unknown. | N/A
33 | Tank 401 | Whey | 8000 | Cheese Room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation. Extent of control unknown. | Drained within the Cheese Room and transferred to the WPF | All filled from whey clarification tanks. Leakages will be drained to WPF. | Level instrumentation. Visual inspection. | N/A | Full maintenance schedules and inspections in place. Full maintenance schedule unknown. | N/A
34 | Tank 402 | Whey | 2000 | Cheese Room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation. Extent of control unknown. | Drained within the Cheese Room and transferred to the WPF | All filled from whey clarification tanks. Leakages will be drained to WPF. | Level instrumentation. Visual inspection. | N/A | Full maintenance schedules and inspections in place. Full maintenance schedule unknown. | N/A
35 | Tank 403 | Whey | 1000 | Cheese Room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation. Extent of control unknown. | Drained within the Cheese Room and transferred to the WPF | All filled from whey clarification tanks. Leakages will be drained to WPF. | Level instrumentation. Visual inspection. | N/A | Full maintenance schedules and inspections in place. Full maintenance schedule unknown. | N/A
36 | Tank 501 | Curds / Whey | 33000 | Cheese Room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation and alarmed. Extent of control unknown. | Drained within the Cheese Room and transferred to the WPF | N/A. No tanker fill point. Any drips from pipework will be contained by drainage in the building and transferred to the WPF. | Level monitoring. Visual inspection | N/A | Full maintenance schedules and inspections in place, details unknown | N/A
37 | Tank 503 | Curds / Whey | 33000 | Cheese Room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation and alarmed. Extent of control unknown. | Drained within the Cheese Room and transferred to the WPF | N/A. No tanker fill point. Any drips from pipework will be contained by drainage in the building and transferred to the WPF. | Level monitoring. Visual inspection | N/A | Full maintenance schedules and inspections in place, details unknown | N/A
38 | Tank 504 | Curds / Whey | 33000 | Cheese Room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation and alarmed. Extent of control unknown. | Drained within the Cheese Room and transferred to the WPF | N/A. No tanker fill point. Any drips from pipework will be contained by drainage in the building and transferred to the WPF. | Level monitoring. Visual inspection | N/A | Full maintenance schedules and inspections in place, details unknown | N/A
39 | Tank 505 | Curds / Whey | 33000 | Cheese Room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation and alarmed. Extent of control unknown. | Drained within the Cheese Room and transferred to the WPF | N/A. No tanker fill point. Any drips from pipework will be contained by drainage in the building and transferred to the WPF. | Level monitoring. Visual inspection | N/A | Full maintenance schedules and inspections in place, details unknown | N/A
40 | Tank 506 | Curds / Whey | 33000 | Cheese Room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation and alarmed. Extent of control unknown. | Drained within the Cheese Room and transferred to the WPF | N/A. No tanker fill point. Any drips from pipework will be contained by drainage in the building and transferred to the WPF. | Level monitoring. Visual inspection | N/A | Full maintenance schedules and inspections in place, details unknown | N/A
41 | Tank 507 | Curds / Whey | 33000 | Cheese Room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation and alarmed. Extent of control unknown. | Drained within the Cheese Room and transferred to the WPF | N/A. No tanker fill point. Any drips from pipework will be contained by drainage in the building and transferred to the WPF. | Level monitoring. Visual inspection | N/A | Full maintenance schedules and inspections in place, details unknown | N/A
42 | Tank 508 | Curds / Whey | 33000 | Cheese Room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation and alarmed. Extent of control unknown. | Drained within the Cheese Room and transferred to the WPF | N/A. No tanker fill point. Any drips from pipework will be contained by drainage in the building and transferred to the WPF. | Level monitoring. Visual inspection | N/A | Full maintenance schedules and inspections in place, details unknown | N/A
43 | Tank 509 | Curds / Whey | 33000 | Cheese Room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation and alarmed. Extent of control unknown. | Drained within the Cheese Room and transferred to the WPF | N/A. No tanker fill point. Any drips from pipework will be contained by drainage in the building and transferred to the WPF. | Level monitoring. Visual inspection | N/A | Full maintenance schedules and inspections in place, details unknown | N/A
44 | Tank 510 | Curds / Whey | 33000 | Cheese Room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation and alarmed. Extent of control unknown. | Drained within the Cheese Room and transferred to the WPF | N/A. No tanker fill point. Any drips from pipework will be contained by drainage in the building and transferred to the WPF. | Level monitoring. Visual inspection | N/A | Full maintenance schedules and inspections in place, details unknown | N/A
45 | Tank 511 | Curds / Whey | 33000 | Cheese Room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation and alarmed. Extent of control unknown. | Drained within the Cheese Room and transferred to the WPF | N/A. No tanker fill point. Any drips from pipework will be contained by drainage in the building and transferred to the WPF. | Level monitoring. Visual inspection | N/A | Full maintenance schedules and inspections in place, details unknown | N/A
46 | Tank 512 | Curds / Whey | 33000 | Cheese Room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Not yet in use | Drained within the Cheese Room and transferred to the WPF | Not yet in use | Not yet in use | Not yet in use | Not yet in use | Not yet in use
47 | Tank502 | Curds / Whey | 33000 | Cheese Room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation and alarmed | Drained within the Cheese Room and transferred to the WPF | All filled from pasteurising room, drips will be drained to WPF | Level monitoring | N/A | Full maintenance schedules and inspections in place, details unknown | N/A
48 | Topaz MD1 25 l drums | Topaz MD1 | 25 | Cheese Room | Plastic | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | None | Drained within the Cheese Room and transferred to the WPF | N/A | Visual only. | N/A | None | N/A
49 | Ansep CIP IBC | Sodium Hydroxide (5% to 10%) and sodium Hypochlorite ( 3% to 5%) | 1000 | CIP Five (Tanker) inside | Plastic | Tanker CIP IBC bund | Yes | Yes (Horolith IBC) | 950 |  | 95% | Plastic | No | No | N/A. IBCs are filled off-site and empty IBCs are replaced in situ. | Drained within CIP 5 and transferred to the WPF | N/A | Visual inspection | Unknown | Environmental Walk Days/ Night Shifts | Overpump from sump to red drain (WPF)
50 | Gamo GR 20 l drum | Gamo GR | 20 | CIP Five (Tanker) inside | Plastic | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | None | Drained within CIP 5 and transferred to the WPF | N/A (empty contianer replaced with new container in situ) | Visual only. | N/A | Environmental Walk Days/ Night Shifts | Free drain to red drain (WPF)
51 | Horolith SD IBC | Sulphamic acid (15%-20%) | 1000 | CIP Five (Tanker) inside | Plastic | Tanker CIP IBC bund | Yes | Yes (Caustic IBC) | 950 |  | 95% | Plastic | No | No | N/A. IBCs are filled off-site and empty IBCs are replaced in situ. | Drained within CIP 5 and transferred to the WPF | N/A | Visual inspection | Unknown | Environmental Walk Days/ Night Shifts | Overpump from sump to red drain (WPF)
52 | Tank 951 | Water | 5000 | CIP Five (Tanker) inside | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation . Control/ inhibition of forward feed unknown. | Drained within CIP 5 and transferred to the WPF | N/A | Level instrumentation . Visual inspection | N/A | Full maintenance schedules and inspections in place. Actual schedule unknown. | Free drain to red drain (WPF)
53 | Tank 952 | Recovery Rinse | 2000 | CIP Five (Tanker) inside | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation . Control/ inhibition of forward feed unknown. | Drained within CIP 5 and transferred to the WPF | N/A | Level instrumentation . Visual inspection | N/A | Full maintenance schedules and inspections in place. Actual schedule unknown. | Free drain to red drain (WPF)
54 | Tank 954 | Ansep Caustic 0.18%/ Horolith Acid @ 0.2% | 4000 | CIP Five (Tanker) inside | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation . Control/ inhibition of forward feed unknown. | Drained within CIP 5 and transferred to the WPF | Filled from IBCs behind the tank. No tanker fill point | Level instrumentation . Visual inspection | N/A | Full maintenance schedules and inspections in place. Actual schedule unknown. | Free drain to red drain (WPF)
55 | Triquart AM 20l drum | Triquart AM | 20 | CIP Five (Tanker) inside | Plastic | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | None | Drained within CIP 5 and transferred to the WPF | Container replaced with new container in situ when empty. | Visual only. | N/A | Environmental Walk Days / Nights shifts | Free drain to red drain (WPF)
56 | Milk tanker wash area | Wash water from milk tanker cleaning. | N/A | CIP Five (Tanker) outside | Concrete | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | None (vivual inspection of surface drianage only). | Drainage via the surface water drain and transferred to the WPF | N/A | N/A | N/A | Unknown | Free drain to red drain (WPF) | This area collects the wash out of the milk delivery tankers. These are cleaned after each delivery.
57 | Condensate recovery tank | Condensate | TBC | Cip One inside | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Not yet in use, level instrumentation will be put in place. Intrumentation control unknown. | Drained within CIP 1 and transferred to the WPF | Not currently in use | Not currently in use | N/A | Not currently in use | N/A | Still to be commissioned. Currently not in service.
58 | Tank 911 | Water | 6000 | Cip One inside | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation, control unknown. | Drained within CIP 1 and transferred to the WPF | No tanker fill point. Internal pipework fed from IBCs outside the building. | Level instrumentation (unknown if alarmed). Visual inspection. | N/A | Planned maintenance schedules and inspections. Actual schedule unknown. | N/A
59 | Tank 912 | Rinse Recovery | 6000 | Cip One inside | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation, control unknown. | Drained within CIP 1 and transferred to the WPF | No tanker fill point. Internal pipework fed from IBCs outside the building. | Level instrumentation (unknown if alarmed). Visual inspection. | N/A | Planned maintenance schedules and inspections. Actual schedule unknown. | N/A
60 | Tank 913 | Acid .8% or Caustic 1% | 6000 | Cip One inside | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation, control unknown. | Drained within CIP 1 and transferred to the WPF | No tanker fill point. Internal pipework fed from IBCs outside the building. | Level instrumentation (unknown if alarmed). Visual inspection. | N/A | Planned maintenance schedules and inspections. Actual schedule unknown. | N/A
61 | P3 Oxysan IBC 1 | P3 Oxysan (30% to 50% acetic acid, 5% to 10% peracetic acid, 5% to 8% hydrogen peroxide, 3% to 5% octanoic acid, 0.5% to 1% peroxyoctanoic acid) | 1000 | Cip Seven inside | Plastic | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Full IBCs are delivered to site. Empty IBCs are replaced in situ. Visual indication of level. | Drainage within CIP 7 and transferred to the WPF | N/A | Visual inspection | Unknown | Environmental Walk Days/ Night Shifts | N/A
62 | Tank 973 | Acid @ .9% | 20000 | Cip Seven inside | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation. Control unknown. | Drainage within CIP 7 and transferred to the WPF | No tanker fill point. Acid supplied from bulk acid storage tank. Water supplied from mains system. | Level monitoring and visual inspection. | N/A | Planned maintenance schedules and inspections. Actual schedule unknown. | N/A
63 | Tank 974 | Caustic 1.1% | 20000 | Cip Seven inside | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation. Control unknown. | Drainage within CIP 7 and transferred to the WPF | No tanker fill point. Caustic provided from bulk storage tank. Water provided from mains system. | Level monitoring and visual inspection. | N/A | Planned maintenance schedules and inspections. Actual schedule unknown. | N/A
64 | P3 Oxysan IBC 2 | P3 Oxysan (30% to 50% acetic acid, 5% to 10% peracetic acid, 5% to 8% hydrogen peroxide, 3% to 5% octanoic acid, 0.5% to 1% peroxyoctanoic acid) | 1000 | Cip Seven outside | Plastic | P3 Oxysan Bund 1 | Yes | No | 1100 | 1.6m x 1.3m x 0.7m | 110% | Plastic | No | No | Full IBCs are delivered to site. Empty IBCs are replaced in situ. Visual indication of level. | Drainage via the surface water drain and transferred to the WPF | N/A | Visual inspection | Unknown | Environmental Walk Days/ Night Shifts | Pumped out
65 | Tank 971 | Water | 40000 | Cip Seven outside | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation. Control unknown. | Drainage via the surface water drain and transferred to the WPF | No tanker fill point. Tank is filled via internal pipework. | Level monitoring. Visual inspection. | N/A | Environmental Walk Days/ Night Shifts. Maintenance schedule unknown. | N/A
66 | Tank 975 | Hot water | 40000 | Cip Seven outside | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation. Control unknown. | Drainage via the surface water drain and transferred to the WPF | No tanker fill point. Tank is filled via internal pipework. | Level monitoring. Visual inspection. | N/A | Environmental Walk Days/ Night Shifts. Maintenance schedule unknown. | N/A
67 | Paracetic Acid IBC | Paracetic acid | 1000 | Cip Three inside | Plastic | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Full IBCs are delivered to site. Empty IBCs are replaced in situ. Visual indication of level. | Drained within CIP 3 and transferred to the WPF | IBCs are filled off-site | Visual inspection | Unknown | Environmental Walk Days/ Night Shifts. Maintenance schedule unknown. | Bund emptied via a submersible pump
68 | Tank 933 | Nitric acid .9% | 20000 | Cip Three inside | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation. Control unknown. | Drained within CIP 3 and transferred to the WPF | Filled from bulk nitric acid storage tank and diluted into a solution. Filled via internal pipework, not tanker fill point. Drip capture not appliocable. | Level instrumentation. Control unknown. | N/A | Visual inspections. Actual maintenance schedule unknown. | N/A
69 | Tank 934 | Caustic 1.1% | 20000 | Cip Three inside | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation. Control unknown. | Drained within CIP 3 and transferred to the WPF | Filled from bulk nitric acid storage tank and diluted into a solution. Filled via internal pipework, not tanker fill point. Drip capture not appliocable. | Level instrumentation. Control unknown. | N/A | Visual inspections. Actual maintenance schedule unknown. | N/A
70 | IBC HCL Scrubber | HCL Scrubber | 1000 | Cip Three outside | Plastic | Scrubber IBC | Yes | No | 1100 | 1.15m x 1.57m x 0.5m | 110% | Plastic | No | No | Full IBCs are delivered to site. Empty IBCs are replaced in situ. Visual indication of level. | Drainage via the surface water drain and transferred to the WPF | Full IBC delivered to site. Tanker fill point and drip collection not applicable. | Visual inspection | Unknown | Environmental Walk Days/ Night Shifts. Maintenance schedule unknown. | Bund emptied via a submersible pump
71 | Tank 931 | Water | 40000 | Cip Three outside | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation. Control unknown. | Drainage via the surface water drain and transferred to the WPF | No tanker fill point. Supplied by internal pipework | Level instrumentation. Control unknown. | N/A | Environmental Walk Days/ Night Shifts. Maintenance schedule unknown. | N/A
72 | Tank 932 | Rinse Recovery | 113000 | Cip Three outside | Stainless Steel | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation. Control unknown. | Drainage via the surface water drain and transferred to the WPF | No tanker fill point. Supplied by internal pipework. | Level instrumentation. Control unknown. | N/A | Environmental Walk Days/ Night Shifts. Maintenance schedule unknown. | N/A
73 | Attenuation Tank | CIP return/waste | 120000 | Cip Three outside (next to Tank 931 and 932) | Stainless Steel | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Unknown. | Drainage via the surface water drain and transferred to the WPF | Tank fed from contained pipework. No tanker fill point. | Visual inspection. | N/A | N/A | N/A
74 | AP1500 Multiflo polymer make up system | Polymer solution | 1500 | Calcium Phosphate Plant | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation unknown. | Drainage via the surface water drain and transferred to the WPF | N/A. Filled with liquid polymer from IBCs and water from mains water supply. | Visual inspection. Unknown level instrumentation/control. | N/A | Operational walk over. Maintenance schedule unknown. | N/A
75 | AP500 - Belt press automatic polymer system | Polymer solution | 500 | Calcium Phosphate Plant (CPP) | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Assumed level instrumentation to inhibit polymer make up. | Drainage via the surface water drain and transferred to the WPF | No tanker connection, tank is filled with water and liquid polymer via integral pipework | Visual inspection. | N/A | Unknown | N/A. If tank were to leak, contents would flow to site drainage and ultimately to the WPF.
76 | Aquatreat N223 F (polymer) IBC 1 | Aquatreat N223 F (polymer) | 1000 | CPP | Plastic | N/A | Yes | Yes (Other N223F IBC) | 1150 | 2.34m x 1.36m x 0.52m | 115% | Plastic | No | No | IBCs are delivered to site full and the empty IBC replaced in situ. Overfill protection not applicable. | Drainage via the surface water drain and transferred to the WPF | IBCs are delivered to site full and the empty IBC replaced in situ. | Visual inspection | Unknown | Environmental Walk Days/ Night Shifts | Bund emptied using submersible pump.
77 | Aquatreat N223 F (polymer) IBC 2 | Aquatreat N223 F (polymer) | 1000 | CPP | Plastic | N/A | Yes | Yes (Other N223F IBC) | 1150 | 2.34m x 1.36m x 0.52m | 115% | Plastic | No | No | IBCs are delivered to site full and the empty IBC replaced in situ. Overfill protection not applicable. | Drainage via the surface water drain and transferred to the WPF | IBCs are delivered to site full and the empty IBC replaced in situ. | Visual inspection | Unknown | Environmental Walk Days/ Night Shifts | Bund emptied using submersible pump.
78 | Buffer Tank | Untreated Demin Waste Water | 260000 | CPP | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Unknown | Drainage via the surface water drain and transferred to the WPF | N/A. Feed via pipework. | Visual inspection. | N/A | N/A | N/A
79 | Bund lagoon fill | Unknown | Not a tank | CPP | Concrete | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | None | Any accumulation within the Lagoons are transferred to the WPF | N/A. No tanker fill point. | None | Unknown | EnvironmentalWalks | N/A
80 | CPP Lagoon | Various | 330000 | CPP | Concrete / Blockwork | N/A | Underground tank | N/A | N/A | N/A | N/A | N/A | N/A | N/A | None | Drainage via the surface water drain and transferred to the WPF | N/A. No tanker fill point. | Visual inspection. Unknown level instrumentation/control. | Unknown | EnvironmentalWalks | N/A
81 | Fire Sprinkler Storage Tank | Water | 1094000 | CPP | Stainless Steel | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Unknown | Drainage via the surface water drain and transferred to the WPF | N/A. No tanker fill point. | Visual inspection. Unknown level instrumentation/control. | N/A | Operational walk over. Maintenance schedule unknown. | N/A
82 | Lime silo | Calcium hydroxide | 11976.0479 | CPP | Glass Lined Steel | Lime silo bund | Yes | Yes (Lime slurry mixing tanks) | 7662.465 | 6.33m x 8.07m x 0.15m | 63.98% | Concrete | Yes - drain runs through the centre of the bunded area. | No | None | Drainage via the surface water drain and transferred to the WPF | Fill point at low level and contained within the bunded area. | Visual inspection. Unknown level instrumentation/control. | Unknown | Operational walk over. Maintenance schedule unknown. | Hosed down into drainage in the middle of the bund.
83 | Lime Slurry Mixing Tank 1 | Calcium hydroxide | 3500 | CPP | Glass Lined Steel | Lime silo bund | Yes | Yes (Lime silo and other lime slurry mixing tank) | 7662.465 | 6.33m x 8.07m x 0.15m | 218.9% | Concrete | Yes - drain runs through the centre of the bunded area. | No | Overflow pipe | Drainage via the surface water drain and transferred to the WPF | N/A filled with lime from the silo and water. Drip capture not applicable. | Visual inspection. Unknown level instrumentation/control. | Unknown | Operational walk over. Maintenance schedule unknown. | Hosed down into drainage in the middle of the bund.
84 | Lime Slurry Mixing Tank 2 | Calcium hydroxide | 3500 | CPP | Glass Lined Steel | Lime silo bund | Yes | Yes (Lime silo and other lime slurry mixing tank) | 7662.465 | 6.33m x 8.07m x 0.15m | 218.9% | Concrete | Yes - drain runs through the centre of the bunded area. | No | Overflow pipe | Drainage via the surface water drain and transferred to the WPF | N/A filled with lime from the silo and water. Drip capture not applicable. | Visual inspection. Unknown level instrumentation/control. | Unknown | Operational walk over. Maintenance schedule unknown. | Hosed down into drainage in the middle of the bund.
85 | Oil tank (adjacent to fire sprinklet tank) | Oil | 2500 | CPP | Plastic | Oil storage tank and bund. | Yes | Integral | TBC | TBC | TBC | Plastic | No | No | Overfill prevention valve | Drainage via the surface water drain and transferred to the WPF | Fill point within a locked cabinet. Any drips are contained within the integral bund og the tank | Unknown | Unknown | Operational walk over. Maintenance schedule unknown. | Sealed bund which will be pumped out
86 | Prod Lagoon | Various | 330000 | CPP | Concrete / Blockwork | N/A | Underground tank | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Unknown. | Drainage via the surface water drain and transferred to the WPF | N/A | N/A | N/A | Unknown | N/A
87 | Sulphuric Acid IBC | Sulphuric acid | 1000 | CPP | Plastic | Fire sprinkley sulphuric acid IBC Bund | Yes | Yes (waste oil drums) | 1140 | N/A | 114% | Plastic | No | No | N/A. Full IBCs delivered to site. Empty IBCs are replaced in situ. | Drainage via the surface water drain and transferred to the WPF | N/A. Empty IBCs are replaced with full IBCs in situ | Visual inspection | Unknown | Operational walk over. Maintenance schedule unknown. | Pumped out
88 | Sulphuric Tank 1 | Sulphuric Acid | Unknown. Tank offline. | CPP | Plastic | Sulphuric acid tank 1 | Yes | No | Unknown | Unknown | #VALUE! | Plastic | No | No | External site glass during delivery. Unkown if there is digital level monitoring | Drainage via the surface water drain and transferred to the WPF | Tanker fill p[oint adjacent to main road. Drips contained in local hardstanding. Unknown if the delivery area is a bunded area. | Visual inspection, external level indication. | Unknown | Operational walk over. Maintenance schedule unknown. | Sealed bund which will be pumped out
89 | Sulphuric tank 2 | Sulphuric Acid | Unknown. Tank offline. | CPP | Plastic | Sulphuric acid tank 2 | Yes | No | Unknown | Unknown | #VALUE! | Plastic | No | No | External site glass during delivery. Unkown if there is digital level monitoring | Drainage via the surface water drain and transferred to the WPF | Tanker fill p[oint adjacent to main road. Drips contained in local hardstanding. Unknown if the delivery area is a bunded area. | Visual inspection, external level indication. | Unknown | Operational walk over. Maintenance schedule unknown. | Sealed bund which will be pumped out
90 | Sulpuric Acid Tank No1 | 77% Sulphuric | 7500 | CPP | Plastic | Temporary sulphuric acid tank 1 bund | Yes - Double Bunded | No | Unknown | Unknown | #VALUE! | Plastic | Yes | No | Unknown. | Drainage via the surface water drain and transferred to the WPF | Tankers pull up near tank and fill from fill valve. Drips are captured in a temporary plastic container. | Visual inspection. Level monitoring. Cat and mouse level indication. | Unknown | Operational walk over. Maintenance schedule unknown. | Via a drain valve. | Temporary installation whilst permanent sulphuric acid storage tanks are replaced.
91 | Sulpuric Acid Tank No2 | 77% Sulphuric | 7500 | CPP | Plastic | Temporary sulphuric acid tank 2 bund | Yes - Double Bunded | No | Unknown | Unknown | #VALUE! | Plastic | Yes | No | Unknown. | Drainage via the surface water drain and transferred to the WPF | Tankers pull up near tank and fill from fill valve. Drips are captured in a temporary plastic container. | Visual inspection. Level monitoring. Cat and mouse level indication. | Unknown | Operational walk over. Maintenance schedule unknown. | Via a drain valve. | Temporary installation whilst permanent sulphuric acid storage tanks are replaced.
92 | Sulpuric Acid Tank No3 | 77% Sulphuric | 7500 | CPP | Plastic | Temporary sulphuric acid tank 3 bund | Yes - Double Bunded | No | Unknown | Unknown | #VALUE! | Plastic | Yes | No | Unknown. | Drainage via the surface water drain and transferred to the WPF | Tankers pull up near tank and fill from fill valve. Drips are captured in a temporary plastic container. | Visual inspection. Level monitoring. Cat and mouse level indication. | Unknown | Operational walk over. Maintenance schedule unknown. | Via a drain valve. | Temporary installation whilst permanent sulphuric acid storage tanks are replaced.
93 | Sulphuric Acid IBC 2 by Buffer Tank | 50% Sulphuric acid | 1000 | CPP (Buffer Tank) | Plastic | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A. Full IBCs delivered to site. Empty IBCs are replaced in situ. | Drainage via the surface water drain and transferred to the WPF | N/A. Empty IBCs are replaced with full IBCs in situ | Visual inspection | N/A | Operational walk over. Maintenance schedule unknown. | Pumped out | Used IBCs with approximately 100L and 200L of liquid in each IBC respectively.
94 | Sulphuric Acid IBC by Buffer Tank | 50% Sulphuric acid | 1000 | CPP (Buffer Tank) | Plastic | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A. Full IBCs delivered to site. Empty IBCs are replaced in situ. | Drainage via the surface water drain and transferred to the WPF | N/A. Empty IBCs are replaced with full IBCs in situ | Visual inspection | N/A | Operational walk over. Maintenance schedule unknown. | Pumped out | Used IBCs with approximately 100L and 200L of liquid in each IBC respectively. Correct at time of site visit.
95 | 106T100 CIP | Water | 12000 | Demin D90 CIP room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Unknown. Unable to survey as CIP room was cordoned off due to an acid leak. | Drained within Demin D90 CIP room and transferred to the WPF | No tanker fill point. Tank is filled by pipework. Drip capture not applicable. | TBC | Unknown | TBC | TBC
96 | 106T200 CIP Rinse Water | CIP Rinse Water | 12000 | Demin D90 CIP room | Stainless Steel | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Unknown. Unable to survey as CIP room was cordoned off due to an acid leak. | Drained within Demin D90 CIP room and transferred to the WPF | No tanker fill point. Tank is filled of Demin plant CIP rinse water by closed pipework. Drip capture not applicable. | TBC | Unknown | TBC | TBC
97 | 106T300 CIP | Caustic 1.1 - 1.5 % | 12000 | Demin D90 CIP room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Unknown. Unable to survey as CIP room was cordoned off due to an acid leak. | Drained within Demin D90 CIP room and transferred to the WPF | No tanker fill point. Tank is filled from main caustic tank by closed pipework. Drip capture not applicable. | TBC | Unknown | TBC | TBC
98 | 106T400 CIP | Nitric Acid 0.9% – 1.1% | 12000 | Demin D90 CIP room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Unknown. Unable to survey as CIP room was cordoned off due to an acid leak. | Drained within Demin D90 CIP room and transferred to the WPF | No tanker fill point. Tank is filled from main nitric acid tank by closed pipework. Drip capture not applicable. | TBC | Unknown | TBC | TBC
99 | 103T100 Water recovery tank | Brine | 110000 | Demin general care room | Stainless Steel | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC - assumed level instrumentation and alarm. | Drained within Demin general care room and transferred to the WPF | No tanker fill point. Water recovery from anionic flushes and hot washes fed by pipework. Drip capture not applicable. | TBC. Assumed level instrumentation and visual inspections. | N/A. No designated tank bund. | Not known. | N/A | Common drain in building also receives drainage from pumps and pipework.
100 | 103T200 Water recovery tank | Brine | 110000 | Demin general care room | Stainless Steel | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC - assumed level instrumentation and alarm. | Drained within Demin general care room and transferred to the WPF | Water recovery from anionic flushes for reuse and twice a week used for a hot wash of the anioninc tank | TBC. Assumed level instrumentation and visual inspections. | N/A. No designated tank bund. | Not known. | N/A | Common drain in building also receives drainage from pumps and pipework.
101 | 105T100 CIP recovery tank | Water | TBC | Demin general care room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation. Control unknown. | Drained within Demin general care room and transferred to the WPF | AWC acid water treatment from resin tanks | TBC. Assumed level instrumentation and visual inspections. | N/A. No designated tank bund. | Not known. | N/A | Common drain in building also receives drainage from pumps and pipework when taken offline for maintenance.
102 | 105T200 CIP recovery tank | Water and Caustic | TBC | Demin general care room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation. Control unknown. | Drained within Demin general care room and transferred to the WPF | TBC | TBC. Assumed level instrumentation and visual inspections. | N/A. No designated tank bund. | Not known. | N/A | Common drain in building also receives drainage from pumps and pipework when taken offline for maintenance.
103 | 101T100 NF Buffer Tank | Whey | 110000 | Demin high care tank farm | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC - assumed level instrumentation and alarm. | Drained within Demin high care tank farm and transferred to the WPF | No tanker fill point. Delivered from whey seperation (tank farm) via closed pipework. | TBC. Assumed level instrumentation and visual inspections. | N/A. No designated tank bund. | N/A. No designated tank bund | N/A | Common drain in building also receives drainage from pumps and pipework when taken offline for maintenance.
104 | 102T100 D90 Concentration Tank | Concentrated Whey | 170000 | Demin high care tank farm | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC - assumed level instrumentation and alarm. | Drained within Demin high care tank farm and transferred to the WPF | No tanker fill point. Fed from demin. Demineralised waste to evaporator and drier. Drip capture not applicable. | TBC. Assumed level instrumentation and visual inspections. | N/A. No designated tank bund. | N/A. No designated tank bund | N/A | Common drain in building also receives drainage from pumps and pipework when taken offline for maintenance.
105 | 102T200 D90 Concentration Tank | Concentrated Whey | 170000 | Demin high care tank farm | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC - assumed level instrumentation and alarm. | Drained within Demin high care tank farm and transferred to the WPF | No tanker fill point. Fed from demin. Demineralised waste to evaporator and drier. Drip capture not applicable. | TBC. Assumed level instrumentation and visual inspections. | N/A. No designated tank bund. | N/A. No designated tank bund | N/A | Common drain in building also receives drainage from pumps and pipework when taken offline for maintenance.
106 | 102T300 D90 Concentration Tank | Concentrated Whey | 170000 | Demin high care tank farm | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC - assumed level instrumentation and alarm. | Drained within Demin high care tank farm and transferred to the WPF | No tanker fill point. Fed from demin. Demineralised waste to evaporator and drier. Drip capture not applicable. | TBC. Assumed level instrumentation and visual inspections. | N/A. No designated tank bund. | N/A. No designated tank bund | N/A | Common drain in building also receives drainage from pumps and pipework when taken offline for maintenance.
107 | 104T100 | Water Tanks | 160000 | Demin high care tank farm | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC - assumed level instrumentation and alarm. | Drained within Demin high care tank farm and transferred to the WPF | No tanker fill point. Chilled water is stored and recycled from the mains supply | TBC. Assumed level instrumentation and visual inspections. | N/A. No designated tank bund. | N/A. No designated tank bund | N/A | Common drain in building also receives drainage from pumps and pipework when taken offline for maintenance.
108 | 104T200 | Water Tanks | 160000 | Demin high care tank farm | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC - assumed level instrumentation and alarm. | Drained within Demin high care tank farm and transferred to the WPF | No tanker fill point. Chilled water is stored and recycled from the mains supply | TBC. Assumed level instrumentation and visual inspections. | N/A. No designated tank bund. | N/A. No designated tank bund | N/A | Common drain in building also receives drainage from pumps and pipework when taken offline for maintenance.
109 | Recovered water Tank 20 | Recovered water | TBC | Demin high care tank farm | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC - assumed level instrumentation and alarm. | Drained within the Demin High Care Tank Farm and transferred to the WPF | TBC | TBC. Assumed level instrumentation and visual inspections. | N/A. No designated tank bund. | N/A. No designated tank bund | N/A
110 | 207T110 | KOH 12.5 % | 2000 | Demin mineral standardising room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation. Control unknown. | Drained within Demin mineral standardising room and transferred to the WPF. Common drain shared with 207T120, 207T130 and 207T210. | N/A. Tank fed from KOH IBCs in the chemical stores.. | Level instrumentation. Unknown control. Visual inspection during operational checks. | N/A. No tank bund. | N/A. No tank bund. | Tank not bunded. Drainage flows via the red drain system and ultimately the WPF.
111 | 207T120 | Caustic 10 % | 2000 | Demin mineral standardising room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation. Control unknown. | Drained within Demin mineral standardising room and transferred to the WPF. Common drain shared with 207T110, 207T130 and 207T210. | N/A. Caustic fed from main caustic supply. Potable water fed from network, | Level instrumentation. Unknown control. Visual inspection during operational checks. | N/A. No tank bund. | N/A. No tank bund. | Tank not bunded. Drainage flows via the red drain system and ultimately to the WPF.
112 | 207T130 | CaOH2 Tank (Never used) | 2000 | Demin mineral standardising room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation. Control unknown. | Drained within Demin mineral standardising room and transferred to the WPF. Common drain shared with 207T110, 207T120 and 207T210. | From chemical stores transferring from KOH IBCs. | Level instrumentation. Unknown control. Visual inspection during operational checks. | N/A. No tank bund. | N/A. No tank bund. | Tank not bunded. Drainage flows via the red drain system and ultimately to the WPF.
113 | 207T210 | Citric acid 25 % | 4000 | Demin mineral standardising room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation. Control unknown. | Drained within Demin mineral standardising room and transferred to the WPF. Common drain shared with 207T110, 207T120 and 207T130. | N/A. Tank fed from citric acid IBCs in the chemical stores.. | Level instrumentation. Unknown control. Visual inspection during operational checks. | N/A. No tank bund. | N/A. No tank bund. | Tank not bunded. Drainage flows via the red drain system and ultimately to the WPF.
114 | 201C100 Carboxyl Tank | Resin (whey and HCL flushed through) | 14000 | Demin whey process area | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation. Unknown control. Site glass. | Drained within the Demin Whey Process Area and transferred to the WPF | Unknown how the resin is filled. Liquid flow is fed from the seperated whey silos via pipework. | Site glass, visual inspections. Extent of level instrumentation and its control is unknown. | N/A. No tank bund. | Unknown. Tank bund not applicable. | N/A. No tank bund.
115 | 201C200 Carboxyl Tank | Resin (whey and HCL flushed through) | 14000 | Demin whey process area | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation. Unknown control. Site glass. | Drained within the Demin Whey Process Area and transferred to the WPF | Unknown how the resin is filled. Liquid flow is from the seperated whey silos. | Site glass, visual inspections. Extent of level instrumentation and its control is unknown. | N/A. No tank bund. | Unknown. Tank bund not applicable. | N/A. No tank bund.
116 | 202C100 Mixed Beds | Resin (whey and HCL flushed through) | 14000 | Demin whey process area | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation. Unknown control. Site glass. | Drained within the Demin Whey Process Area and transferred to the WPF | Unknown how the resin is filled. Liquid flow is from the seperated whey silos. | Site glass, visual inspections. Extent of level instrumentation and its control is unknown. | N/A. No tank bund. | Unknown. Tank bund not applicable. | N/A. No tank bund.
117 | 202C200 Mixed Beds | Resin (whey and HCL flushed through) | 14000 | Demin whey process area | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation. Unknown control. Site glass. | Drained within the Demin Whey Process Area and transferred to the WPF | Unknown how the resin is filled. Liquid flow is from the seperated whey silos. | Site glass, visual inspections. Extent of level instrumentation and its control is unknown. | N/A. No tank bund. | Unknown. Tank bund not applicable. | N/A. No tank bund.
118 | 203T001 Nanofiltration Retentate Tank | Seperated whey (retentate from nanofiltration) | 1500 | Demin whey process area | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Unknown | Drained within the Demin Whey Process Area and transferred to the WPF | N/A. Seperated whey is fed from the tank farm by pipework | Visual inspections. Extent of level instrumentation and its control is unknown. | N/A. No tank bund. | Unknown. Tank bund not applicable. | N/A. No tank bund.
119 | 204T100 Pasteurisation tank | Whey | 1000 | Demin whey process area | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Unknown | Drained within the Demin Whey Process Area and transferred to the WPF | No tanker fill point. Drip capture not applicable. | Visual inspections. Extent of level instrumentation and its control is unknown. | N/A. No tank bund. | Unknown maintenance schedule for the tanks. No bund therefore no bund maintenance. | N/A.
120 | 204T160 Electodialysis Buffer tank | Seperated whey | 3000 | Demin whey process area | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Unknown | Drained within the Demin Whey Process Area and transferred to the WPF | N/A. Tank fed by pipework. | Visual inspections. Extent of level instrumentation and its control is unknown. | N/A. No tank bund. | Unknown. Tank bund not applicable. | N/A. No tank bund.
121 | 204T200 Brine Tank 1 | Brine | 2000 | Demin whey process area | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Overflow pipework to drain. | Drained within the Demin Whey Process Area and transferred to the WPF | No tanker fill point. Fed by pipework from nanofiltration units (permeate stream). | Visual inspections. Extent of level instrumentation and its control is unknown. | N/A. No tank bund. | Unknown maintenance schedule for the tanks. No bund therefore no bund maintenance. | N/A.
122 | 204T201 Brine Tank 2 | Brine | 2000 | Demin whey process area | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Overflow pipework to drain via brine tank 1. | Drained within the Demin Whey Process Area and transferred to the WPF | No tanker fill point. Fed by pipework from nanofiltration units (permeate stream). | Visual inspections. Extent of level instrumentation and its control is unknown. | N/A. No tank bund. | Unknown maintenance schedule for the tanks. No bund therefore no bund maintenance. | N/A.
123 | 204T300 Electrolite Tank | Nitric acid 13 - 20 % | 2000 | Demin whey process area | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation. Control unknown. | Drained within the Demin Whey Process Area and transferred to the WPF | N/A. Tank fed by pipework from the whey seperation area. Drip capture not applicable. | Level monitors and pressure readings | N/A. No tank bund. | Unknown maintenance schedule for the tanks. No bund therefore no bund maintenance. | N/A.
124 | 206C100 Anionic Column | Resin, (Whey and caustic flush through) | 12000 | Demin whey process area | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation. Control unknown. | Drained within the Demin Whey Process Area and transferred to the WPF | N/A. Tank fed by pipework from the whey seperation area. Drip capture not applicable. | Level monitoring and checks from engineers | N/A. No tank bund. | Unknown maintenance schedule for the tanks. No bund therefore no bund maintenance. | N/A.
125 | 206C200 Anionic Column | Resin, (Whey and caustic flush through) | 12000 | Demin whey process area | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation. Control unknown. | Drained within the Demin Whey Process Area and transferred to the WPF | N/A. Tank fed by pipework from the whey seperation area. Drip capture not applicable. | Level monitoring and checks from engineers. Visual inspection | N/A. No tank bund. | Unknown maintenance schedule for the tanks. No bund therefore no bund maintenance. | N/A.
126 | 206T001 Anionic Buffer Tank | whey | 1500 | Demin whey process area | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation. Control unknown. | Drained within the Demin Whey Process Area and transferred to the WPF | N/A. Tank fed by pipework from the pasteuriser. Drip capture not applicable. | Level monitoring and checks from engineers. Visual inspection | N/A. No tank bund. | Unknown maintenance schedule for the tanks. No bund therefore no bund maintenance. | N/A.
127 | 209T001 RO Buffer Tank | permeate | 1000 | Demin whey process area | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation. Control unknown. | Drained within the Demin Whey Process Area and transferred to the WPF | No tanker fill point. Fed from raw water recovery tank farm. Drip capture not applicable | Level monitoring and checks from engineers. Visual inspection | N/A. No tank bund. | Unknown maintenance schedule for the tanks. No bund therefore no bund maintenance. | N/A.
128 | C21C01 WPC Tank | Whey | 2000 | Demin whey process area | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation. Control unknown. | Drained within the Demin Whey Process Area and transferred to the WPF | No tanker fill point. Drip capture not applicable. | Level monitoring and checks from engineers. Visual inspection | N/A. No tank bund. | Unknown maintenance schedule for the tanks. No bund therefore no bund maintenance. | N/A.
129 | C21C02 WPC Tank | Whey | 2000 | Demin whey process area | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation. Control unknown. | Drained within the Demin Whey Process Area and transferred to the WPF | No tanker fill point. Drip capture not applicable. | Level monitoring and checks from engineers. Visual inspection | N/A. No tank bund. | Unknown maintenance schedule for the tanks. No bund therefore no bund maintenance. | N/A.
130 | Drier CIP Tank 1 | Caustic solution | TBC | Drier | TBC | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation. Control unknown. | Drained within the Drier Area and transferred to the WPF | No tanker fill point. Fed by closed pipework from the bulk caustic system. Drip capture not applicable. | Visual inspections. Extent of level instrumentation and its control is unknown. | N/A. | Unknown maintenance schedule for the tanks. No bund therefore no bund maintenance. | N/A.
131 | Drier CIP Tank 2 | Nitric acid solution | TBC | Drier | TBC | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation. Control unknown. | Drained within the Drier Area and transferred to the WPF | No tanker fill point. Fed by closed pipework from the bulk nitric acid system. Drip capture not applicable. | Visual inspections. Extent of level instrumentation and its control is unknown. | N/A. | Unknown maintenance schedule for the tanks. No bund therefore no bund maintenance. | N/A.
132 | Buffer Tank 1 | Sweet Whey. Tank no longer in use | 30000 | Evaporation (crystaliser room) | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | The tank is currently not in use and is only in use if there are PH issues in the crystallisation tanks, no overfill protection in place. | Drained within the Crystalisation Room and transferred to the WPF | No tanker fill point. Drip capture not applicable. | Unknown | N/A | Tanks inspected every 12 months, EA inspect valves unless there is a fault and Saputo will fix accordingly. | N/A
133 | Buffer Tank 2 | Sweet Whey. Tank no longer in use | 30000 | Evaporation (crystaliser room) | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | The tank is currently not in use and is only in use if there are PH issues in the crystallisation tanks, no overfill protection in place. | Drained within the Crystalisation Room and transferred to the WPF | No tanker fill point. Drip capture not applicable. | Unknown | N/A | Tanks inspected every 12 months, EA inspect valves unless there is a fault and Saputo will fix accordingly. | N/A
134 | Crystalliser 1 | Concentrated, demineralised whey (57 %) | 30000 | Evaporation (crystaliser room) | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation and alarms to warm of overfilling | Drained within the Crystalisation Room and transferred to the WPF | The tanks are filled via pipework from the Evaporator Room. Drip capture not applicable. | Level monitoring and hourly walk over. Unknown level control. | N/A | Tanks inspected every 12 months, EA inspect valves unless there is a fault and Saputo will fix accordingly. | N/A
135 | Crystalliser 2 | Concentrated, demineralised whey (57 %) | 30000 | Evaporation (crystaliser room) | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation and alarms to warm of overfilling | Drained within the Crystalisation Room and transferred to the WPF | The tanks are filled via pipework from the Evaporator Room. Drip capture not applicable. | Level monitoring and hourly walk over. Unknown level control. | N/A | Tanks inspected every 12 months, EA inspect valves unless there is a fault and Saputo will fix accordingly. | N/A
136 | Crystalliser 3 | Concentrated, demineralised whey (57 %) | 30000 | Evaporation (crystaliser room) | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation and alarms to warm of overfilling | Drained within the Crystalisation Room and transferred to the WPF | The tanks are filled via pipework from the Evaporator Room. Drip capture not applicable. | Level monitoring and hourly walk over. Unknown level control. | N/A | Tanks inspected every 12 months, EA inspect valves unless there is a fault and Saputo will fix accordingly. | N/A
137 | Crystalliser 4 | Concentrated, demineralised whey (57 %) | 30000 | Evaporation (crystaliser room) | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation and alarms to warm of overfilling | Drained within the Crystalisation Room and transferred to the WPF | The tanks are filled via pipework from the Evaporator Room. Drip capture not applicable. | Level monitoring and hourly walk over. Unknown level control. | N/A | Tanks inspected every 12 months, EA inspect valves unless there is a fault and Saputo will fix accordingly. | N/A
138 | Crystalliser 5 | Concentrated, demineralised whey (57 %) | 30000 | Evaporation (crystaliser room) | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation and alarms to warm of overfilling | Drained within the Crystalisation Room and transferred to the WPF | The tanks are filled via pipework from the Evaporator Room. Drip capture not applicable. | Level monitoring and hourly walk over. Unknown level control. | N/A | Tanks inspected every 12 months, EA inspect valves unless there is a fault and Saputo will fix accordingly. | N/A
139 | Crystalliser 6 | Concentrated, demineralised whey (57 %) | 30000 | Evaporation (crystaliser room) | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation and alarms to warm of overfilling | Drained within the Crystalisation Room and transferred to the WPF | The tanks are filled via pipework from the Evaporator Room. Drip capture not applicable. | Level monitoring and hourly walk over. Unknown level control. | N/A | Tanks inspected every 12 months, EA inspect valves unless there is a fault and Saputo will fix accordingly. | N/A
140 | Crystalliser 7 | Concentrated, demineralised whey (57 %) | 30000 | Evaporation (crystaliser room) | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation and alarms to warm of overfilling | Drained within the Crystalisation Room and transferred to the WPF | The tanks are filled via pipework from the Evaporator Room. Drip capture not applicable. | Level monitoring and hourly walk over. Unknown level control. | N/A | Tanks inspected every 12 months, EA inspect valves unless there is a fault and Saputo will fix accordingly. | N/A
141 | Crystalliser 8 | Concentrated, demineralised whey (57 %) | 30000 | Evaporation (crystaliser room) | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation and alarms to warm of overfilling | Drained within the Crystalisation Room and transferred to the WPF | The tanks are filled via pipework from the Evaporator Room. Drip capture not applicable. | Level monitoring and hourly walk over. Unknown level control. | N/A | Tanks inspected every 12 months, EA inspect valves unless there is a fault and Saputo will fix accordingly. | N/A
142 | Feed Tank 1 | demineralised whey 20% | 1000 | Evaporation (crystaliser room) | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation and alarms to warm of overfilling | Drained within the Crystalisation Room and transferred to the WPF | Tank is filled from the crystalisers by pipework. Feed Tank 1 is not in use if Feed Tank 2 is in operation. Drip capture not applicable. | Level monitoring and hourly walk over. Unknown level control. | N/A | Tanks inspected every 12 months, EA inspect valves unless there is a fault and Saputo will fix accordingly. | N/A
143 | Feed Tank 2 | demineralised whey 20% | 1000 | Evaporation (crystaliser room) | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation and alarms to warm of overfilling | Drained within the Crystalisation Room and transferred to the WPF | Tank is filled from the crystalisers by pipework. Feed Tank 2 is not in use if Feed Tank 1 is in operation. Drip capture not applicable. | Level monitoring and hourly walk over. Unknown level control. | N/A | Tanks inspected every 12 months, EA inspect valves unless there is a fault and Saputo will fix accordingly. | N/A
144 | Recovery Tank | Not in Use | 6000 | Evaporation (crystaliser room) | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No longer in use since sweet whey production stopped | Drained within the Crystalisation Room and transferred to the WPF | No longer in use | No longer in use | N/A | Tanks inspected every 12 months, EA inspect valves unless there is a fault and Saputo will fix accordingly. | N/A
145 | Transit | Acids/Alkalis | 25 | Freezer Corridor | Plastic | Transit bund | Yes | Yes | 240 | 0.88m x 1.22m x 0.33m | 960 | Plastic | No | No | Visual | Drained within the Freezer Corridor and transferred to the WPF | NA | Visual inspection. | Not known | Visual | Pumped out
146 | Recovered Water Tank 1 | Water | 30000 | GOS (tank located in Demin high care tank farm) | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC | Drained at the Site Entrance and transferred to the WPF | TBC | TBC | N/A | No bund inspection. Unsure of maintenance schedules for the tanks. | N/A
147 | Recovered Water Tank 2 | Water | 30000 | GOS (tank located in Demin high care tank farm) | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC | Drained at the Site Entrance and transferred to the WPF | TBC | TBC | N/A | No bund inspection. Unsure of maintenance schedules for the tanks. | N/A
148 | Caustic/ Acid Tank | Caustic/acid | 10000 | GOS CIP room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC | Drained within the GOS CIP Room and transferred to the WPF | N/A. Tank filled via closed pipework from main caustic ring main. Drip capture not applicable. | TBC. Assumed level instrumentation and site walk over. | N/A. No tank bund. | Maintenance schedule for the tank TBC. | N/A
149 | Hot water tank 10 | Hot water | 15000 | GOS CIP room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC | Drained within the GOS CIP Room and transferred to the WPF | N/A. Tank filled via closed pipework from main caustic ring main. Drip capture not applicable. | TBC. Assumed level instrumentation and site walk over. | N/A. No tank bund. | Maintenance schedule for the tank TBC. | N/A
150 | Rinse Water Tank | Rinse Water | 15000 | GOS CIP room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC | Drained within the GOS CIP Room and transferred to the WPF | N/A. Tank filled via closed pipework from main caustic ring main. Drip capture not applicable. | TBC. Assumed level instrumentation and site walk over. | N/A. No tank bund. | Maintenance schedule for the tank TBC. | N/A
151 | Evaporator 1 | Powedered whey | TBC | GOS evaporation room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC | Drained within the GOS Evaporation Room and transferred to the WPF | N/A. Fed via pipework from the evaporator buffer tank. Drip capture not applicable. | TBC | N/A | Bund inspection not applicbale. Not sure of evaporator maintenances schedule.N/A | N/A
152 | Evaporator 2 | Powedered whey | TBC | GOS evaporation room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC | Drained within the GOS Evaporation Room and transferred to the WPF | N/A. Fed via pipework from the evaporator buffer tank. Drip capture not applicable. | TBC | N/A | Bund inspection not applicbale. Not sure of evaporator maintenances schedule.N/A | N/A
153 | Evaporator 3 | Powedered whey | TBC | GOS evaporation room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC | Drained within the GOS Evaporation Room and transferred to the WPF | N/A. Fed via pipework from the evaporator buffer tank. Drip capture not applicable. | TBC | N/A | Bund inspection not applicbale. Not sure of evaporator maintenances schedule.N/A | N/A
154 | Evaporator 4 | Powedered whey | TBC | GOS evaporation room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC | Drained within the GOS Evaporation Room and transferred to the WPF | N/A. Fed via pipework from the evaporator buffer tank. Drip capture not applicable. | TBC | N/A | Bund inspection not applicbale. Not sure of evaporator maintenances schedule.N/A | N/A
155 | Evaporator Feed Tank | Retentate from nanofiltration units (25%w/w), cotric acid and product from the cricket filter at 47% (w/w) | TBC | GOS evaporation room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC | Drained within the GOS Evaporation Room and transferred to the WPF | Automatically fed by closed pipework. Drip capture not applicable. | Visual inspection.Unsure of the degree of level monitoring. | N/A | Maintenance schedule TBC. | N/A
156 | EP01- Enzyme (not used) | Tank Empty | 15000 | GOS general care room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A. Not filled, currently empty | Drained within the GOS General Care Room and transferred to the WPF | N/A | N/A | N/A | N/A | N/A
157 | Carbon Filter | Dilluted GOS | TBC | GOS high care | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC | Drained within the GOS High Care Room and transferred to the WPF | N/A. Filled by closed pipework. Drip capture not applicable. | Visual inspection.Unsure of the degree of level monitoring. | N/A | Unknown tank maintenance schedule. Bund maintenance not applicable. | N/A
158 | Carbon Tank 10 | lactose, carbon and water | 10000 | GOS high care | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC | Drained within the GOS High Care Room and transferred to the WPF | N/A. Filled by closed pipework. Drip capture not applicable. | Visual inspection.Unsure of the degree of level monitoring. | N/A | Unknown tank maintenance schedule. Bund maintenance not applicable. | N/A
159 | Carbon Tank 20 | lactose, carbon and water | 10000 | GOS high care | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC | Drained within the GOS High Care Room and transferred to the WPF | N/A. Filled by closed pipework. Drip capture not applicable. | Visual inspection.Unsure of the degree of level monitoring. | N/A | Unknown tank maintenance schedule. Bund maintenance not applicable. | N/A
160 | DT10 Dissolving Tank 1 | Lactose, water and citric acid | 7500 | GOS high care | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC | Drained within the GOS High Care Room and transferred to the WPF | N/A. Filled by closed pipework with citric acid, hot water and lactose. Drip capture not applicable. | Visual inspection.Unsure of the degree of level monitoring. | N/A | Unknown tank maintenance schedule. Bund maintenance not applicable. | N/A
161 | DT10 Disused Tank | Empty | 7500 | GOS high care | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC | Drained within the GOS High Care Room and transferred to the WPF | N/A. Filled by closed pipework. Drip capture not applicable. | Visual inspection.Unsure of the degree of level monitoring. | N/A | Unknown tank maintenance schedule. Bund maintenance not applicable. | N/A
162 | DT20 Dissolving Tank 2 | Lactose, water and citric acid | 7500 | GOS high care | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC | Drained within the GOS High Care Room and transferred to the WPF | N/A. Filled by closed pipework with citric acid, hot water and lactose. Drip capture not applicable. | Visual inspection.Unsure of the degree of level monitoring. | N/A | Unknown tank maintenance schedule. Bund maintenance not applicable. | N/A
163 | EP02- Carbon Addition Mixing Tank | Carbon preparation from carbon filter and mains water and fed from the GOS reaction tank. | 15000 | GOS high care | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC | Drained within the GOS High Care Room and transferred to the WPF | N/A. Filled by closed pipework from carbon preparation area and reaction tank. Drip capture not applicable. | Visual inspection.Unsure of the degree of level monitoring. | N/A | Unknown tank maintenance schedule. Bund maintenance not applicable. | N/A
164 | Evap Buffer Tank 10 | Dilluted GOS | 30000 | GOS high care | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC | Drained within the GOS High Care Room and transferred to the WPF | N/A. Filled by closed pipework. Drip capture not applicable. | Visual inspection.Unsure of the degree of level monitoring. | N/A | Unknown tank maintenance schedule. Bund maintenance not applicable. | N/A
165 | Evap Buffer Tank 20 | Dilluted GOS | 30000 | GOS high care | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC | Drained within the GOS High Care Room and transferred to the WPF | N/A. Filled by closed pipework. Drip capture not applicable. | Visual inspection.Unsure of the degree of level monitoring. | N/A | Unknown tank maintenance schedule. Bund maintenance not applicable. | N/A
166 | GBF Mixing Tank | lactose and water | 1000 | GOS high care | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC | Drained within the GOS High Care Room and transferred to the WPF | N/A. Filled by closed pipework. Drip capture not applicable. | Visual inspection.Unsure of the degree of level monitoring. | N/A | Unknown tank maintenance schedule. Bund maintenance not applicable. | N/A
167 | NF balance tank | Water | 1000 | GOS high care | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC | Drained within the GOS High Care Room and transferred to the WPF | N/A. Filled by closed pipework from the cricket filter. Drip capture not applicable. | Visual inspection.Unsure of the degree of level monitoring. | N/A | Unknown tank maintenance schedule. Bund maintenance not applicable. | N/A
168 | NFT Tank 1 | Dilluted GOS | 15000 | GOS high care | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC | Drained within the GOS High Care Room and transferred to the WPF | N/A. Filled by closed pipework. Drip capture not applicable. | Visual inspection.Unsure of the degree of level monitoring. | N/A | Unknown tank maintenance schedule. Bund maintenance not applicable. | N/A
169 | NFT Tank 2 | Dilluted GOS | 15000 | GOS high care | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC | Drained within the GOS High Care Room and transferred to the WPF | N/A. Filled by closed pipework. Drip capture not applicable. | Visual inspection.Unsure of the degree of level monitoring. | N/A | Unknown tank maintenance schedule. Bund maintenance not applicable. | N/A
170 | Reactor Tank 10 | lactose, enzyme and water | 7500 | GOS high care | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC | Drained within the GOS High Care Room and transferred to the WPF | N/A. Filled by closed pipework. Drip capture not applicable. | Visual inspection.Unsure of the degree of level monitoring. | N/A | Unknown tank maintenance schedule. Bund maintenance not applicable. | N/A
171 | Reactor Tank 20 | lactose, enzyme and water | 7500 | GOS high care | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC | Drained within the GOS High Care Room and transferred to the WPF | N/A. Filled by closed pipework. Drip capture not applicable. | Visual inspection.Unsure of the degree of level monitoring. | N/A | Unknown tank maintenance schedule. Bund maintenance not applicable. | N/A
172 | Reactor Tank 30 | lactose, enzyme and water | 7500 | GOS high care | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC | Drained within the GOS High Care Room and transferred to the WPF | N/A. Filled by closed pipework. Drip capture not applicable. | Visual inspection.Unsure of the degree of level monitoring. | N/A | Unknown tank maintenance schedule. Bund maintenance not applicable. | N/A
173 | Reactor Tank 40 | lactose, enzyme and water | 7500 | GOS high care | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC | Drained within the GOS High Care Room and transferred to the WPF | N/A. Filled by closed pipework. Drip capture not applicable. | Visual inspection.Unsure of the degree of level monitoring. | N/A | Unknown tank maintenance schedule. Bund maintenance not applicable. | N/A
174 | Reactor Tank 50 | lactose, enzyme and water | 7500 | GOS high care | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC | Drained within the GOS High Care Room and transferred to the WPF | N/A. Filled by closed pipework. Drip capture not applicable. | Visual inspection.Unsure of the degree of level monitoring. | N/A | Unknown tank maintenance schedule. Bund maintenance not applicable. | N/A
175 | Reactor Tank 60 | lactose, enzyme and water | 7500 | GOS high care | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC | Drained within the GOS High Care Room and transferred to the WPF | N/A. Filled by closed pipework. Drip capture not applicable. | Visual inspection.Unsure of the degree of level monitoring. | N/A | Unknown tank maintenance schedule. Bund maintenance not applicable. | N/A
176 | RO Buffer Tank | Permeate from the nanofiltration units | 1000 | GOS high care | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC | Drained within the GOS High Care Room and transferred to the WPF | N/A. Filled by closed pipework from the nanofiltration units. Drip capture not applicable. | Visual inspection.Unsure of the degree of level monitoring. | N/A | Unknown tank maintenance schedule. Bund maintenance not applicable. | N/A
177 | Spare tank for DT10 or DT20 | Empty | 7500 | GOS high care | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC | Drained within the GOS High Care Room and transferred to the WPF | N/A. Filled by closed pipework. Drip capture not applicable. | Visual inspection.Unsure of the degree of level monitoring. | N/A | Unknown tank maintenance schedule. Bund maintenance not applicable. | N/A
178 | ST10 | GOS | 30000 | GOS high care | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC | Drained within the GOS High Care Room and transferred to the WPF | N/A. Filled by closed pipework from the evaporators. Drip capture not applicable. | Visual inspection.Unsure of the degree of level monitoring. | N/A | Unknown tank maintenance schedule. Bund maintenance not applicable. | N/A
179 | ST20 | GOS | 30000 | GOS high care | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC | Drained within the GOS High Care Room and transferred to the WPF | N/A. Filled by closed pipework from the evaporators. Drip capture not applicable. | Visual inspection.Unsure of the degree of level monitoring. | N/A | Unknown tank maintenance schedule. Bund maintenance not applicable. | N/A
180 | ST30 | GOS | 30000 | GOS high care (annexe) | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC | Drained within the GOS High Care Room and transferred to the WPF | N/A. Filled by closed pipework from the evaporators. Drip capture not applicable. | Visual inspection.Unsure of the degree of level monitoring. | N/A | Unknown tank maintenance schedule. Bund maintenance not applicable. | N/A
181 | Chiller 1 | Glycol | TBC | Heat Recovery | Steel | Heat Recovery chiller 1 bund | Yes | No | 4368 | 0.14m x 9.75m x 3.2m | #VALUE! | Concrete | Yes | No | Unknown | Drainage via the surface water drainage system | NA | Visual/process detection | Not known | Daily walk overs. Maintenance schedule unknown. | Manual valve to ground, or can be controlled using sump pump or pipe connection to the drain point.
182 | Chiller 2 | Glycol | TBC | Heat Recovery | Steel | Heat Recovery chiller 2 bund | Yes | No | 15319.85 | 11.83m x 0.35m x 3.7m | #VALUE! | Concrete | Yes | No | Unknown | Drainage via the surface water drainage system | NA | Visual/process detection | Not known | Daily walk overs. Maintenance schedule unknown. | Manual valve to ground, or can be controlled using sump pump or pipe connection to the drain point.
183 | Chiller 3 | Glycol | TBC | Heat Recovery | Steel | Heat Recovery chiller 3 bund | Yes | No | 4527.6 | 3.08m x 0.15m x 9.8m | #VALUE! | Concrete | Yes | No | Unknown | Drainage via the surface water drainage system | NA | Visual/process detection | Not known | Daily walk overs. Maintenance schedule unknown. | Manual valve to ground, or can be controlled using sump pump or pipe connection to the drain point. | Bund will overflow into the chemical delivery area, and contained within the bunded area. Unsure if this will be sent straight to drain or contained in an interceptor.
184 | Expansion tank | Glycol | 5355 | Heat Recovery | Steel | Expansion tank bund | Yes | No | 5912.5 | 0.86m x 2.5m x 2.75m | 110.4% | Concrete | Yes | Yes | Overflow and level instrumentation | Drainage via the surface water drainage system | NA | Level monitoring | Not known | Daily walk overs. Maintenance schedule unknown. | Manual valve to ground. Can be pumped out in case of spill.
185 | IBC Glycol 1 | Glycol mpg 25% | 1000 | Heat Recovery | Plastic | Glycol Bund | Yes | Yes | 1150 | 3.32m x 0.43m x 1.21m | 115% | Plastic | No | No | Full IBCs are delivered to site. Empty IBCs are replaced in situ. Visual indication of level. | Drainage via the surface water drainage system | Full IBCs delivered to site. | Visual inspection | Unknown | Daily walk overs. Maintenance schedule unknown. | Sealed bund which will be pumped out
186 | IBC Glycol 2 | Glycol mpg 25% | 1000 | Heat Recovery | Plastic | Glycol Bund | Yes | Yes | 1150 | 3.32m x 0.43m x 1.21m | 115% | Plastic | No | No | Full IBCs are delivered to site. Empty IBCs are replaced in situ. Visual indication of level. | Drainage via the surface water drainage system | Full IBCs delivered to site. | Visual inspection | Unknown | Daily walk overs. Maintenance schedule unknown. | Sealed bund which will be pumped out
187 | IBC Glycol 3 | Glycol mpg 25% | 1000 | Heat Recovery | Plastic | Glycol Bund 2 | Yes | No | 1100 | 1m x 1m x 1.15m | 110% | Plastic | No | No | Full IBCs are delivered to site. Empty IBCs are replaced in situ. Visual indication of level. | Drainage via the surface water drainage system | Full IBCs delivered to site. | Visual inspection | Unknown | Daily walk overs. Maintenance schedule unknown. | Sealed bund which will be pumped out
188 | Tank 73 | Caustic 47% | 30000 | Heat Recovery | Stainless Steel | Heat Recovery bund (self bundled) | Yes | No | Unknown |  |  | Plastic | Yes | No | Unknown | Drainage via the surface water drainage system | Bulk Chemical off loading, drip tray, hosed to WPF drain | Level monitoring | Not known | Daily walk overs. Maintenance schedule unknown. | Emptied by drain valve
189 | Tank 81 | Warm Water | 225000 | Heat Recovery | Stainless Steel | Heat Recovery bund | Yes | Yes (Tank 83) | 164527.6841 | 12.22m x 1.4m x 12.22m | 73.12% | Concrete | Yes | No | Unknown | Drainage via the surface water drainage system | Tank filled internally, no tanker connection point. Drip capture not applicable. | Level monitoring | Not known | Daily walk overs. Maintenance schedule unknown. | Overpump from sump to red drain (WPF) | Site drainage
190 | Tank 82 | Cold Water | 225000 | Heat Recovery | Stainless Steel | Heat Recovery bund | Yes | Yes (With Tank 73) | 183534.3197 | 12.22m x 1.4m x 12.22m | 81.57% | Concrete | Yes | No | Unknown | Drainage via the surface water drainage system | Tank filled internally, no tanker connection point. Drip capture not applicable. | Level monitoring | Not known | Daily walk overs. Maintenance schedule unknown. | Overpump from sump to red drain (WPF) | Site drainage
191 | Tank 83 | Water | 225000 | Heat Recovery | Stainless Steel | Heat Recovery bund | Yes | Yes (With Tank 81 | 164527.6841 | 12.22m x 1.4m x 12.22m | 73.12% | Concrete | Yes | No | Unknown | Drainage via the surface water drainage system | Tank filled internally, no tanker connection point. Drip capture not applicable. | Level monitoring | Not known | Daily walk overs. Maintenance schedule unknown. | Overpump from sump to red drain (WPF) | Site drainage
192 | 374T100 | HCl 32 - 36 % | 30000 | Hydrochloric acid storage tanks | Unknown (Camplas tank). | T374T100 tank bund | Yes | Yes (374T200) | Unknown | Unknown | Unknown | Combination of concrete and brickwork on upper layer. | Unknown | Unknown | Assumed level instrumentation with control to inhibit forward feed. | Drainage via the surface water drainage system | N/A | Visual inspection.Unsure of the degree of level monitoring. | Unknown. | Unknown | Overpumping or removed by tanker
193 | 374T200 | HCl 32 - 36 % | 30000 | Hydrochloric acid storage tanks | Unknown (Camplas tank). | T374T200 tank bund | Yes | Yes (374T100) | Unknown | Unknown | Unknown | Combination of concrete and brickwork on upper layer. | Unknown | Unknown | Assumed level instrumentation with control to inhibit forward feed. | Drainage via the surface water drainage system | N/A | Visual inspection.Unsure of the degree of level monitoring. | Unknown. | Unknown | Overpumping or removed by tanker
194 | Empty IBCs | Empty | 1000 per IBC | Milk delivery slab | Plastic | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Drainage via the surface water drainage system | IBCs are filled off-site and delivered full. IBCs not reused. | Visual inspection | N/A | Daily walk overs. Maintenance schedule unknown. | N/A
195 | Milk delivery slab | Milk | NA | Milk delivery slab | Concrete slab | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Drainage via the surface water drainage system | Tanker connection point outside and transfers across to the milk storage tanks. Drips captured locally and collected by drainage. | N/A. No tank storage. Any leak in the milk delivery tankers would be identified by visual inspection. | N/A | Daily walk overs. Maintenance schedule unknown. | N/A
196 | Pripan 25 l drum | Pripan | 25 | Milk delivery slab | Plastic | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Drainage via the surface water drainage system | N/A. Full container delivered to site and replaced in situ when empty. | Visual inspection | N/A | Daily walk overs. Maintenance schedule unknown. | N/A
197 | Triquart AM 25 l drum | Triquart AM | 25 | Milk delivery slab | Plastic | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Drainage via the surface water drainage system | N/A. Full container delivered to site and replaced in situ when empty. | Visual inspection | N/A | Daily walk overs. Maintenance schedule unknown. | N/A
198 | Silo 11 | Milk | 346000 | Milk Silos | Stainless Steel | MS Bund 1 | Yes | Milk Silo 12, Milk Silo 13, Milk Silo 14, Skimmed Milk Silo 21, Skimmed Milk Silo 22. | 13103.9085 | 31.39m x 5.39m x 0.2m | 3.787% | Concrete | Yes | N | TBC | Drainage via the surface water drainage system | Tanks are fill point is in the milk reception across the road. Filling is monitored by the delivery drivers. Any drips are contained within local drainage for discharge to the WPF. | Visual inspections. Low level alarm. | Unknown. | Daily walk overs. Maintenance schedule unknown. | Drained by removing the plug or overpump from sump by a contractor.
199 | Silo 12 | Milk | 346000 | Milk Silos | Stainless Steel | MS Bund 1 | Yes | Milk Silo 11, Milk Silo 13, Milk Silo 14, Skimmed Milk Silo 21, Skimmed Milk Silo 22. | 13103.9085 | 31.39m x 5.39m x 0.2m | 3.787% | Concrete | Yes | N | TBC | Drainage via the surface water drainage system | Tanks are fill point is in the milk reception across the road. Filling is monitored by the delivery drivers. Any drips are contained within local drainage for discharge to the WPF. | Visual inspections. Low level alarm. | Unknown. | Daily walk overs. Maintenance schedule unknown. | Drain with plug or overpump from sump
200 | Silo 13 | Milk | 346000 | Milk Silos | Stainless Steel | MS Bund 1 | Yes | Milk Silo 11, Milk Silo 12, Milk Silo 14, Skimmed Milk Silo 21, Skimmed Milk Silo 22. | 13103.9085 | 31.39m x 5.39m x 0.2m | 3.787% | Concrete | Yes | N | TBC | Drainage via the surface water drainage system | Tanks are fill point is in the milk reception across the road. Filling is monitored by the delivery drivers. Any drips are contained within local drainage for discharge to the WPF. | Visual inspections. Low level alarm. | Unknown. | Daily walk overs. Maintenance schedule unknown. | Drain with plug or overpump from sump
201 | Silo 14 | Milk | 346000 | Milk Silos | Stainless Steel | MS Bund 1 | Yes | Milk Silo 11, Milk Silo 12, Milk Silo 13, Skimmed Milk Silo 21, Skimmed Milk Silo 22. | 13103.9085 | 31.39m x 5.39m x 0.2m | 3.787% | Concrete | Yes | N | TBC | Drainage via the surface water drainage system | Tanks are fill point is in the milk reception across the road. Filling is monitored by the delivery drivers. Any drips are contained within local drainage for discharge to the WPF. | Visual inspections. Low level alarm. | Unknown. | Daily walk overs. Maintenance schedule unknown. | Drain with plug or overpump from sump to WPF (dependent on testing)
202 | Silo 15 | Milk | 346000 | Milk Silos | Stainless Steel | MS Bund 2 | Yes | Milk Silo 16, Milk Silo 17, Milk Silo 18, Cream Tank 25, Cream Tank 26. | 17379.0275 | 32.4m x 6m x 0.15m | 5.023% | Concrete | Yes | N | TBC | Drainage via the surface water drainage system | Tanks are fill point is in the milk reception across the road. Filling is monitored by the delivery drivers. Any drips are contained within local drainage for discharge to the WPF. | Visual inspections. Low level alarm. | Unknown. | Daily walk overs. Maintenance schedule unknown. | Rainwater is removed by a permanantly installed sump pump by manual start to blue drain system. Milk in the bund can be emptied by temporary sump pump for controlled removal.
203 | Silo 16 | Milk | 346000 | Milk Silos | Stainless Steel | MS Bund 2 | Yes | Milk Silo 15, Milk Silo 17, Milk Silo 18, Cream Tank 25, Cream Tank 26. | 17379.0275 | 32.4m x 6m x 0.15m | 5.023% | Concrete | Yes | N | TBC | Drainage via the surface water drainage system | Tanks are fill point is in the milk reception across the road. Filling is monitored by the delivery drivers. Any drips are contained within local drainage for discharge to the WPF. | Visual inspections. Low level alarm. | Unknown. | Daily walk overs. Maintenance schedule unknown. | Rainwater is removed by a permanantly installed sump pump by manual start to blue drain system. Milk in the bund can be emptied by temporary sump pump for controlled removal.
204 | Silo 17 | Milk | 346000 | Milk Silos | Stainless Steel | MS Bund 2 | Yes | Milk Silo 15, Milk Silo 16, Milk Silo 18, Cream Tank 25, Cream Tank 26. | 17379.0275 | 32.4m x 6m x 0.15m | 5.023% | Concrete | Yes | N | TBC | Drainage via the surface water drainage system | Tanks are fill point is in the milk reception across the road. Filling is monitored by the delivery drivers. Any drips are contained within local drainage for discharge to the WPF. | Visual inspections. Low level alarm. | Unknown. | Daily walk overs. Maintenance schedule unknown. | Rainwater is removed by a permanantly installed sump pump by manual start to blue drain system. Milk in the bund can be emptied by temporary sump pump for controlled removal.
205 | Silo18 | Milk | 346000 | Milk Silos | Stainless Steel | MS Bund 2 | Yes | Milk Silo 15, Milk Silo 16, Milk Silo 17, Cream Tank 25, Cream Tank 26. | 17379.0275 | 32.4m x 6m x 0.15m | 5.023% | Concrete | Yes | N | TBC | Drainage via the surface water drainage system | Tanks are fill point is in the milk reception across the road. Filling is monitored by the delivery drivers. Any drips are contained within local drainage for discharge to the WPF. | Visual inspections. Low level alarm. | Unknown. | Daily walk overs. Maintenance schedule unknown. | Rainwater is removed by a permanantly installed sump pump by manual start to blue drain system. Milk in the bund can be emptied by temporary sump pump for controlled removal.
206 | Tank 25 | Cream | Redundant | Milk Silos Area | Stainless Steel | MS Bund 2 | Yes | Milk Silo 15, Milk Silo 16, Milk Silo 17, Milk Silo 18, Cream Tank 26. | 17379.0275 | 32.4m x 6m x 0.15m | N/A | Concrete | Yes | N | TBC | Drainage via the surface water drainage system | Tanks are fill point is in the milk reception across the road. Filling is monitored by the delivery drivers. Any drips are contained within local drainage for discharge to the WPF. | Visual inspections. Low level alarm. | Unknown. | Daily walk overs. Maintenance schedule unknown. | Rainwater is removed by a permanantly installed sump pump by manual start to blue drain system. Milk in the bund can be emptied by temporary sump pump for controlled removal.
207 | Tank 26 | Cream | Redundant | Milk Silos Area | Stainless Steel | MS Bund 2 | Yes | Milk Silo 15, Milk Silo 16, Milk Silo 17, Milk Silo 18, Cream Tank 25. | 17379.0275 | 32.4m x 6m x 0.15m | N/A | Concrete | Yes | N | TBC | Drainage via the surface water drainage system | Tanks are fill point is in the milk reception across the road. Filling is monitored by the delivery drivers. Any drips are contained within local drainage for discharge to the WPF. | Visual inspections. Low level alarm. | Unknown. | Daily walk overs. Maintenance schedule unknown. | Rainwater is removed by a permanantly installed sump pump by manual start to blue drain system. Milk in the bund can be emptied by temporary sump pump for controlled removal.
208 | Tank 27 | Cream | 60000 | Milk Silos Area | Stainless Steel | MS Bund 3 connects to milk silo corridor. | Yes | Yes. Tank 28 | 4312.247 | 4.33m x 4.33m x 0.23m | 7.187% | Concrete | Yes | N | TBC | Drainage via the surface water drainage system | Filled from Separation house by closed pipework. Drip capture not applicable. | Visual inspections. Low level alarm. | Unknown. | Daily walk overs. Maintenance schedule unknown. | Drain with plug or overpump from sump to WPF (dependent on testing)
209 | Tank 28 | Cream | 60000 | Milk Silos Area | Stainless Steel | MS Bund 3 connects to milk silo corridor. | Yes | Yes. Tank 27. | 4312.247 | 4.33m x 4.33m x 0.23m | 7.187% | Concrete | Yes | N | TBC | Drainage via the surface water drainage system | Filled from Separation house by closed pipework. Drip capture not applicable. | Visual inspections. Low level alarm. | Unknown. | Daily walk overs. Maintenance schedule unknown. | Drain with plug or overpump from sump to WPF (dependent on testing)
210 | Polix Chlorant 25 l drum Milk Silo Corridor | Polix Chlorant | 25 | Milk Silos Corridor | Plastic | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A. | Drainage via the surface water drainage system | N/A. Plastic containers filled off site and delivered as full containers. Empty containers are replaced in situ. | Visual inspection.Unsure of the degree of level monitoring. | N/A | N/A | N/A
211 | Tank 24 | Cream Buffer Tank | 23000 | Milk Silos Corridor | Stainless Steel | CBT bund | Yes | No | 3335.92 | 3.92m x 3.7m x 0.23m | 14.5% | Concrete | Yes | No | High level instrumentation. Extent of control unknown | Drainage via the surface water drainage system | N/A. Tank fed via pipework. Drip capture not applicable. | Visual inspection.Unsure of the degree of level monitoring. | Unknown | Daily walk overs. Maintenance schedule unknown. | Rain water can be emptied form the bund by removing the drain plug. Contents can also be pumped out using a sump pump.
212 | Triquart 25 l drum Milk Silo Corridor | Triquart | 25 | Milk Silos Corridor | Plastic | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A. | Drainage via the surface water drainage system | N/A. Full plastic container delivered to site. Empty container replaced in situ. | Visual inspection.Unsure of the degree of level monitoring. | N/A | N/A | N/A
213 | Waste Oil Tank | Waste oil | Unknown | Oil and Chemical Store | Plastic | Waste oil bund | Yes | No | 1498.464 |  | #VALUE! | Concrete block | No | No | Level gauge | Contained within the Oil and Chemical Store local drainage and transferred to the WPF | Within tank bund. Waste oil physically poured into the tank via large opening. | Visual inspection.Unsure of the degree of level monitoring. | Unknown | Unknown. | Overpumping or removed by tanker
214 | Cream buffer tank (Tank 24) | Cream | 20000 | Outside of powder mixing room | Stainless Steel | Cream buffer tank (Tank 24) bund | Yes | No | 4641.28 | 3.92m x 3.7m x 0.32m | 23.21% | Concrete | Yes | No | Unknown. | Drainage via the surface water drainage system | Filled from the Separation House via internal pipework, no drip capture not applicable. | Visual inspection. Level monitoring and alarms to identify when the silo is not filling or emptying. Extent of control unknown | Unknown | Environmental Walk Days/ Night Shifts. Details of the maintenance schedule unknown. | Drain with plug or overpump from sump to WPF (dependent on contents).
215 | Hot water tank | Hot water | TBC | Pasteurising Room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation monitored from the control room | Drained within the Pasteurising Room and transferred to the WPF | Unknown. System not online. | Visual inspection and trended level indication. | N/A | Unknown tank maintenance schedule. Bund maintenance not applicable. | N/A
216 | Polix Chlorate 25 l drum | Polix Chlorate | 25 | Pasteurising Room | Plastic | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | None | Drained within the Pasteurising Room and transferred to the WPF | N/A. Full plastic containers are delivered to site. Empty containers replaced in situ. | None | N/A | Environmental Walk Days/ Night Shifts. Details of the maintenance schedule unknown. | N/A
217 | Pripan 25 l drum 2 | Pripan | 25 | Pasteurising Room | Plastic | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | None | Drained within the Pasteurising Room and transferred to the WPF | N/A. Full plastic containers are delivered to site. Empty containers replaced in situ. | None | N/A | Environmental Walk Days/ Night Shifts. Details of the maintenance schedule unknown. | N/A
218 | Tank 30 Retentate Tank | Milk protein at 11% + milk solids | 10000 | Pasteurising Room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Routine checks and level instrumentation that can be monitored from the control room. Overflow pipework will flow to WPF. | Drained within the Pasteurising Room and transferred to the WPF | Filled from UF/Silo corrdior | Visual inspection. Low level instrumentation. | n/a | Environmental Walk Days/ Night Shifts. Details of the maintenance schedule unknown. | N/A
219 | Topaz MDI 25 l drum | Topaz MDI | 25 | Pasteurising Room | Plastic | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | None | Drained within the Pasteurising Room and transferred to the WPF | None. Full containers delivered to siteand empty containers are replaced in situ. | Visual inspection only. | Na | Environmental Walk Days/ Night Shifts. Details of the maintenance schedule unknown. | N/A
220 | Triquart 25 l drum | Triquart | 25 | Pasteurising Room | Plastic | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | None | Drained within the Pasteurising Room and transferred to the WPF | None. Full containers delivered to siteand empty containers are replaced in situ. | Visual inspection only. | Na | Environmental Walk Days/ Night Shifts. Details of the maintenance schedule unknown. | N/A
221 | Powder Silo 1 | Whey Powder | 30000 | Powder Bagging Area | Stainless Steel | N/A | No - solid | N/A | N/A | N/A | N/A | N/A | N/A | N/A | None identified. | No liquid should be present. If there is, it will be drained within the Powder Bagging Area and transferred to the WPF | Tank filled via internal pipework, drip capture not applicable. | Visual inspection every 3 hours. Unsure of the extent of level monitoring | N/A | 12 monthly inspections of the tanks. If there are any detected issues, this will be replaced by Saputo. | NA
222 | Powder Silo 2 | Powder | 30000 | Powder Bagging Area | Stainless Steel | N/A | No - solid | N/A | N/A | N/A | N/A | N/A | N/A | N/A | None identified. | No liquid should be present. If there is, it will be drained within the Powder Bagging Area and transferred to the WPF | Tank filled via internal pipework, drip capture not applicable. | Visual inspection every 3 hours. Unsure of the extent of level monitoring | N/A | 12 monthly inspections of the tanks. If there are any detected issues, this will be replaced by Saputo. | NA
223 | Powder Silo 3 | Powder | 30000 | Powder Bagging Area | Stainless Steel | N/A | No - solid | N/A | N/A | N/A | N/A | N/A | N/A | N/A | None identified. | No liquid should be present. If there is, it will be drained within the Powder Bagging Area and transferred to the WPF | Tank filled via internal pipework, drip capture not applicable. | Visual inspection every 3 hours. Unsure of the extent of level monitoring | N/A | 12 monthly inspections of the tanks. If there are any detected issues, this will be replaced by Saputo. | NA
224 | Powder Silo 4 | Powder | 20000 | Powder Bagging Area | Stainless Steel | N/A | No - solid | N/A | N/A | N/A | N/A | N/A | N/A | N/A | None identified. | No liquid should be present. If there is, it will be drained within the Powder Bagging Area and transferred to the WPF | Tank filled via internal pipework, drip capture not applicable. | Visual inspection every 3 hours. Unsure of the extent of level monitoring | N/A | 12 monthly inspections of the tanks. If there are any detected issues, this will be replaced by Saputo. | NA
225 | Tank 21 | Skimmed milk | TBC | Skimmed Milk Silos | Stainless Steel | Skimmed milk silo bund | Yes | Milk Silo 12, Milk Silo 13, Milk Silo 14, Milk Silo 15, Skimmed Milk Silo 22. | 13103.9085 | 31.39m x 5.39m x 0.2m | #VALUE! | Concrete | Yes | No | TBC | Drainage via the surface water drain and transferred to the WPF | Milk Reception - control and drains to WPF | Visual inspection and 'silo empty' alarm. | Not known other than on rainfall and control | Environmental Walk Days/ Night Shifts | Rainwater removed by permanently installed sump pump. Bund can be emptied by overpumping in case of milk spill.
226 | Tank 22 | Skimmed milk | TBC | Skimmed Milk Silos | Stainless Steel | Skimmed milk silo bund | Yes | Milk Silo 12, Milk Silo 13, Milk Silo 14, Milk Silo 15, Skimmed Milk Silo 21. | 13103.9085 | 31.39m x 5.39m x 0.2m | #VALUE! | Concrete | Yes | No | TBC | Drainage via the surface water drain and transferred to the WPF | Milk Reception - control and drains to WPF | Visual inspection and 'silo empty' alarm. | Not known other than on rainfall and control | Environmental Walk Days/ Night Shifts | Rainwater removed by permanently installed sump pump. Bund can be emptied by overpumping in case of milk spill.
227 | Steam Accumulator | Steam | TBC | Steam Accumulator Room | TBC (Believed to be an insulated steel tank) | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Unknown | Unsure. Presumably site drainage. | Steam from boilers transferred to this tank for storage. | Unknown | Unknown | N/A | N/A
228 | Aquatreat 179SE Tank | Aquatreat 179SE (Potassium Hydroxide) | 500 | Water Treatment Plant for Boilers | Plastic | Aquatreat 179SE Bund | Yes | No | 1183.9877 | 1.5m diameter x 0.67m. Tapered shape do volume is slightly smaller than stated. | 236.8% | Plastic | No | No | Visual only. | Sump in centre of the room which is then manually pumed out to site drainage. | Connection point for filling located within tank bund (in centre of bund) which should contain any spills. | None observed. | Unknown | Unknown | Bund emptied using a pump. Pump not permanently installed.
229 | Aquatreat 216 Tank | Aquatreat 216 | 500 | Water Treatment Plant for Boilers | Plastic | Aquatreat 216 bund | Yes | No | 1183.9877 | 1.5m diameter x 0.67m. Tapered shape do volume is slightly smaller than stated. | 236.8% | Plastic | No | No | Visual only. | Sump in centre of the room which is then manually pumed out to site drainage. | Connection point for filling located within tank bund (in centre of bund) which should contain any spills. | None observed. | Unknown | Unknown | Bund emptied using a pump. Pump not permanently installed.
230 | Aquatreat a32 Tank | Aquatreat a32 | 500 | Water Treatment Plant for Boilers | Plastic | Aquatreat A32 Bund | Yes | No | 1183.9877 | 1.5m diameter x 0.67m. Tapered shape do volume is slightly smaller than stated. | 236.8% | Plastic | No | No | Visual only. | Sump in centre of the room which is then manually pumed out to site drainage. | Connection point for filling located within tank bund (in centre of bund) which should contain any spills. | None observed. | Unknown | Unknown | Bund emptied using a pump. Pump not permanently installed.
231 | Boiler Water Softener 1 | Resin | TBC | Water Treatment Plant for Boilers | Stainless Steel | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | None | Floor slopes towards a low point in the room. Sump pump and flexible hose used to transfer contents to site drainage. | N/A | Visual inspection.Unsure of the degree of level monitoring. | N/A | Bund inspection N/A. Maintenance schedule of tanks TBC. | N/A
232 | Boiler Water Softener 2 | Resin | TBC | Water Treatment Plant for Boilers | Stainless Steel | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | None | Floor slopes towards a low point in the room. Sump pump and flexible hose used to transfer contents to site drainage. | N/A | Visual inspection.Unsure of the degree of level monitoring. | N/A | Bund inspection N/A. Maintenance schedule of tanks TBC. | N/A
233 | Boiler Water Softener 3 | Resin | TBC | Water Treatment Plant for Boilers | Stainless Steel | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | None | Floor slopes towards a low point in the room. Sump pump and flexible hose used to transfer contents to site drainage. | N/A | Visual inspection.Unsure of the degree of level monitoring. | N/A | Bund inspection N/A. Maintenance schedule of tanks TBC. | N/A
234 | Boiler Water Softener 4 | Resin | TBC | Water Treatment Plant for Boilers | Stainless Steel | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | None | Floor slopes towards a low point in the room. Sump pump and flexible hose used to transfer contents to site drainage. | N/A | Visual inspection.Unsure of the degree of level monitoring. | N/A | Bund inspection N/A. Maintenance schedule of tanks TBC. | N/A
235 | Brine Tank | Brine | 731.5984 | Water Treatment Plant for Boilers | Plastic | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | None | Floor slopes towards a low point in the room. Sump pump and flexible hose used to transfer contents to site drainage. | N/A | Visual inspection.Unsure of the degree of level monitoring. | N/A | Bund inspection N/A. Maintenance schedule of tanks TBC. | N/A
236 | Tank 11-201 | Water | TBC | Whey Cip | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Unknown | Drained within Whey CIP and transferred to the WPF | Unknown | Unknown | N/A | Bund inspection N/A. Maintenance schedule of tanks TBC. | N/A
237 | Tank 11-202 | Circulation Water | TBC | Whey Cip | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Unknown | Drained within Whey CIP and transferred to the WPF | Unknown | Unknown | N/A | Bund inspection N/A. Maintenance schedule of tanks TBC. | N/A
238 | Tank 11-203 | Nitric acid 0.9 - 1..1 % | TBC | Whey Cip | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Unknown | Drained within Whey CIP and transferred to the WPF | Unknown | Unknown | N/A | Bund inspection N/A. Maintenance schedule of tanks TBC. | N/A
239 | Tank 11-204 | Caustic 1.1 - 1.5 % | TBC | Whey Cip | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Unknown | Drained within Whey CIP and transferred to the WPF | Unknown | Unknown | N/A | Bund inspection N/A. Maintenance schedule of tanks TBC. | N/A
240 | Tank 11-205 | Bag filter CIP (used 1ce per year) | TBC | Whey Cip | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Unknown | Drained within Whey CIP and transferred to the WPF | Unknown | Unknown | N/A | Bund inspection N/A. Maintenance schedule of tanks TBC. | N/A
241 | Tank 941 | Circulation Water Tank | 8000 | Whey Cip 4 | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Visual inspection. Level instrumentation. Unsure of control | Drained within Whey CIP 4 and transferred to the WPF | No tanker fill point. Fed by a pipework system. Drip capture not applicable. | Level monitoring and visual inspection. Extent of control unknown. | N/A | No bund inspection. Unsure of maintenance schedules for the tanks. | N/A
242 | Tank 942 | Rinse Water | 12000 | Whey Cip 4 | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Visual inspection. Level instrumentation. Unsure of control | Drained within Whey CIP 4 and transferred to the WPF | No tanker fill point. Fed by a pipework system. Drip capture not applicable. | Level monitoring and visual inspection. Extent of control unknown. | N/A | No bund inspection. Unsure of maintenance schedules for the tanks. | N/A
243 | Tank 943 | Nitric Acid 0.9% – 1.1% | 12000 | Whey Cip 4 | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Visual inspection. Level instrumentation. Unsure of control | Drained within Whey CIP 4 and transferred to the WPF | No tanker fill point. Fed from nitric acid system. Drip capture not applicable. | Level monitoring and visual inspection. Extent of control unknown. | N/A | No bund inspection. Unsure of maintenance schedules for the tanks. | N/A
244 | Tank 944 | Caustic 1.1 - 1.5 % | 12000 | Whey Cip 4 | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Visual inspection. Level instrumentation. Unsure of control | Drained within Whey CIP 4 and transferred to the WPF | No tanker fill point. Fed from caustic acid system. Drip capture not applicable. | Level monitoring and visual inspection. Extent of control unknown. | N/A | No bund inspection. Unsure of maintenance schedules for the tanks. | N/A
245 | Potable Water tank 1 GOS Gos | Potable water for GOS | 72000 | Whey outside | GRP | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Visual inspection. Level instrumentation. Unsure of control | Drained via the surface water drainage system | Filled via internal pipework, drip capture not applicable | Level monitoring and visual inspection. Extent of control unknown. | N/A | Environmental Walk Days/ Night Shifts. Maintenance schedule of the tanks unknown. | N/A
246 | Potable Water Tank 1 Tank | Potable water supply from South West Water | TBC | Whey outside | GRP | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Visual inspection. Level instrumentation. Unsure of control | Drained via the surface water drainage system | Filled via internal pipework, drip capture not applicable | Level monitoring and visual inspection. Extent of control unknown. | N/A | Environmental Walk Days/ Night Shifts. Maintenance schedule of the tanks unknown. | N/A
247 | Potable Water tank 2 GOS Gos | Potable water for GOS | 72000 | Whey outside | GRP | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Visual inspection. Level instrumentation. Unsure of control | Drained via the surface water drainage system | Filled via internal pipework, drip capture not applicable | Level monitoring and visual inspection. Extent of control unknown. | N/A | Environmental Walk Days/ Night Shifts. Maintenance schedule of the tanks unknown. | N/A
248 | Potable Water Tank 2 Tank | Potable water supply from South West Water | TBC | Whey outside | GRP | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Visual inspection. Level instrumentation. Unsure of control | Drained via the surface water drainage system | Filled via internal pipework, drip capture not applicable | Level monitoring and visual inspection. Extent of control unknown. | N/A | Environmental Walk Days/ Night Shifts. Maintenance schedule of the tanks unknown. | N/A
249 | Process Water Tank 1 Tank | Process Water Tank 1 | 760000 | Whey outside | GRP | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC | Drained via the surface water drainage system | TBC | TBC | TBC | TBC | N/A
250 | Process Water Tank 2 Tank | Process Water Tank 2 | 760000 | Whey outside | GRP | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC | Drained via the surface water drainage system | TBC | TBC | TBC | TBC | N/A
251 | Tank 494 Separated Whey Storage | Separated Whey | 225000 | Whey Separation house | Stainless Steel | Separated Whey bund | Yes | Tank 495 | 8453.6729 | 11.4m x 4.3m x 0.25m | 3.757% | Concrete | Yes | No | Visual inspection. Level instrumentation. Unsure of control | Drained within Whey Separation house and transferred to the WPF | N/A. Tank fed by pipework. Drip capture not applicable. | Level monitoring and visual inspection. Extent of control unknown. | Unknown | Unknown maintenance schedule for both bund and tank. | Rain water can be emptied via the permanently installed sump pump. In case of spill of whey, can overpump from sump to red drain (WPF).
252 | Tank 495 Separated Whey Storage | Separated Whey | 225000 | Whey Separation house | Stainless Steel | Separated Whey bund | Yes | Tank 494 | 8453.6729 | 11.4m x 4.3m x 0.25m | 3.757% | Concrete | Yes | No | Visual inspection. Level instrumentation. Unsure of control | Drained within Whey Separation house and transferred to the WPF | N/A. Tank fed by pipework. Drip capture not applicable. | Level monitoring and visual inspection. Extent of control unknown. | Unknown | Unknown maintenance schedule for both bund and tank. | Rain water can be emptied via the permanently installed sump pump. In case of spill of whey, can overpump from sump to red drain (WPF).
253 | Tank 496 Separated Whey Storage | Separated Whey | 225000 | Whey Separation house | Stainless Steel | Separated Whey bund2 | Yes | Tank 499 | 8453.6729 | 11.4m x 4.3m x 0.25m | 3.757% | Concrete | Yes | No | Visual inspection. Level instrumentation. Unsure of control | Drained within Whey Separation house and transferred to the WPF | N/A. Tank fed by pipework. Drip capture not applicable. | Level monitoring and visual inspection. Extent of control unknown. | Unknown | Unknown maintenance schedule for both bund and tank. | Rain water can be emptied via the permanently installed sump pump. In case of spill of whey, can overpump from sump to red drain (WPF).
254 | Tank 499 Separated Whey Storage | Separated Whey | 136000 | Whey Separation house | Stainless Steel | Separated Whey bund2 | Yes | Tank 496 | 8453.6729 | 11.4m x 4.3m x 0.25m | 6.216% | Concrete | Yes | No | Visual inspection. Level instrumentation. Unsure of control | Drained within Whey Separation house and transferred to the WPF | N/A. Tank fed by pipework. Drip capture not applicable. | Level monitoring and visual inspection. Extent of control unknown. | Unknown | Unknown maintenance schedule for both bund and tank. | Rain water can be emptied via the permanently installed sump pump. In case of spill of whey, can overpump from sump to red drain (WPF).
255 | Tank 414 | Pasteurised whey cream storage | 15000 | Whey Separation room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Visual inspection. Level instrumentation. Unsure of control | Drained within Whey Separation room and transferred to the WPF | N/A. Tank fed by pipework. Drip capture not applicable. | Level monitoring and visual inspection. Extent of control unknown. | N/A | Unknown maintenance schedule. Bund maintenance not applicable. | N/A.
256 | Tank 415 | Pasteurised whey cream storage | 15000 | Whey Separation room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Visual inspection. Level instrumentation. Unsure of control | Drained within Whey Separation room and transferred to the WPF | N/A. Tank fed by pipework. Drip capture not applicable. | Level monitoring and visual inspection. Extent of control unknown. | N/A | Unknown maintenance schedule. Bund maintenance not applicable. | N/A.
257 | Tank 420 | Unpasteurised whey cream | 6000 | Whey Separation room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Visual inspection. Level instrumentation. Unsure of control | Drained within Whey Separation room and transferred to the WPF | N/A. Tank fed by pipework. Drip capture not applicable. | Level monitoring and visual inspection. Extent of control unknown. | N/A | Unknown maintenance schedule. Bund maintenance not applicable. | N/A.
258 | Tank 420A Whey cream buffer tank | Whey cream | 1000 | Whey Separation room | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Visual inspection. Level instrumentation. Unsure of control | Drained within Whey Separation room and transferred to the WPF | N/A. Tank fed by pipework. Drip capture not applicable. | Level monitoring and visual inspection. Extent of control unknown. | N/A | Unknown maintenance schedule. Bund maintenance not applicable. | N/A.
259 | Whey separation tank 1 Tank | Whey separation tank 1 | TBC | Whey Separation room | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC | Drained within Whey Separation room and transferred to the WPF | TBC | TBC | TBC | TBC | TBC
260 | Whey Separation tank 2 Tank | Whey Separation tank 2 | TBC | Whey Separation room | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC | Drained within Whey Separation room and transferred to the WPF | TBC | TBC | TBC | TBC | TBC
261 | Polished Water Tank | Polished Water | 135000 | Whey Separation silo corridor | Stainless Steel | N/A | No - Process Drains to WPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC | Drainage via the surface water drain and transferred to the WPF | TBC | TBC | N/A | Tank maintenance schedule unknown. Bund maintenance not applicable. | N/A
262 | Tank 411 | Unseparated Whey | 135000 | Whey Separation silo corridor | Stainless Steel | Whey separation silo bund | Yes | Yes - Tank 412 and 497 | 3638 | Approximately 10m x 5m x 0.2m | 2.695% | Concrete | No | No | TBC | Drainage via the surface water drainage system | TBC | TBC | TBC | TBC | Overpump from sump to red drain system (WPF)
263 | Tank 412 | Unseparated Whey | 135000 | Whey Separation silo corridor | Stainless Steel | Whey separation silo bund | Yes | Yes - Tank 411 and 497 | 3638 | Approximately 10m x 5m x 0.2m | 2.695% | Concrete | No | No | TBC | Drainage via the surface water drainage system | TBC | TBC | TBC | TBC | Overpump from sump to red drain system (WPF)
264 | Tank 413 | Unseparated Salt Whey | 135000 | Whey Separation silo corridor | Stainless Steel | Whey separation silo bund | Yes | No | 6000 |  | 4.444% | Concrete | Yes | No | Level instrumentation | Drainage via the surface water drainage system | Whey separation process system | Level monitoring | Unknown | Environmental wal around | Overpump from sump to red drain system (WPF)
265 | Tank 416 | Permeate | 50000 | Whey Separation silo corridor | Stainless Steel | Tank 417, Tank 418 | Yes | Yes. Tank 417 and Tank 418 | 3994.1379 |  | 7.988% | Concrete | No | No | Level instrumentation | Drainage via the surface water drainage system | Whey separation process system | Level monitoring | Unknown | External walk. Unsure of maintenance schedule for tanks and bund. | Overpump from sump to red drain system (WPF)
266 | Tank 417 | Permeate | 50000 | Whey Separation silo corridor | Stainless Steel | Tank 416, Tank 418 | Yes | Yes. Tank 416 and Tank 418 | 3994.1379 |  | 7.988% | Concrete | No | No | Level instrumentation | Drainage via the surface water drainage system | Whey separation process system | Level monitoring | Unknown | External walk. Unsure of maintenance schedule for tanks and bund. | Overpump from sump to red drain system (WPF) | Rarely used
267 | Tank 418 | Salt Whey | 50000 | Whey Separation silo corridor | Stainless Steel | Tank 416, Tank 417 | Yes | Yes. Tank 416 and Tank 417 | 3994.1379 |  | 7.988% | Concrete | No | No | Level instrumentation | Drainage via the surface water drainage system | Whey separation process system | Level monitoring | Unknown | External walk. Unsure of maintenance schedule for tanks and bund. | Overpump from sump to red drain system (WPF)
268 | Tank 497 | GOS Permeate (empty, clean, irreparable) | 110000 | Whey Separation silo corridor | Stainless Steel |  | Yes | Yes - Shared with 412 and 411 | 3638 |  | 3.307% | Concrete | No | No | TBC | Drainage via the surface water drainage system | TBC | TBC | TBC | TBC | Overpump from sump to red drain system (WPF)
269 | Process water tank | Recovered water (RO), abstracted water, towns potable | TBC | Whey Silo area | GRP | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC | Drained at the Site Entrance and transferred to the WPF | Fed from pipework from other tanks or water supplies. No tanker connection point. | TBC | N/A | Bund inspections not applicable. Unknown tank inspectino schedule | N/A. No tank bund.
270 | Process Water Tank 2 | Recovered water (RO), abstracted water, towns potable | TBC | Whey Silo area | GRP | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC | Drained at the Site Entrance and transferred to the WPF | Fed from pipework from other tanks or water supplies. No tanker connection point. | TBC | N/A | Bund inspections not applicable. Unknown tank inspectino schedule | N/A. No tank bund.
WATER PROCESSING FACILITY (WPF) |  |  |  |  | No No: Please see comments in Column X | [6 empty] | The WPF is served by a tertiary containment concrete wall of sectional sealed construction to the down gradient bondaries north, east and south of the WPF. The WPF containment wall is sized to contain the inventory of the largest WPF tank (AT2). The containment wall is buried to impermeable ground level minimising shallow groundwater movement. Ground water collection sumps are installed inside the bunded area and shallow ground water acumulating in the sumps is returned to the WPF for treatment.
271 | DAF 3 Flocculation Tank | Wastewater and flocculant | 3000 TBC | WPF | Steel | N/A | No | No | N/A | N/A | N/A | N/A | N/A | N/A | Bundled initially by concrete around it. Hills drilled into wall for chemicals so will be bundled by ibcs area | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage on the way to the lower end of site could intercept any leakages and return to the head of the works. | N/A. No tanker fill point. | None | N/A | Unknown | Gravitate to works drainage
272 | 2no. black tanks outisde of Southern side of the DAF building. | Two black tanks outside of DAF 1 half within a brickwork bund and half out of the top. Pipework between them which leads out of the sump into a graveled area. Both tanks have an external bund, unsafe to enter. | TBC | WPF | Concrete wall for bunding | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC
273 | 2no. DAF 1 Ferric chloride IBCs | 40% Ferric Chloride | 1000 each | WPF | Plastic | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A. Full IBCs delivered to site. Empty IBCs replaced in situ. | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage will intercept some liquid and return it to the head of the works. | N/A. Empty IBCs are replaced in situ. | Visual inspection. | N/A | N/A | N/A | The number of IBCs stored here may vary
274 | AFM Feed Tank | Processed Water | TBC | WPF | Plastic | AFM Feed Tank Bund | TBC Believe double bunded | No | Unknown | Unknown | Unknown | Plastic | Unknown | Unknown | Assumed level instrumentation with control to inhibit forward feed. | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage on the way to the lower end of site could intercept any leakages and return to the head of the works. | Tank fed from ST3 with contained pipework. No external fill point. Drip capture not applicable. | Assumed level detection. Visual inspection. | Unknown | Unknown | Sealed bund. Unknown if there is a bund drain valve.
275 | Anoxic 1 | Chemically treated industrial wastewater and AFM backwash water | 300000 | WPF | Concrete | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Assumed level instrumentation with control to inhibit forward feed. | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. | No tanker fill point. Fed from BT2 through internal pipework and also receives backwash water from the AFM filters, no drip capture point applicable. | Visual inspection only, tank is below ground. | N/A | N/A | N/A. If anoxic zones were to overflow, site drainage downhill of the anoxic zones and site boundary wall will contain any overflow.
276 | Anoxic 2 | Chemically treated industrial wastewater | 50000 | WPF | Concrete / Blockwork | N/A | No (below ground tank). Blockwork surrounding the chambers provides some degree of additonal coping. | Tank structure shared with Anoxic 3 and sludge pumping station. | N/A | N/A | N/A | Additional cooping provided by blockwork (Approximatley 0.43m (2no. Blocks)) | N/A | N/A | Assumed level instrumentation with control to inhibit forward feed. Visual inspections. Overflows into sludge pit or other anoxic sump. If levels continue to rise, the water will overflow the blockwork and flow downhill before being contained by the boundary wall. Surface drainage will intercept any lost material and be returned to the head of the works. | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Surface drainage will intercept liquid and return to the head of the works. | No tanker fill point. Anoxic sump 2 is filled by supernatant from ST1, BT2, BT2 bypass pipework from DAF2 and DAF3 and RAS WAS chamber, ST1 descum via internal pipework. | Visual inspection and level monitoring | Unknown | Unknown | Only overflow contained within the extended blockwork coping can be pumped out.
277 | Anoxic 3 | Chemically treated industrial wastewater | 50000 | WPF | Concrete / Blockwork | N/A | No (below ground tank). Blockwork surrounding the chambers provides some degree of additonal coping. | Tank structure shared with Anoxic 2 and sludge pumping station. | N/A | N/A | N/A | Additional cooping provided by blockwork (Approximatley 0.43m (2no. Blocks)) | N/A | N/A | Assumed level instrumentation with control to inhibit forward feed. Visual inspections. Overflows into sludge pit or other anoxic sump. If levels continue to rise, the water will overflow the blockwork and flow downhill before being contained by the boundary wall. Surface drainage will intercept any lost material and be returned to the head of the works. | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Surface drainage will intercept liquid and return to the head of the works. | No tanker fill point. Anoxic sump 3 is filled by supernatant from ST1, BT2 and receives a dose of ferric chloride. | Visual inspection and level monitoring | Unknown | Unknown | Only overflow contained within the extended blockwork coping can be pumped out.
278 | Antifoam IBC adjacent to AT2 | Antifoam (Aquatreat 5449) | 1000 | WPF | Plastic | AT2 Ferric chloride IBC Bund | Yes | Ferric chloride IBC for AT2 | 1140 | N/A | 114% | Plastic | No | No | N/A. Full IBCs delivered to site. Empty IBCs replaced in situ | Ground water (chippings/ gravel). No specific drainage | N/A. Full IBCs delivered to site and replaced in situ. Any drips from decoupling flexible pipework is contained within the bund. | Visual inspection | Unknown | Unknown | Pumped out
279 | Antiscalant by ro3 Ro | Antiscalant by ro3 | 127.6272 | WPF | Plastic | Antiscalant Bund | Yes | No | 162.5 | 0.5m x 0.5m x 0.65m | 127.3% | Plastic | No | No | Storage tank manually filled. Visual inspection. | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage | Storage tank is filled manually by removing the cabinet screen and manually filling. Drips would be collected within the tank bund. | Level switch in tank bund. Visual inspection | Unknown | Unknown | Bund emptied using a pump. Pump not permanently installed.
280 | AT1A | Effluent | 3500000 | WPF | Concrete | N/A | No. Small channel around the periphery of the tank, but of no significant volume relative to tank volume. | Common site bund (boundary wall at lower end of site) | Volime of blockwork is 4830 litres. (total volume of site containment unknown) | One layer of blockwork 0.3m from tank wall. | N/A | N/A | N/A | N/A | Unknown. Overflow pipe at high level will control level | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. | Tank is filled from Anoxic 1 fed via internal pipework, drip capture not applicable. | Visual inspection | Unknown | Environmental Walk Days/ Night Shifts. Details of maintenance schedule unknown, | N/A | Any significant leaks are designed to be retained by the site bund.
281 | AT1B | Effluent | 3500000 | WPF | Concrete | N/A | No. Small channel around the periphery of the tank, but of no significant volume relative to tank volume. | Common site bund (boundary wall at lower end of site) | Volime of blockwork is 4830 litres. (total volume of site containment unknown) | One layer of blockwork 0.3m from tank wall. | N/A | N/A | N/A | N/A | Unknown. Overflow pipe at high level will control level | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. | Tank is filled from Anoxic 1, fed via internal pipework, drip capture not applicable. | Visual inspection | Unknown | Environmental Walk Days/ Night Shifts. Details of maintenance schedule unknown, | N/A | Any significant leaks are designed to be retained by the site bund.
282 | AT2 | Effluent fed from anoxic tank 2 | 5000000 | WPF | Glass Lined Steel | N/A | No. Small channel around the periphery of the tank, but of no significant volume relative to tank volume. | Common site bund (boundary wall at lower end of site) | N/A (total volume of site containment unknown) | N/A | N/A | N/A | N/A | N/A | Filled from anoxic 2. Effluent leaves the tank via an overflow pipework. A blockage in this pipe would lead to the tank overflowing (pumped transfer). | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage on the way to the lower end of site could intercept any leakages and return to the head of the works. | No tanker fill point (fed by internal pipework). Drip capture not applicbale. | Visual inspection | N/A | Bund maintenance not applicable for the tank. Unsure of tank maintenance schedule. | N/A. No tank bund. | Any significant spillage is designed to flow to the lowest point of the works and be retained by the wall around the site boundary.
283 | AT2 ferric chloride dosing chamber | Biologically treated wastewater from AT2 and ferric chloride. | Unknown | WPF | Steel | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A. Wastewater flows from high level of AT2, through the chamber by gravity. Fixed flow rate. | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage on the way to the lower end of site could intercept any leakages and return to the head of the works. | N/A. Chamber is fed by pipework from AT2 and dosing pipework from a ferric chloride IBC | Visual inspection | N/A | Unknown. Bund maintenance not applicable. | N/A
284 | AT2 Ferric chloride IBC | Ferric chloride (40%) | 1000 | WPF | Plastic | AT2 Ferric chloride IBC Bund | Yes | Antifoam (Aquatreat 5449 IBC) | 1140 | N/A | 114% | Plastic | No | No | N/A. Full IBCs delivered to site. Empty IBCs replaced in situ | Ground water (chippings/ gravel). No specific drainage | N/A. Full IBCs delivered to site and replaced in situ. Any drips from decoupling flexible pipework is contained within the bund. | Visual inspection | Unknown | Unknown | Pumped out
285 | AT3 | Effluent fed from anoxic tank 3 | 2100000 | WPF | Glass Lined Steel | N/A | No. Small channel around the periphery of the tank, but of no significant volume relative to tank volume. | Common site bund (boundary wall at lower end of site) | N/A (total volume of site containment unknown) | N/A | N/A | N/A | N/A | N/A | Filled from anoxic 3. Effluent leaves the tank via an overflow pipework. A blockage in this pipe would lead to the tank overflowing (pumped transfer). | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage on the way to the lower end of site could intercept any leakages and return to the head of the works. | No tanker fill point (fed by internal pipework). Drip capture not applicbale. | Visual inspection | N/A | Bund maintenance not applicable for the tank. Unsure of tank maintenance schedule. | N/A. No tank bund. | Any significant spillage is designed to flow to the lowest point of the works and be retained by the wall around the site boundary.
286 | AT3 adjacent plastic tank | TBC | 15000 | WPF | GRP GRP: Plastic; No No: TBC Believe double bunded; N/A N/A: No; TBC TBC: Big question mark for this one | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage on the way to the lower end of site could intercept any leakages and return to the head of the works. | Feeds centrifugal and polymaker |  |  |  | Sealed bund
287 | Attenuation Tank (horizontal) | Processed Water | 100000 | WPF | Steel | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Overflow from UF feed tank | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage on the way to the lower end of site could intercept any leakages and return to the head of the works. | Not bunded | Visual inspection | Unknown | Unknown Bund maintenance not applicable | Gravitate to works drainage
288 | Balance tank DIOX IBC | DIOX | 1000 | WPF | Plastic | Balance Tank DIOX IBC Bund | Yes | No | 1100 | N/A | 110% | Plastic | No | No | N/A. Full IBCs are delivered to site and empty IBCs replaced in situ | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage can intercept flowing water and return to the head of the works. | N/A. Full IBCs delivered to site. | Visual inspection | Unknown | Unknown | Contents pumped out
289 | Black tank next to MBR | MBR Permeate | Don't think it has internal bund and filled anoxic 3 | WPF | Plastic | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage will intercept some liquid and return it to the head of the works. | TBC | TBC | TBC | TBC | TBC
290 | Bottom sludge pit | DAF 2 and DAF 3 sludge, RAW/WAS chamber, ST2 descum, Tertiary filter backwash. | Unknown | WPF | Brick, mostly below ground | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Unknown | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. | N/A. No tanker fill point. | None | N/A | Unknown tank maintenance reigime. Bund maintenance not applicable. | N/A
291 | BT1 | Untreated industrial wastewater | 2300000 | WPF | Glass Lined Steel | BT1 Bund | Yes. 1.3m deep wall 0.8m from the tank wall around the tank, and a shared bund with the diverter tank | Yes with Divert Tank | Unknown. | Unknown | Unknown | Block work & Cast Concrete | No | No | Level instrumentation and alarmed | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage will intercept some liquid and return it to the head of the works. | Above ground pipework is contained within the bund | Level monitoring | Unknown | Tanks inspected, visual inspections and environmental walk Days/Night shifts | Overpump from sump to works drainage | Tank is covered. If there is a leak and local bunding overflows, the contents will flow down hill towards the east of site and retained by the boundary wall.
292 | BT1 DIOX IBC | DIOX | 1000 | WPF | Plastic | Balance Tank DIOX IBC Bund | Yes | No | 1100 | N/A | 110% | Plastic | No | No | N/A. Full IBCs are delivered to site and empty IBCs replaced in situ | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage can intercept flowing water and return to the head of the works. | N/A. Full IBCs delivered to site. | Visual inspection | Unknown | Unknown | Contents pumped out
293 | BT1 DIOX IBC 2 | DIOX | 1000 | WPF | Plastic | Balance Tank DIOX IBC Bund | Yes | No | 1100 | N/A | 110% | Plastic | No | No | N/A. Full IBCs are delivered to site and empty IBCs replaced in situ | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage can intercept flowing water and return to the head of the works. | N/A. Full IBCs delivered to site. | Visual inspection | Unknown | Unknown | Contents pumped out
294 | BT1 Scrubber | Wet chemical | Approx. 15000 | WPF | Plastic | BT1 Scrubber bund | No designated tank bund, but located within common bunding with the dry scrubbers, BT1 and diverter tank. | Yes | Unknown. | Unknown | Unknown | Plastic | Unknown | No | Unused but drains to bottom of site | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage will intercept some liquid and return it to the head of the works. | No tanker fill point. Filled from closed pipework from balance tank 1. | Visual inspection. Extent of level monitoring unknown. | Unknown | Unknown | N/A. Common bund would need empything via a sump pump. | Tank is covered. If there is a leak and local bunding overflows, the contents will flow down hill towards the east of site and retained by the boundary wall.
295 | BT2 | Effluent | 1500000 | WPF | Concrete | N/A | No. Small drainage channel into the bunded area of settlement tank 1, which will then flow towards the lower end of site. | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Level instrumentation | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage will intercept some liquid and return it to the head of the works. | Tank filled from all three DAFs via internal pipework, no drip protection. | Level monitoring and alarmed | N/A | Tanks inspected, visual inspections and environmental walk Days/Night shifts | N/A | Tank is covered. If there is a leak and local bunding overflows, the contents will flow down hill towards the east of site and retained by the boundary wall.
296 | Centrate Header Tank | Centrate | 15000 | WPF | Plastic | Centrate header tank bund | Yes - internal bund | No | TBC |  |  | Plastic |  |  | Fed from centrifuges and not internally bunded | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage will intercept some liquid and return it to the head of the works. | No tanker fill point. Drip capture not applicable. | Level instrumentation | TBC | Unknwon | Sealed bund
297 | Centrifuge 1 polymer IBC | Concentrated liquid polymer (type unknown) | 1000 | WPF | Plastic | Centrifuge polymer 1 IBC bund | Yes | No | 1100 | N/A | 110% | Plastic | No | No | N/A. Full IBCs are delivered to site, and empty IBCs are replaced in situ. | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage will intercept some liquid and return it to the head of the works. | No tanker fill point. Full IBCs are delivered to site. Empty IBCs replaced in situ. Leakages from any flexible pipework decoupled during change over will be contianed within the bund. | Visual inspection. | Unknown | N/A for the IBC. Bund maintenanc unknown. | Temporary pump
298 | Centrifuge 2 polymer IBC | Concentrated liquid polymer (type unknown) | 1000 | WPF | Plastic | Centrifuge polymer 2 IBC bund | Yes | No | 1100 | N/A | 110% | Plastic | No | No | N/A. Full IBCs are delivered to site, and empty IBCs are replaced in situ. | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage will intercept some liquid and return it to the head of the works. | No tanker fill point. Full IBCs are delivered to site. Empty IBCs replaced in situ. Leakages from any flexible pipework decoupled during change over will be contianed within the bund. | Visual inspection. | Unknown | N/A for the IBC. Bund maintenanc unknown. | Temporary pump
299 | Centrifuge cake skip | Centrifuge sludge cake | TBC | WPF | Steel | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A. Centrifuges operated until the skip is full. | Local drainage within the centrifuge shelter. All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage will intercept some liquid and return it to the head of the works. | Trailer is filled by sludge automatically discharged from the chutes. Open skip area larghe enough to conatin the sludge. | Visual inspection | N/A | N/A. Skip may not be a Saputo owned asset. | N/A
300 | Citric Acid IBC for tertiary filters | Citric acid | 1000 | WPF | Plastic | Citric acid IBC bund | Yes | No | 1100 | N/A | 110% | Plastic | No | No | N/A. Full IBCs are delivered to site, and empty IBCs are replaced in situ. | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. | IBCs are filled off-site | Visual inspection | Unknown | Environmental Walk Days/ Night Shifts | Sealed bund which will be pumped out
301 | DAF 1 | Wastewater/sludge | TBC | WPF | Steel | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. | Fill from balancing tank | TBC | TBC | TBC | Gravitate to works drainage
302 | DAF 1 Caustic Tank 1 | Sodium Hydroxide (Caustic) 32% | 15000 | WPF | Plastic | DAF 1 Caustic Tank 1 Bund | Yes - Double Bunded | No | TBC | TBC | TBC | Plastic | Yes | Yes (Drain line) | External visual indication of the level. Overflow pipework goes to ground and is not contained locally. Any spills will be contained within the site bund. Any liquid captured by site drianage will be returned to the head of the works. | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage will intercept some liquid and return it to the head of the works. | Delivery area in front of tank. Access through a locaked gate. No drip cature facility. | Visual inspection. Plastic tube on the outside of the bund shows the liquid level within the bund. | Unknown | Unknown | Controlled drianage via a drain valve. Bund covered so there is no requirement to empty rain water.
303 | DAF 1 Caustic Tank 2 | Sodium Hydroxide (Caustic) 32% | 15000 | WPF | Plastic | DAF 1 Caustic Tank 2 Bund | Yes - Double Bunded | No | TBC | TBC | TBC | Plastic | Yes | Yes (Drain line) | External visual indication of the level. Overflow pipework goes to ground and is not contained locally. Any spills will be contained within the site bund. Any liquid captured by site drianage will be returned to the head of the works. | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage will intercept some liquid and return it to the head of the works. | Delivery area in front of tank. Access through a locaked gate. No drip cature facility. | Visual inspection. Plastic tube on the outside of the bund shows the liquid level within the bund. | Unknown | Unknown | Controlled drianage via a drain valve. Bund covered so there is no requirement to empty rain water.
304 | DAF 1 Ferric Chloride 1 | 40% Ferric Chloride | 15000 | WPF | Plastic | DAF 1 Ferric Chloride Tank 1 Bund | Yes - Double Bunded | No | TBC | TBC | TBC | Plastic | Yes | Yes (Drain line) | External visual indication of the level. Overflow pipework goes to ground and is not contained locally. Any spills will be contained within the site bund. Any liquid captured by site drianage will be returned to the head of the works. | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage will intercept some liquid and return it to the head of the works. | Delivery area in front of tank. Access through a locaked gate. No drip cature facility. | Visual inspection. Plastic tube on the outside of the bund shows the liquid level within the bund. | Unknown | Unknown | Controlled drianage via a drain valve. Bund covered so there is no requirement to empty rain water.
305 | DAF 1 Ferric Chloride 2 | 40% Ferric Chloride | 15000 | WPF | Plastic | DAF 1 Ferric Chloride Tank 2 Bund | Yes - Double Bunded | No | TBC | TBC | TBC | Plastic | Yes | Yes | External visual indication of the level. Overflow pipework goes to ground and is not contained locally. Any spills will be contained within the site bund. Any liquid captured by site drianage will be returned to the head of the works. | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage will intercept some liquid and return it to the head of the works. | Delivery area in front of tank. Access through a locaked gate. No drip cature facility. | Visual inspection. Plastic tube on the outside of the bund shows the liquid level within the bund. | Unknown | Unknown | Controlled drianage via a drain valve. Bund covered so there is no requirement to empty rain water.
306 | DAF 1 MBR Permeate Tank | MBR Permeate and treated water from the water reuse plant | TBC | WPF | TBC | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Unknown | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. | Fed by puipework from the MBR units and the water reuse plant. Drip capture not applicable. | TBC | N/A | Unknown. Bund integrity test not applicable. | N/A | Any leak in the tank will drain to local drainage for return to the head of the works.
307 | DAF 1 polymer make up unit | Liquid polymer solution. Unknown concentration | Unknown | WPF | Plastic | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Unknwon. Level instrumentation and control TBC. | Local drainage within DAF1 building. | N/A. Polyme rmake up unit is filled by neat polymer rpumped from the concentrated polymer storage. Water fed from the potable water supply.Lots of flexible pipework. Any drips will go to floor and eventually washed to DAF1 drainage. | Visual inspection. Unknown level instrumentation/control. | N/A | Unknown tank maintenance schedule. Bund maintenance not applicable. | N/A
308 | DAF 1 Polymer storage IBC | Concentrated liquid polymer (Aquatreat N223F) | 1000 | WPF | Plastic | DAF 1 Polymer Bund | Yes | No | 1100 | 1*1*1.15 | 110% | Plastic | No | No | N/A. Full IBCs are delivered to site. Empty IBCs replaced in situ. | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. | N/A | Visual inspection | Unknown | Environmental Walk Days/ Night Shifts | Sump pump. | Any leak of the IBC bund can be contained within the DAF1 unit building.
309 | DAF 1 Sulphuric Acid 1 | 77% Sulphic Acid | 15000 | WPF | Plastic | DAF1 sulphuric acid storage tank bund | Yes - Double Bunded | No | TBC | TBC | TBC | Plastic | Yes | Yes | External level indication. Overflow pipework will drain to local area, Not contained. | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. | Low level adjacent to the security gate for the tanks. No drip capture. | Visual inspection. Transparent plastic tubing on the external of the tank indicates the liquid level in the bund. | Unknown | Unknown | Sealed bund. Bund emptied in a controlled manner by the bund drain valve. | Any leak in the tank flow down towards the lower end of site. If intercepted by site drianage, it will then be returned to the head of the works.
310 | DAF 2 | Wastewater/sludge | TBC | WPF | Steel | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A (overflow weir) | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. | N/A. Fed by pipework from BT1 | Visual inspection. Unknown level instrumentation/control. | N/A | Unknown. Bund maintenance N/A | Gravitate to works drainage
311 | DAF 2 Caustic Tank 1 | 32% Caustic | 15000 | WPF | Plastic | DAF 2 Caustic Tank 1 Bund | Yes - Double Bunded | No | TBC | TBC | TBC | Plastic | Yes | Yes | External visual indication of the level. Overflow pipework goes to ground and is not contained locally. Any spills will be contained within the site bund. Any liquid captured by site drianage will be returned to the head of the works. | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage will intercept some liquid and return it to the head of the works. | Delivery area in front of tank. Access through a locaked gate. No drip cature facility. | Visual inspection. Plastic tube on the outside of the bund shows the liquid level within the bund. | Unknown | Unknown | Controlled drianage via a drain valve. Bund covered so there is no requirement to empty rain water.
312 | DAF 2 Ferric Chloride bulk storage tank | 40% Ferric Chloride | 15000 | WPF | Plastic | DAF 2 Ferric Chloride Tank Bund | Yes - Double Bunded | No | TBC | TBC | TBC | Plastic | Yes | Yes | Visual level indication on the tank. Any overflow will spill to floor and will not be contained. | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage will intercept some liquid and return it to the head of the works. | Tanker fill point at low level and not contained within a bund. No drip capture. | Visual inspection. Liquid level within the bund is displayed on the outside of the bund and can be seen from pedestrian walkways. | Unknown | Unknown | Drain valve. Temporary pipework required to drain the contents to a safe container. | Any spills from the tank, or tank overflow, will spill to ground and will not be contained locally. Liquid will flow down to the bottom of site and be contained by the site boundary wall, if not intercepted by site drainge before.
313 | DAF 2 ferric chloride IBC | Ferric chloride | 1000 | WPF | Plastic | DAF 2 ferric chloride IBC | Yes | No | 1100 | N/A | 110% | Plastic | No | No | N/A. Full IBCs are delivered to site and empty IBCs replaced in situ | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage can intercept flowing water and return to the head of the works. | N/A. Full IBCs delivered to site. | Visual inspection | Unknown | Unknown | Contents pumped out
314 | DAF 2 polymer make up unit | Liquid polymer solution. Unknown concentration | Unknown | WPF | Plastic | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Unknwon. Level instrumentation and control TBC. | Local drainage within DAF2 building. | N/A. Polyme rmake up unit is filled by neat polymer rpumped from the concentrated polymer storage. Water fed from the potable water supply.Lots of flexible pipework. Any drips will go to floor and eventually washed to DAF2 drainage. | Visual inspection. Unknown level instrumentation/control. | N/A | Unknown tank maintenance schedule. Bund maintenance not applicable. | N/A
315 | DAF 2 Polymer storage IBC | Concentrated liquid polymer (Aquatreat N223F) | 1000 | WPF | Plastic | DAF 2 Polymer IBC bund | Yes | No | 1100 | N/A | 110% | Plastic | No | No | N/A. Full IBCs are delivered to site, and empty IBCs are replaced in situ. | Local drainage within the DAF 2 building. Site drainage returned to the head of works. | N/A. Full IBCs deliovered to site. Drips from connecting plastic pipework are contained within the bund. | Visual inspection. Unknown level instrumentation/control. | Unknown | Unknown | Sump pump used to empty bund.
316 | DAF 3 | Wastewater/sludge | 35000 | WPF | Steel | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | None. Weir on discharge will maintain set level in the unit. | Local drainage within the DAF 2 building. Site drainage returned to the head of works. | The tank is filled via internal pipework from the DAF 3 Flocculation Tank. No drip capture method. | Visual inspection. Unknown level instrumentation/control. | Unknown | Environmental Walk Days/ Night Shifts | N/A | Any spills will be contained within the site drainage of DAF 2 building and returned to the head of the works.
317 | DAF 3 Mixer tank | Wastewater dosed with ferric chloride and polymer. | 8000 | WPF | Steel | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | No bund, more like a container wall. Hole has been cored through the wall for the chemical dosing pipework, tehrefore no containement at all | No overfill protection. Wastewater is pumped into the unit and leaves by gravity. Hydraulically designed not to overfill. | Site drainage. No means of containment. | No tanker fill point. Mixer is fed by temporary pipework (bauer coupling) from the bnalance tank. Drip collection not applicable, however minor pipework leaks will be collected by site drainage. | Visual inspection and flow meters. | N/A | Unknown maintenance schedule for the mixer unit. Bund inspections not applicable. | N/A | Any spills from the tank not be contained locally will flow down to the bottom of site and be contained by the site boundary wall, if not intercepted by site drainge before.
318 | DAF MBR CIP Tank | TBC | TBC | WPF | TBC | TBC | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBC | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. | N/A. Tanker filled from internal pipework. Drip capture not applicable. | TBC | TBC | TBC | N/A | TBC
319 | DAF2 ferric chloride IBC | 40% Ferric Chloride | 1000 | WPF | Plastic | DAF2 ferri chloride IBC bund | Yes | No | 1110 | N/A | 111% | Plastic | No | No | N/A. Full IBCs are delivered to site, and empty IBCs are replaced in situ. | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage will intercept some liquid and return it to the head of the works. | N/A. Full IBCs deliovered to site. Drips from connecting plastic pipework are contained within the bund. | Visual inspection. Unknown level instrumentation/control. | Unknown | Unknown | Sump pump used to empty bund.
320 | Divert Tank | Sludge centrate, GOS & Demin and divert from the cheese and whey feed stream. | 900000 | WPF | Glass Lined Steel | Divert tank bund | Yes | Yes - BT1 | Unable to measure bund volume on site. Bund shared with BT1. |  | TBC | Block work & Cast Concrete | No | No | Level instrumentation and alarmed. Automatic control unknown. | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. | N/A. Tanker filled from internal pipework. Drip capture not applicable. | Visual inspection. Unknown level instrumentation/control. | Unknown | Unknwon | Overpump from sump to works drainage | If the tank bund overflows, contents will flow downhill towards the site boundary wall and contained within the site boundary.
321 | Drainage pumping station | Site drainage water | Unknown (below ground) | WPF | Concrete | N/A | No | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A. Site drainage gravitates to this chamber and is then pumped to the head of works. | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Areas of chippings around the lower part of site which may permit discharge to groundwater. | N/A | Ultrasonic level transmitter and trends on SCADA. | N/A | Unknown. Bund maintenance not applicable. | N/A
322 | Ferric Chloride IBC 2 for dosing of AT2 | Ferric Chloride | 1000 | WPF | Plastic | AT2 Ferric chloride doesing IBC Bund | Yes | Yes - Ferric Chloride IBC for dosing of AT2 | 1150 | N/A | 115% | Plastic | No | No | IBCs are delivered to site full and the empty IBC replaced in situ. Overfill protection not applicable. | Drainage via the surface water drain and transferred to the WPF | IBCs are delivered to site full and the empty IBC replaced in situ. | Visual inspection. Unknown level instrumentation/control. | Unknown | Environmental Walk Days/ Night Shifts | Bund emptied using submersible pump.
323 | Ferric chloride IBC adjacent to RO plant | Ferric chloride | 1000 | WPF | Plastic | N/A | Yes | No | 546.75 | N/A | 54.68% | Stainless Steel | No | No | N/A. Full IBCs are delivered to site and empty IBCs replaced in situ | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage can intercept flowing water and return to the head of the works. | N/A. Full IBCs delivered to site. Any drips from connecting flexible pipework to the IBC outlet will be contained within the bund. | Visual inspection. Unknown level instrumentation/control. | Unknown | Environmental Walk Days/ Night Shifts | Bund emptied via a sump pump.
324 | Ferric Chloride IBC for dosing of AT2 | Ferric Chloride | 1000 | WPF | Plastic | AT2 Ferric chloride doesing IBC Bund | Yes | Yes - Ferric Chloride IBC 2 for dosing of AT2 | 1150 | N/A | 115% | Plastic | No | No | IBCs are delivered to site full and the empty IBC replaced in situ. Overfill protection not applicable. | Drainage via the surface water drain and transferred to the WPF | IBCs are delivered to site full and the empty IBC replaced in situ. | Visual inspection. Unknown level instrumentation/control. | Unknown | Environmental Walk Days/ Night Shifts | Bund emptied using submersible pump.
325 | HW Overflow Tank | Wastewater from main site | TBC | WPF | Steel | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Overflow tank for human waste not used before entrane | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage can intercept flowing water and return to the head of the works. | Unknown. Unkown how the tank is filled. | Visual inspection. Level monitor. | N/A | Unknown. Bund inspection not applicable. | N/A
326 | Hydrochloric acid chemical container for chlorine dioxide generator | 9% hydrochloric acid | 60 | WPF | Plastic | Chlorine dioxide generator bund | Yes | Sodium hypochlorite chemical container for the chlorine dioxide generator | 98 | 0.7m x 0.8m x 0.2m | 163.3% | Plastic | Yes | No | N/A. Full containers brought to site | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage on the way to the lower end of site could intercept any leakages and return to the head of the works. | N/A. No tanker fill point. Any drip from connecting and disconnecting dosing pump pipework will be contained within the bund. | Visual inspection. Unknown level instrumentation/control. | Unknown | Tank inspection not applicable (empty containers are replaced in situ). Unknown maintenance measures for the bund. | Via a small drain valve. Contents must be collected in a container to allow for safe disposal.
327 | IBC chemical store adjacent to DAF3 | 2no. Polymer IBCs (1 in use, both bunded). 1no. Ferric chloride IBC (in use, bunded). 6no. 50% sulphuric acid IBCs. | 1000 each | WPF | Plastic | DAF3 chemical bund | Yes (Both polymer IBCs and the ferric chloride IBC only. The 6no. Sulphuric acid IBCs are not bunded. | Both polymer IBCs and the ferric chloride IBC share a bund | 1140 | N/A | 114% | Plastic (where applicable) | No | No | N/A. Full IBCs are delivered to site and empty IBCs replaced in situ | Some liquid will be contained within the chemical storage unit. Should the liquid overflow, the contents will drain to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage can intercept flowing water and return to the head of the works. . | N/A. Full IBCs delivered to site. Any drips from connecting flexible pipework to the IBC outlet will be contained within the bund. | Visual inspection. Unknown level instrumentation/control. | Unknown | Unknown | Pumped out | The storage unit itself has a containment area of approx. 5m x 6m x 0.2m (6000L)
328 | Inlet Well | Effluent | TBC | WPF | Concrete / Blockwork | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Unknown | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage on the way to the lower end of site could intercept any leakages and return to the head of the works. | N/A. Well filled by gravity from the inlet flume. Drip collection not applicable. | Visual inspection. Unknown level instrumentation/control. | N/A | Unknown | Not applicable. Below ground tank
329 | Bulk Caustic Tank adjacent to chemical store | 32% Caustic | 15000 | WPF | Plastic | Inlet well caustic tank bunding | Yes internal bunding | No | Unknown | Unknown | N/A | Plastic | Unknown | Unknown | Unknown | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage on the way to the lower end of site could intercept any leakages and return to the head of the works. | Fill point next too tank drips drain to bottom of site | Visual inspection. Unknown level instrumentation/control. | Unknown | Unknown | Sealed bund
330 | Locked IBC chemical store at the top of site close to the control room | 10no. IBCs of different chemicals. Not certain of type | 1000 each | WPF | Plastic | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A. Full IBCs are delivered to site and stored here. | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage can intercept flowing liquid and return to the head of the works. | N/A. Full IBCs delivered to site and simply stored here. | Visual inspection. Unknown level instrumentation/control. | N/A | Unknown | N/A | Number of IBCs may vary. IBCs are delivered with the valves and top sealed.
331 | MBR Potable Water | Water | TBC | WPF | Plastic | TBC | TBC | No | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Big black tan AT3 | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. |  | Visual inspection. Unknown level instrumentation/control. |  |  | Sealed bund
332 | MBR1 Wehrle AC10 | Nitric acid and orthophosphoric acid | 20 | WPF | Plastic | MBR1 Werhle AC10 bund | Yes | Yes | 96 | 0.8m x 0.6m x 0.2m | 480% | Plastic | No | No | N/A. Full containers delivered to site. Empty containers replaced in situ. | Hard standing contained within DAF1 building/ outdoor bunding | N/A. Full containers delivered to site. Empty containers replaced in situ. Any drips from changing over flexible pipework will be contained within the tank bund. | Visual inspection. Unknown level instrumentation/control. | Unknown | Unknown | Contents poured away to drain.
333 | MBR2 Wehrle AC10 | Nitric acid and orthophosphoric acid | 20 | WPF | Plastic | MBR2 Werhle AC10 bund | Yes | Yes | 96 | 0.8m x 0.6m x 0.2m | 480% | Plastic | No | No | N/A. Full containers delivered to site. Empty containers replaced in situ. | Hard standing contained within DAF2 building/ outdoor bunding | N/A. Full containers delivered to site. Empty containers replaced in situ. Any drips from changing over flexible pipework will be contained within the tank bund. | Visual inspection. Unknown level instrumentation/control. | Unknown | Unknown | Contents poured away to drain.
334 | MBR2 Wehrle AL10 | Tetrasodium ethylenediaminetetraacetate | 20 | WPF | Plastic | MBR1 Wehrle AL10 bund | Yes | Yes | 96 | 0.8m x 0.6m x 0.2m | 480% | Plastic | No | No | N/A. Full containers delivered to site. Empty containers replaced in situ. | Hard standing contained within DAF1 building/ outdoor bunding | N/A. Full containers delivered to site. Empty containers replaced in situ. Any drips from changing over flexible pipework will be contained within the tank bund. | Visual inspection. Unknown level instrumentation/control. | Unknown | Unknown | Contents poured away to drain.
335 | MBR2 Wehrle AL10 | Tetrasodium ethylenediaminetetraacetate | 20 | WPF | Plastic | MBR2 Wehrle AL10 bund | Yes | Yes | 96 | 0.8m x 0.6m x 0.2m | 480% | Plastic | No | No | N/A. Full containers delivered to site. Empty containers replaced in situ. | Hard standing contained within DAF2 building/ outdoor bunding | N/A. Full containers delivered to site. Empty containers replaced in situ. Any drips from changing over flexible pipework will be contained within the tank bund. | Visual inspection. Unknown level instrumentation/control. | Unknown | Unknown | Contents poured away to drain.
336 | No 2 Klargester | Sewage fed from the HWT located in the car park. | TBC | WPF | Fibreglass | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Unknown | Tanks are below ground. Concrete hardstanding at ground level goes to surface drainage. Some could go to the grassy area and to ground water. | Pipework that feeds the RBC is below ground. No tanker fill point, | Visual inspection. Unknown level instrumentation/control. | N/A | Unknown. Tank bund inspection not applicable. | N/A
337 | No1 Klargester | Sewage fed from the HWT located in the car park. | TBC | WPF | Fibreglass | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Unknown | Tanks are below ground. Concrete hardstanding at ground level goes to surface drainage. Some could go to the grassy area and to ground water. | Pipework that feeds the RBC is below ground. No tanker fill point, | Visual inspection. Unknown level instrumentation/control. | N/A | Unknown. Tank bund inspection not applicable. | N/A
338 | Process Water Return | Processed Water | TBC | WPF | Plastic | Process water return tank bund | TBC Believe double bunded | No | Unknown | N/A | N/A | Plastic | Unknown | Unknown | Number 4 in the tanks together | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage on the way to the lower end of site could intercept any leakages and return to the head of the works. | Unknown | Visual inspection. Unknown level instrumentation/control. | Unknown | Unknown | Sealed bund
339 | RO 1 CIP tank | CIP circulation water | TBC. 2000L to 3000L | WPF | Plastic | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | In shipping container and couldn't inspect safely | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage on the way to the lower end of site could intercept any leakages and return to the head of the works. | No tanker fill point. Fed closed pipework. Drip collection not applicable. | Visual inspection. Unknown level instrumentation/control. | Unknown | Unknown | Unknown
340 | RO 2 CIP tank | CIP circulation water | TBC. 2000L to 3000L | WPF | Plastic | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | In shipping container and couldn't inspect safely | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage on the way to the lower end of site could intercept any leakages and return to the head of the works. | No tanker fill point. Fed closed pipework. Drip collection not applicable. | Visual inspection. Unknown level instrumentation/control. | Unknown | Unknown | Unknown
341 | RO 3 CIP tank | CIP circulation water | TBC | WPF | Plastic | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Fed from potable water; no bund | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage on the way to the lower end of site could intercept any leakages and return to the head of the works. | No tanker fill point. Fed by closed pipework from potable water supply | Visual inspection. Unknown level instrumentation/control. | Unknown | Unknown | Unknown
342 | RO 3 Hot Water tank | Water | TBC | WPF | Stainless Steel | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Fed from potable water; no bund | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage on the way to the lower end of site could intercept any leakages and return to the head of the works. | No tanker fill point. Fed by closed pipework from potable water supply | Visual inspection. Unknown level instrumentation/control. | Unknown | Unknown | Unknown
343 | RO Feed Tank 1 | Retentate from the ultrafiltration units | TBC | WPF | Plastic | RO Feed Tank 1 Bund | TBC Believe double bunded | No | Unknown | Unknown | Unknown | Plastic | Unknown | Unknown | Unknown | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage on the way to the lower end of site could intercept any leakages and return to the head of the works. Areas of chippings around the lower part of site which may permit discharge to groundwater. | No tanker fill point. Fed by pipework from the UF membranes. Drip collection not applicable | Visual inspection. Unknown level instrumentation/control. | Unknown | Unknown | Unknown
344 | RO Feed Tank 2 | Retentate from the ultrafiltration units | TBC | WPF | Plastic | RO Feed Tank 1 Bund | TBC Believe double bunded | No | Unknown | Unknown | Unknown | Plastic | Unknown | Unknown | Unknown | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage on the way to the lower end of site could intercept any leakages and return to the head of the works. | No tanker fill point. Fed by pipework from the UF membranes. Drip collection not applicable, | Visual inspection. Unknown level instrumentation/control. | Unknown | Unknown | Unknown
345 | RO permeate tank | RO Permeate | TBC | WPF | Plastic | RO Permeate tank bund | TBC | No | Unknown | Unknown | Unknown | Plastic | Unknown | Unknown | Unknown | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage on the way to the lower end of site could intercept any leakages and return to the head of the works. | No tanker fill point. Fed by pipework from the RO membranes. Drip collection not applicable. | Visual inspection. Unknown level instrumentation/control. | Unknown | Unknown | Unknown
346 | Serpentine flocculations for DAF 2 | Chemically dosed water from BT1 | TBC | WPF | Plastic | N/A | No | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Drains to DAF 2 drainage located within the building. Contents returned to the head of the works. | No tanker fill point. Closed pipework. | Visual inspection. Unknown level instrumentation/control. | N/A | Unknown maintenance reigime for the serpentine flocculator. Bund inspection not applicable. | N/A
347 | Sodium bisulphite IBC adjacent to RO plant | Sodium bisulphite (20%) | 1000 | WPF | Plastic | N/A | Yes | No | 546.75 | N/A | 54.68% | Stainless Steel | No | No | N/A. Full IBCs are delivered to site and empty IBCs replaced in situ | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage can intercept flowing water and return to the head of the works. Risk that some surface water will contaminate the groundwater close to this area. | N/A. Full IBCs delivered to site. Any drips from connecting flexible pipework to the IBC outlet will be contained within the bund. | Visual inspection. Unknown level instrumentation/control. | Unknown | Environmental Walk Days/ Night Shifts | Bund emptied via a sump pump.
348 | Sodium hydroxide IBC at head of the works | Sodium hydroxide (47%) | 1000 | WPF | Plastic | Inlet flume sodium hydroxide IBC bund | Yes | No | 1100 | N/A | 110% | Plastic | No | No | N/A. Full IBCs are delivered to site and empty IBCs replaced in situ | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage can intercept flowing liquid and return to the head of the works. | N/A. Full IBCs delivered to site. | Visual inspection. Unknown level instrumentation/control. | Unknown | Unknown | Contents pumped out
349 | Sodium hydroxide IBC for dosing itno inlet well | Sodium hydroxide (47%) | 1000 | WPF | Plastic | Inlet well sodium hydroxide IBC bund | Yes | No | 1100 | N/A | 110% | Plastic | No | No | N/A. Full IBCs are delivered to site and empty IBCs replaced in situ | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage can intercept flowing liquid and return to the head of the works. | N/A. Full IBCs delivered to site. | Visual inspection. Unknown level instrumentation/control. | Unknown | Unknown | Contents pumped out
350 | Sodium hypochlorite chemical container for chlorine dioxide generation | 7.5% sodium hypochlorite | 60 | WPF | Plastic | Chlorine dioxide generator bund | Yes | Hycrochloric acid chemical container for the chlorine dioxide generator | 98 | 0.7m x 0.8m x 0.2m | 163.3% | Plastic | Yes | No | N/A. Full containers brought to site | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage on the way to the lower end of site could intercept any leakages and return to the head of the works. | N/A. No tanker fill point. Any drip from connecting and disconnecting dosing pump pipework will be contained within the bund. | Visual inspection. Unknown level instrumentation/control. | Unknown | Tank inspection not applicable (empty containers are replaced in situ). Unknown maintenance measures for the bund. | Via a small drain valve. Contents must be collected in a container to allow for safe disposal.
351 | Sodium hypochlorite IBC adjacent to RO plant | Sodium hypochlorite | 1000 | WPF | Plastic | N/A | Yes | No | 546.75 | N/A | 54.68% | Stainless Steel | No | No | N/A. Full IBCs are delivered to site and empty IBCs replaced in situ | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage can intercept flowing water and return to the head of the works. | N/A. Full IBCs delivered to site. Any drips from connecting flexible pipework to the IBC outlet will be contained within the bund. | Visual inspection. Unknown level instrumentation/control. | Unknown | Environmental Walk Days/ Night Shifts | Bund emptied via a sump pump.
352 | ST1 | Biologically treated wastewater from AT1a and AT1b. | TBC | WPF | Glass Lined Steel | N/A | Yes | N/A | 14049.2023 | N/A | #VALUE! | N/A | N/A | N/A | None. Peripheral weir dictates level. | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage on the way to the lower end of site could intercept any leakages and return to the head of the works. | N/A. No tanker fill point. Tank is fed via pipework from AT1A and AT1B. | None | Unknown | Unknown | Emptied via sump pump. | When this small bund overfills, the contents will flow by graviy to the lower end of site, contained by the boundary wall. Site drainage inbetween the tank and the lower end will intercept run off and return to the head of the works.
353 | ST1 RAS WAS | Settled sludge from ST1 | TBC | WPF | Concrete | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Unknown | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage on the way to the lower end of site could intercept any leakages and return to the head of the works. | No tanker fill point. Fed by pipework from ST1 | Visual inspection. Unknown level instrumentation/control. | N/A | Unknown | N/A
354 | ST2 | Biologically treated wastewater from AT2 | TBC | WPF | Concrete | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | None. Peripheral weir dictates level. | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage on the way to the lower end of site could intercept any leakages and return to the head of the works. | N/A. ST2 fed by internal pipework from AT2, | Visual inspection. Unknown level instrumentation/control. | N/A | Unknown | N/A
355 | ST2 RAS WAS Chamber | Settled sludge from ST2 | TBC | WPF | Concrete | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Unknown | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage on the way to the lower end of site could intercept any leakages and return to the head of the works. Areas of chippings around the lower part of site which may permit discharge to groundwater. | N/A. Fed by pipework from ST2. | Visual inspection. Unknown level instrumentation/control. | N/A | Unknown | N/A
356 | ST3 | Chemically treated RO reject water | TBC | WPF | Concrete | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | None. Peripheral weir dictates level. | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage on the way to the lower end of site could intercept any leakages and return to the head of the works. | N/A. Fed by pipework from the RO reject water flocculator | Visual inspection. Unknown level instrumentation/control. | N/A | Unknown | N/A
357 | ST4 | Not in Use | TBC | WPF | Concrete | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Not in use | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage on the way to the lower end of site could intercept any leakages and return to the head of the works. | N/A | N/A | N/A | N/A | N/A
358 | Sulphuric acid for RO3 | Sulphuric acid (50%) | 25 | WPF | Plastic | RO3 sulphuric acid drum bund | Yes | No | 162.5 | 0.5m x 0.5m x 0.65m | 650% | Plastic | Not visible | No | N/A. Full containers delivered to site and empty containers are replaced in situ. | Any spills of the bund will be contained by the container drainage. | No tanker fill point. Any drips from changing plastic pipework will be contained within the bund. | Unknown | Unknown | Unknown | Contents are pumped out.
359 | Tertiary filter 1 | Settled wastewater from ST2 | Unknown | WPF | Steel | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Unknown | Local drainage around the tertiary filter hardstanding. All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage between tank and the lower end of site could intercept any leakages and return to the head of the works. | N/A. Fed by pipework from ST2. | Visual inspection. Unknown level instrumentation/control. | N/A | Unknown. Bund maintenance not applicable. | N/A
360 | Tertiary filter 2 | Settled wastewater from ST2 | Unknown | WPF | Steel | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Unknown | Local drainage around the tertiary filter hardstanding. All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage between tank and the lower end of site could intercept any leakages and return to the head of the works. | N/A. Fed by pipework from ST2. | Visual inspection. Unknown level instrumentation/control. | N/A | Unknown. Bund maintenance not applicable. | N/A
361 | Tertiary filter 3 | Settled wastewater from ST2 | Unknown | WPF | Steel | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Unknown | Local drainage around the tertiary filter hardstanding. All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage between tank and the lower end of site could intercept any leakages and return to the head of the works. | N/A. Fed by pipework from ST2. | Visual inspection. Unknown level instrumentation/control. | N/A | Unknown. Bund maintenance not applicable. | N/A
362 | Tertiary filter backwash tank | Tertiary treated wastewater | TBC (1000L to 2000L) | WPF | GRP | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Overflow pipe which will spill to chippings adjacent to tertiary filter plinth. Instrumentation unknown. | Local drainage around the tertiary filter hardstanding. All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage between tank and the lower end of site could intercept any leakages and return to the head of the works. | N/A. fed by pipework from the tertiary filters. | Visual inspection. Unknown level instrumentation/control. | N/A | Unknown. Bund maintenance not applicable. | N/A
363 | Tertiary filter CIP Tank (TK106) | Solution of 5% citric acid and water | Unknown | WPF | Plastic | Tertiary filter CIP Tank bund | Yes | No | 2106.75 | 2.65m x 2.65m x 0.3m | TBC | Concrete | No | No | Overflow pipe on the tank which is contained within the bund (discharge point at low level to prevent splashing). | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage between tank and the lower end of site could intercept any leakages and return to the head of the works. | N/A. Tank is filled via pumps and pipework from the citric acid IBC adjacent to the tank, and pipework from the potable water supply. | Visual inspection. Unknown level instrumentation/control. | Unknown | Unknown | Sump pump via low point in the bund.
364 | Top sludge pit | Sludge from MBR WAS, ST1 RAS/WAS chamber, DAF 1 Unit | Unknown | WPF | Concrete | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | None | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage on the way to the lower end of site could intercept any leakages and return to the head of the works. | No tanker fill point (fed from bottom sludge pit, MBR WAS and ST1 RAS/WAS chamber | Visual inspection. Unknown level instrumentation/control. | N/A | Unknown maintnenance measures for the tank. Bund maintenance not applicable. | N/A
365 | Treated effluent tank | Treated effluent from the tertiary filters | Unknown | WPF | Stainless Steel | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Unknown. | Local drainage around the tertiary filter hardstanding. All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage between tank and the lower end of site could intercept any leakages and return to the head of the works. | N/A. fed by pipework from the tertiary filters. | Visual inspection. Unknown level instrumentation/control. | N/A | Unknown. Bund maintenance not applicable. | N/A
366 | UF CIP Tank 1 | CIP circulation water | 2000 - 3000 | WPF | Plastic | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Unknown. | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage between tank and the lower end of site could intercept any leakages and return to the head of the works. | N/A. Fed by pipework from the CIP chemical bulk storage containers and potable water supply | Visual inspection. Unknown level instrumentation/control. | N/A | Unknown. Bund maintenance not applicable. | N/A
367 | UF CIP Tank 2 | CIP circulation water | 2000 - 3000 | WPF | Plastic | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Unknown. | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage between tank and the lower end of site could intercept any leakages and return to the head of the works. | N/A. Fed by pipework from the CIP chemical bulk storage containers and potable water supply | Visual inspection. Unknown level instrumentation/control. | N/A | Unknown. Bund maintenance not applicable. | N/A
368 | UF Feed Tank | Processed Water | TBC | WPF | Plastic | UF Feed tank bund | No | No | N/A | N/A | N/A | N/A | N/A | N/A | Unknown | Local drainage around the UF feed tank hard standing area. All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage between tank and the lower end of site could intercept any leakages and return to the head of the works. | N/A. Fed by pipework from ST2 tertiary filter and MBR (AT3) permeate tank. | Visual inspection. Unknown level instrumentation/control. | N/A | Unknown. Bund maintenance not applicable. | N/A
369 | Ultrachlor 15 IBC 1 | Ultrachlor 15 (15% Sodium hypochlorite solution, Brenntag) | 1000 | WPF | Plastic | Ultrachlor 15 IBC1 Bund | Yes | Yes (Ultrachlor 15 IBC 2) | 1140 | N/A | 114% | Plastic | No | No | N/A. Full IBCs delivered to site. Empty IBCs replaced in situ. This is an IBC storage location. | Groundwater. No designated hardstanding area or drianage. | N/A. Full IBCs delivered to site. Empty IBCs replaced in situ. This is an IBC storage location. | Visual inspection. | Unknown | Unknown | Contents pumped out | Number of IBCs may vary. IBCs are delivered with the valves and top sealed.
370 | Ultrachlor 15 IBC 2 | Ultrachlor 15 (15% Sodium hypochlorite solution, Brenntag) | 1000 | WPF | Plastic | Ultrachlor 15 IBC1 Bund | Yes | Yes (Ultrachlor 15 IBC 1) | 1140 | N/A | 114% | Plastic | No | No | N/A. Full IBCs delivered to site. Empty IBCs replaced in situ. This is an IBC storage location. | Groundwater. No designated hardstanding area or drianage. | N/A. Full IBCs delivered to site. Empty IBCs replaced in situ. This is an IBC storage location. | Visual inspection. | Unknown | Unknown | Contents pumped out | Number of IBCs may vary. IBCs are delivered with the valves and top sealed.
371 | Ultrachlor 15 IBC 3 | Ultrachlor 15 (15% Sodium hypochlorite solution, Brenntag) | 1000 | WPF | Plastic | Ultrachlor 15 IBC1 Bund | Yes | No | 1140 | N/A | 114% | Plastic | No | No | N/A. Full IBCs delivered to site. Empty IBCs replaced in situ. This is an IBC storage location. | Groundwater. No designated hardstanding area or drianage. | N/A. Full IBCs delivered to site. Empty IBCs replaced in situ. This is an IBC storage location. | Visual inspection | Unknown | Unknown | Contents pumped out | Number of IBCs may vary. IBCs are delivered with the valves and top sealed.
372 | Urea IBC | 50% Urea | 1000 | WPF | Plastic | Urea IBC bund | Yes | No | 1100 | N/A | 110% | Plastic | No | No | N/A. Full IBCs are delivered to site and empty IBCs replaced in situ | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage can intercept flowing water and return to the head of the works. | N/A. Full IBCs delivered to site. | Visual inspection | Unknown | Unknown | Contents pumped out
373 | Water IBC adjacent to RO plant | Water | 1000 | WPF | Plastic | RO water IBC | Yes | No | 1100 | N/A | 110% | Plastic | No | No | None | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage can intercept flowing water and return to the head of the works. | No tanker fill point. Any spills of water will be contained within the tank IBC bund or will go to ground | Visual inspection | Unknown | Unknown | Contents pumped out
374 | 10no. Sodium chlorate drums | 7.5% sodium chlorate | 210 each | WPF (Chemical storage area adjacent to car park) | Plastic | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Ground water. No specific drainage | N/A. Full drums delivered to site, | Visual inspection | N/A | Visual inspection for the drums. Bund maintenance schedule not aplicable. | N/A | 10no. 210 litre Sodium chlorite drums stored here at time of inspection.
375 | 18no. Container storarge | Unknown | 20 each | WPF (Chemical storage area adjacent to car park) | Plastic | Unknown 25L container bund | Yes | Yes (total of 18no. containers stored on the IBC) | 1140 | N/A | 316.7% | Plastic | No | No | N/A. Full containers delivered to site and taken to point of application when required. Containers are fully sealed. | Ground water. No specific drainage | N/A. Full containers delivered to site. Empty containers replaced in situ. | Visual inspection | Unknown | Unknown | Contents pumped out
376 | 18no. Sodium hydroxide container storage | Sodium hydroxide | 20 each | WPF (Chemical storage area adjacent to car park) | Plastic | Sodium hydroxide container storage bund | Yes | Yes (19no. Acid containers) | 1140 | N/A | 316.7% | Plastic | No | No | N/A. Full containers delivered to site and taken to point of application when required. Containers are fully sealed. | Ground water. No specific drainage | N/A. Full containers delivered to site. Empty containers replaced in situ. | Visual inspection | Unknown | Unknown | Contents pumped out | Number of containers may vary
377 | 19no. acid container storage | Acid. Unsure what type | 20 each | WPF (Chemical storage area adjacent to car park) | Plastic | Acid container storage bund | Yes | Yes (18no. Sodium hydroxide storage containers) | 1140 | N/A | 300% | Plastic | No | No | N/A. Full containers delivered to site and taken to point of application when required. Containers are fully sealed. | Ground water. No specific drainage | N/A. Full containers delivered to site. Empty containers replaced in situ. | Visual inspection | Unknown | Unknown | Contents pumped out | Number of containers may vary
378 | 32no. Ecolab P3-Ultrasil 110 containers | P3 Ultrasil 110 is an alkaline liquid detergent used for membrane filtration plants | 20 each | WPF (Chemical storage area adjacent to car park) | Plastic | Ecolab P3-Ultrasil container | Yes | Yes (other Ultrasil P3 containers) | 1100 | N/A | 171.9% | Plastic | No | No | N/A. Full containers delivered to site and taken to point of application when required. Containers are fully sealed. | Ground water. No specific drainage | N/A. Full containers delivered to site. Empty containers replaced in situ. | Visual inspection | Unknown | Unknown | Contents pumped out | Number of containers may vary
379 | 3no. Sulphuric acid containers | Sulphuric acid | 20 | WPF (Chemical storage area adjacent to car park) | Plastic | Urea IBC bund in chemical store | Yes | Yes (Urea IBC) | 1140 | N/A | 1900% | Plastic | No | No | N/A. Full containers delivered to site and taken to point of application when required. Containers are fully sealed. | Ground water. No specific drainage | N/A. Full containers delivered to site. Empty containers replaced in situ. | Visual inspection | Unknown | Visual inspection for the container. Bund maintenance schedule unknown. | Contents pumped out | Number of containers may vary
380 | Polymer IBC storage | 15no. Polymer IBCs (aquatreat N223F). | 1000 each | WPF (Chemical storage area adjacent to car park) | Plastic | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Concrete plinth that the IBCs stand on has no specific drainage or containment. Area of chippings/ compressed gravel surrounds the storage area. Any leak will go to ground. | N/A. Full IBCs delivered to site. | Visual inspection | N/A | N/A | N/A | Number of containers may vary
381 | Sulphuric acid IBC | 50% sulphuric acid solution | 1000 | WPF (Chemical storage area adjacent to car park) | Plastic | Sulphuric acid IBC bund in chemical store | Yes | No | 1100 | N/A | 110% | Plastic | No | No | N/A. Full IBCs delivered to site and taken to point of application when required. IBCs are fully sealed when delivered. | Ground water. No specific drainage | N/A. Full IBCs delivered to site. Empty IBCs replaced in situ. | Visual inspection | Unknown | Visual inspection for the IBC. Bund maintenance schedule unknown. | Contents pumped out | Number of containers may vary
382 | Unknown blue drums | Unknown | 210 each | WPF (Chemical storage area adjacent to car park) | Plastic | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A. Full containers delivered to site and taken to point of application when required. Containers are fully sealed. | Ground water. No specific drainage | N/A. Full drums delivered to site. Empty containers replaced in situ. | Visual inspection | Unknown | Unknown | Contents pumped out | Number of containers may vary
383 | Unknown IBC 1 | Unknown | 1000 | WPF (Chemical storage area adjacent to car park) | Plastic | Unknown IBC1 storage | Yes | Yes (1no. 120L container, 5no. 25L containers) | 1140 | N/A | 114% | Plastic | No | No | N/A. Full IBCs delivered to site and taken to point of application when required. IBCs are fully sealed when delivered. | Ground water. No specific drainage | N/A. Full IBCs delivered to site. Empty IBCs replaced in situ. | Visual inspection | Unknown | Unknown | Contents pumped out | Number of IBCs may vary
384 | Unknown IBC 3 | Unknown | 1000 | WPF (Chemical storage area adjacent to car park) | Plastic | Unknown IBC3 and 4 storage | Yes | Yes (Unknown IBC4) | 1140 | N/A | 114% | Plastic | No | No | N/A. Full IBCs delivered to site and taken to point of application when required. IBCs are fully sealed when delivered. | Ground water. No specific drainage | N/A. Full IBCs delivered to site. Empty IBCs replaced in situ. | Visual inspection | Unknown | Unknown | Contents pumped out | Number of IBCs may vary
385 | Unknown IBC 4 | Unknown | 1000 | WPF (Chemical storage area adjacent to car park) | Plastic | Unknown IBC3 and 4 storage | Yes | Yes (Unknown IBC3) | 1140 | N/A | 114% | Plastic | No | No | N/A. Full IBCs delivered to site and taken to point of application when required. IBCs are fully sealed when delivered. | Ground water. No specific drainage | N/A. Full IBCs delivered to site. Empty IBCs replaced in situ. | Visual inspection | Unknown | Unknown | Contents pumped out | Number of IBCs may vary
386 | Unknown IBC 5 | Unknown | 1000 | WPF (Chemical storage area adjacent to car park) | Plastic | Unknown IBC5 storage | Yes | No | 1110 | N/A | 111% | Plastic | No | No | N/A. Full IBCs delivered to site and taken to point of application when required. IBCs are fully sealed when delivered. | Ground water. No specific drainage | N/A. Full IBCs delivered to site. Empty IBCs replaced in situ. | Visual inspection | Unknown | Unknown | Contents pumped out | Number of IBCs may vary
387 | Unknown IBC 6 | Unknown | 1000 | WPF (Chemical storage area adjacent to car park) | Plastic | Unknown IBC6 storage | Yes | No | 1110 | N/A | 111% | Plastic | No | No | N/A. Full IBCs delivered to site and taken to point of application when required. IBCs are fully sealed when delivered. | Ground water. No specific drainage | N/A. Full IBCs delivered to site. Empty IBCs replaced in situ. | Visual inspection | Unknown | Unknown | Contents pumped out | Number of IBCs may vary
388 | Unknown IBC 7 | Unknown | 1000 | WPF (Chemical storage area adjacent to car park) | Plastic | Unknown IBC7 and 8 storage | Yes | Yes (Unknown IBC8) | 1140 | N/A | 114% | Plastic | No | No | N/A. Full IBCs delivered to site and taken to point of application when required. IBCs are fully sealed when delivered. | Ground water. No specific drainage | N/A. Full IBCs delivered to site. Empty IBCs replaced in situ. | Visual inspection | Unknown | Unknown | Contents pumped out | Number of IBCs may vary
389 | Unknown IBC 8 | Unknown | 1000 | WPF (Chemical storage area adjacent to car park) | Plastic | Unknown IBC7 and 8 storage | Yes | Yes (Unknown IBC7) | 1140 | N/A | 114% | Plastic | No | No | N/A. Full IBCs delivered to site and taken to point of application when required. IBCs are fully sealed when delivered. | Ground water. No specific drainage | N/A. Full IBCs delivered to site. Empty IBCs replaced in situ. | Visual inspection | Unknown | Unknown | Contents pumped out | Number of IBCs may vary
390 | Unknown IBC2 | Unknown | 1000 | WPF (Chemical storage area adjacent to car park) | Plastic | Unknown IBC2 storage | Yes | No | 1110 | N/A | 111% | Plastic | No | No | N/A. Full IBCs delivered to site and taken to point of application when required. IBCs are fully sealed when delivered. | Ground water. No specific drainage | N/A. Full IBCs delivered to site. Empty IBCs replaced in situ. | Visual inspection | Unknown | Unknown | Contents pumped out | Number of IBCs may vary
391 | Urea IBC | 50% urea solution | 1000 | WPF (Chemical storage area adjacent to car park) | Plastic | Urea IBC bund in chemical store | Yes | Yes (3no. Sulphuric acid containers) | 1140 | N/A | 114% | Plastic | No | No | N/A. Full IBCs delivered to site and taken to point of application when required. IBCs are fully sealed when delivered. | Ground water. No specific drainage | N/A. Full IBCs delivered to site. Empty IBCs replaced in situ. | Visual inspection | Unknown | Visual inspection for the IBC. Bund maintenance schedule unknown. | Contents pumped out | Number of IBCs may vary
392 | T003 (RO Shipping container room) | Unknown |  | WPF: WPF (End shipping container); GRP: Plastic; N/A: N/A; No: Yes; N/A: No; N/A: TBC
393 | Dewatering tank 1 (redundant) | Rainwater. Not in use | TBC | WPF (over sludge pit) | Glass coated steel | N/A | No | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A (not in use) | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage between tank and the lower end of site could intercept any leakages and return to the head of the works. | N/A | Visual inspection | N/A | Visual inspection. Site walk overs. No bund inspection | Not in use
394 | Dewatering tank 2 (redundant) | Rainwater. Not in use | TBC | WPF (over sludge pit) | Glass coated steel | N/A | No | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A (not in use) | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage between tank and the lower end of site could intercept any leakages and return to the head of the works. | N/A | Visual inspection | N/A | Visual inspection. Site walk overs. No bund inspection | Not in use
395 | Genesol 38 storage | 12no, Genesol 38 containers (inorganic scale cleaner and iron deposit remover from RO membranes) | 20 each | WPF (Red shipping container within chemical store adjacent to the car park) | Plastic | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A. Full containers delivered to site. Empty container replaced in situ. | Ground water. No specific drainage | N/A. Full containers delivered to site. Empty container replaced in situ. | None | N/A | Visual inspection. Site walk overs. No bund inspection | N/A | Number and type of containers within the shipping container accurate at the time of the survey.
396 | Genesol 40 storage | 7no. Genesol 40 containers (Alkaline membrane cleaner) | 20 each | WPF (Red shipping container within chemical store adjacent to the car park) | Plastic | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A. Full containers delivered to site. Empty container replaced in situ. | Ground water. No specific drainage | N/A. Full containers delivered to site. Empty container replaced in situ. | None | N/A | Visual inspection. Site walk overs. No bund inspection | N/A | Number and type of containers within the shipping container accurate at the time of the survey.
397 | GOS storage | Approx. 25 20L GOS containers | 20 each | WPF (Red shipping container within chemical store adjacent to the car park) | Plastic | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A. Full containers delivered to site. Empty container replaced in situ. | Ground water. No specific drainage | N/A. Full containers delivered to site. Empty container replaced in situ. | None | N/A | Visual inspection. Site walk overs. No bund inspection | N/A | Number and type of containers within the shipping container accurate at the time of the survey.
398 | Wehrle AC10 storage | Wehrle AC10 | 20 each | WPF (Red shipping container within chemical store adjacent to the car park) | Plastic | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A. Full containers delivered to site. Empty container replaced in situ. | Ground water. No specific drainage | N/A. Full containers delivered to site. Empty container replaced in situ. | None | N/A | Visual inspection. Site walk overs. No bund inspection | N/A | Number and type of containers within the shipping container accurate at the time of the survey.
399 | Wehrle AC11 storage | Wehrle AC11 | 20 each | WPF (Red shipping container within chemical store adjacent to the car park) | Plastic | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A. Full containers delivered to site. Empty container replaced in situ. | Ground water. No specific drainage | N/A. Full containers delivered to site. Empty container replaced in situ. | None | N/A | Visual inspection. Site walk overs. No bund inspection | N/A | Number and type of containers within the shipping container accurate at the time of the survey.
400 | Citric Acid Day Bin | Citric Acid | 300 | WPF (Shipping Containers) | Plastic | Citric acid day bin bund | Yes | No | 321.6 | 0.67m x 0.67m x 0.8m | 107.2% | Plastic | Unknown | No | Unknown. Unknown whether tanks are manually filled or filled from bulk storage containers automatically. | Drainage within the day bin building will return contents to the head of the works. All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage between tank and the lower end of site could intercept any leakages and return to the head of the works. | TBC. If manually filled, any drips will be contained within the tank bund. | Unknown | Unknown | Unknown | Contents pumped out
401 | Ferric Chloride Day Bin | Ferric Chloride | 300 | WPF (Shipping Containers) | Plastic | Ferric chloride day bin | Yes | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A (not in use) | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage between tank and the lower end of site could intercept any leakages and return to the head of the works. | N/A | Visual inspection | N/A | Visual inspection. Site walk overs. No bund inspection | Not in use
402 | Polymer Day Bin | Polymer | 300 | WPF (Shipping Containers) | Plastic | Polymer day bin bund | Yes | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A (not in use) | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage between tank and the lower end of site could intercept any leakages and return to the head of the works. | N/A | Visual inspection | N/A | Visual inspection. Site walk overs. No bund inspection | Not in use
403 | RO Antiscale Day Bin | Antiscale | 300 | WPF (Shipping Containers) | Plastic | RO antiscale day bin | Yes | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A (not in use) | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage between tank and the lower end of site could intercept any leakages and return to the head of the works. | N/A | Visual inspection | N/A | Visual inspection. Site walk overs. No bund inspection | Not in use
404 | RO SMBS Day Bin | Sodium metabisulphate | 300 | WPF (Shipping Containers) | Plastic | RO SMBS day bin bund | Yes | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A (not in use) | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage between tank and the lower end of site could intercept any leakages and return to the head of the works. | N/A | Visual inspection | N/A | Visual inspection. Site walk overs. No bund inspection | Not in use
405 | RO Sodium hydroxide day bin | Sodium Hydroxide | 300 | WPF (Shipping Containers) | Plastic | RO Sodium hydroxide day bin | Yes | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A (not in use) | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage between tank and the lower end of site could intercept any leakages and return to the head of the works. | N/A | Visual inspection | N/A | Visual inspection. Site walk overs. No bund inspection | Not in use
406 | RO Sodium hypochlorite Day Bin | Hypochlorite | 300 | WPF (Shipping Containers) | Plastic | RO sodium hypochlorite day bin bund | Yes | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A (not in use) | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage between tank and the lower end of site could intercept any leakages and return to the head of the works. | N/A | Visual inspection | N/A | Visual inspection. Site walk overs. No bund inspection | Not in use
407 | Sulphuric acid day bin | Sulphuric acid | 300 | WPF (Shipping Containers) | Plastic | RO sulphuric acid day bin | Yes | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A (not in use) | All drains to the lowest point on the WPF. Wall surrounding the site contains any leaks. Site drainage between tank and the lower end of site could intercept any leakages and return to the head of the works. | N/A | Visual inspection | N/A | Visual inspection. Site walk overs. No bund inspection | Not in use
Note on I4: Registered User: If tank is not bunded, please give details of tertiary containment provided
Note on P4: Collett, Simon: Reconfirm in site visit
Note on K6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: From website.
Note on M6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual storage is 55% (110%/2) as this bund is shared with another IBC.
Note on K7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: From website.
Note on M7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual storage is 55% (110%/2) as this bund is shared with another IBC.
Note on K8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: From website.
Note on M8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual storage is 55% (110%/2) as this bund is shared with another IBC.
Note on K9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: From website.
Note on M9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual storage is 110%/2 as this bund is shared with another IBC. At time of visit, only one IBC was stored here.
Note on K10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: From website.
Note on M10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual storage is 110%/2 as this bund is shared with another IBC.
Note on K11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: From website.
Note on M11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual storage is 110%/2 as this bund is shared with another IBC.
Note on K12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: From website.
Note on M12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual storage is 110%/2 as this bund is shared with another IBC.
Note on K13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Capacity taken from supplier website (Romold)
Note on K14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Capacity taken from supplier website (Romold)
Note on K15: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Capacity taken from supplier website (Romold)
Note on K16: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Capacity taken from supplier website (Romold)
Note on M20: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bund shared with other kerosene tank. Actual storage = 82%
Note on M21: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bund shared with other kerosene tank. Actual storage = 82%
Note on M26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total volume of bund. Actual capacity is smaller because the base of the tank sits on legs within the bund. Depth and impact on the bund capacity unknown.
Note on M27: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total volume of bund. Actual capacity is smaller because the base of the tank sits on legs within the bund. Depth unknown.
Note on T35: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Level instrumentation back to SCADA?
Note on T36: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Level instrumentation back to SCADA?
Note on J41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Worth mentioning the vessels are drained
Note on M54: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual bund storage is 48% as the bund is shared with the Horolith SD IBC
Note on M56: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual bund storage is 48% as the bund is shared with the Ansep IBC
Note on M81: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Shared bund. Actually bund capacity is 58%
Note on M82: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Shared bund. Actually bund capacity is 58%
Note on E87: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Assuming a capacity of 40T at a density of 3.34 g/cm3
Note on K92: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: From supplier website
Note on M92: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual storage capacity = 57%. Bund is shared with another IBC.
Note on K150: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: From supplier website.
Note on K190: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: From supplier website
Note on K191: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: From supplier website
Note on K192: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: From supplier website
Note on K193: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tertiary containment contained within the bund shared with Tank 82
Note on K194: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bund volume adjusted to accomodate tank volume that sits within the bund.
Note on M194: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual bund capacity os 36% as the bund is shared with other tanks
Note on M195: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual bund capacity is 48% as the bund is shared with Tank 73
Note on K196: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bund volume adjusted to accomodate tank volume that sits within the bund.
Note on M196: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual bund capacity os 36% as the bund is shared with other tanks
Note on K203: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bund capacity adjusted to accomodate the base of the tanks that share this bund. Milk silo diameter = 5m (from google maps). Skimmed milk silos = 4m diameter (from google maps)
Note on M203: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual bund capacity <1% when all tanks within the shared bund are included in the calculations
Note on K204: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bund capacity adjusted to accomodate the base of the tanks that share this bund. Milk silo diameter = 5m (from google maps). Skimmed milk silos = 4m diameter (from google maps)
Note on M204: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual bund capacity <1% when all tanks within the shared bund are included in the calculations
Note on K205: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bund capacity adjusted to accomodate the base of the tanks that share this bund. Milk silo diameter = 5m (from google maps). Skimmed milk silos = 4m diameter (from google maps)
Note on M205: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual bund capacity <1% when all tanks within the shared bund are included in the calculations
Note on K206: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bund capacity adjusted to accomodate the base of the tanks that share this bund. Milk silo diameter = 5m (from google maps). Skimmed milk silos = 4m diameter (from google maps)
Note on M206: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual bund capacity <1% when all tanks within the shared bund are included in the calculations
Note on K207: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Removes the volume of the bund occupied by the base of the tanks within the bund.
Note on M207: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual bund volume is 1% when the capacity of all tanks is included in the calculation.
Note on K208: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Removes the volume of the bund occupied by the base of the tanks within the bund.
Note on M208: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual bund volume is 1% when the capacity of all tanks is included in the calculation.
Note on K209: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Removes the volume of the bund occupied by the base of the tanks within the bund.
Note on M209: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual bund volume is 1% when the capacity of all tanks is included in the calculation.
Note on K210: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Removes the volume of the bund occupied by the base of the tanks within the bund.
Note on M210: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual bund volume is 1% when the capacity of all tanks is included in the calculation.
Note on K211: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Removes the volume of the bund occupied by the base of the tanks within the bund.
Note on K212: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Removes the volume of the bund occupied by the base of the tanks within the bund.
Note on M213: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual bund capacity is 3.6% when all tanks within the bund are used in the calculations.
Note on K230: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bund capacity adjusted to accomodate the base of the tanks that share this bund. Milk silo diameter = 5m (from google maps). Skimmed milk silos = 4m diameter (from google maps)
Note on K231: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bund capacity adjusted to accomodate the base of the tanks that share this bund. Milk silo diameter = 5m (from google maps). Skimmed milk silos = 4m diameter (from google maps)
Note on E240: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total tank volume. Working volume unknown.
Note on F241: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Different to Whey CIP 4?
Note on K256: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tank sits at the base of the bund. Tank diameter is 4.4m, and the volume of the bund it occupies has been used to calculate bund capacity.
Note on M256: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual bund capacity is 2% when all tanks used in the bund are included in the calculation
Note on K257: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tank sits at the base of the bund. Tank diameter is 4.4m, and the volume of the bund it occupies has been used to calculate bund capacity.
Note on M257: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual bund capacity is 2% when all tanks used in the bund are included in the calculation
Note on K258: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tank sits at the base of the bund. Tank diameter is 4.4m, and the volume of the bund it occupies has been used to calculate bund capacity.
Note on M258: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual bund capacity is 2% when all tanks within the tank bund are unsed in the calculation.
Note on K259: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tank sits at the base of the bund. Tank diameter is 4.4m, and the volume of the bund it occupies has been used to calculate bund capacity.
Note on M259: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual bund capacity is 2% when all tanks within the tank bund are unsed in the calculation.
Note on K267: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tanks sit within the bund. Volume the tanks occupy has been removed from the total bund volume. Tank diameter = 4m
Note on M267: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Only half tof 0.03% as tank 411 is shared with tank 412 and 497 Reply: Actual capacity is 1.5% when all other tanks within the shared bund are considered in the calculation
Note on K268: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tanks sit within the bund. Volume the tanks occupy has been removed from the total bund volume. Tank diameter = 4m
Note on M268: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Only half tof 0.03% as tank 411 is shared with tank 412 and 497 Reply: Actual capacity is 1.5% when all other tanks within the shared bund are considered in the calculation
Note on K269: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bund area taken from google maps
Note on K270: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bund area taken from google maps. Tanks sit on base of the bund, therefore has been removed from the volume.
Note on M270: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual bund capacity is 3% when all tanks within the shared bund are considered
Note on K271: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bund area taken from google maps. Tanks sit on base of the bund, therefore has been removed from the volume.
Note on M271: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual bund capacity is 3% when all tanks within the shared bund are considered
Note on K272: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bund area taken from google maps. Tanks sit on base of the bund, therefore has been removed from the volume.
Note on M272: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual bund capacity is 3% when all tanks within the shared bund are considered
Note on K273: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tanks sit within the bund. Volume the tanks occupy has been removed from the total bund volume. Tank diameter = 4m
Note on M273: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bund capacity shared with 412 and 411
Note on M284: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual bund capacity is 57% (shared with Ferric chloride IBC for AT2)
Note on E285: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tank within a sealed cabinet. Estimation of tank diameter and height as it was unsafe to open cabinet with equipment still live.
Note on T288: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Possibly process instrumentation if available (flow meters or level monitors further downstream). Unlikely to have level instrumentation in the tank.
Note on M290: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual bund capacity is 57% (shared with anitifoam IBC)
Note on C305: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: AW Ultima trailer
Note on C312: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Couldn't safely access to inspect properly
Note on E322: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: From supplier (Siltbuster) website
Note on E323: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: From supplier
Note on M328: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Shared bund. Actually bund capacity is 58%
Note on M330: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Shared bund. Actually bund capacity is 58%
Note on K333: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: From supplier website
Note on M333: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual bund capacity is 38% for all three tanks.
Note on M356: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Capacity if one container fails. If two containmers fail, bund capacity becomes 80% of tank volume.
Note on E358: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Diameter = 16m. Approx. 3m high, unknown cone depth.
Note on K358: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Deep channel around the settlement tank. 0.43m wide and 0.65m deep.
Note on Q358: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Distance between coping level and weir level is unknown
Note on E360: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Diameter is 17.7m
Note on Q360: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Distance between coping level and weir level is unknown
Note on Q362: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Distance between coping level and weir level is unknown
Note on Q365: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Unknown if pumped flow or flow via gravity.
Note on Q366: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Unknown if pumped flow or flow via gravity.
Note on Q367: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Unknown if pumped flow or flow via gravity.
Note on I369: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changed from double bunded. Overflow pipework on the tank and external bund.
Note on M375: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual bund capacity is 57% (bund shared with another Ultrachlor 15 IBC)
Note on M376: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual bund capacity is 57% (bund shared with another Ultrachlor 15 IBC)
Note on M381: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual storage is 158% as it is shared with acid containers. Volume is for total number of containers.
Note on M382: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual storage is 158% as it is shared with acid containers. Volume is for total number of containers.
Note on M383: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual storage is 158% as it is shared with acid containers. Volume is for total number of containers.
Note on M385: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual percentage = 108% when shared with Urea IBC
Note on M389: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not including the volume of the container drums
Note on M390: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual capacity is 57% as the bund is shared by 2 IBCs
Note on M391: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual capacity is 57% as the bund is shared by 2 IBCs
Note on M394: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual capacity is 57% as the bund is shared by 2 IBCs
Note on M395: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual capacity is 57% as the bund is shared by 2 IBCs
Note on M397: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual percentage = 108% when shared with sulphuric acid containers
Note on D408: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Type of polymer unknown