| Serial No: |  | FLT/EA/004 |  | Date of Entry: |  | 6/11/18 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| A |  | B |  | C |  | D |  |  |
| Probability of a significant Environment Impact |  | Potential Consequence |  | Resultant Impact |  | Legal Consequence |  |  |
| 1 - 6 | 3 | 1 - 6 | 5 | 1 - 6 | 4 | 1 - 6 |  | 5 |
| Environmental Risk Score Emergency Conditions A x B x C x D = |  |  |  |  | 300 |  |  |  |
| 1 – 6 | 3 | 1 – 6 | 3 | 1 – 6 | 3 | 1 – 6 | 5 |  |
| Environmental Risk Score Routine Conditions A x B x C x D = |  |  |  |  | 135 |  |  |  |
| Responsible Business Unit: |  |  |  | Engine Services |  |  |  |  |
| Line Manager/Process Supervisor |  |  |  | Repair Manager |  |  |  |  |
| Description of Activity, Process, Operation, Equipment |  |  |  | Engines Cleaning Bay discharge to sewer (Foul and Surface Water) and soil |  |  |  |  |
| Description of Potential or Actual Environmental Effects: |  |  |  | Loss of containment from cleaning bay chemical tanks results in an unlawful discharge to sewer or permeation through hard standing to soil. |  |  |  |  |
|  |  |  |  | Loss of containment of hazardous chemical and non-hazardous rinse water within pipework routing to the tank farm and the effluent treatment plant respectively leads to an unlawful discharge to sewer or soil. |  |  |  |  |
|  |  |  |  | A loss of containment during chemical transport and decanting/ transfer results in an unlawful discharge to sewer or soil. |  |  |  |  |
|  |  |  |  | A loss of containment of scrubber effluent from the three scrubber liquid reservoirs results in a discharge of chemical effluent to drain and soil. |  |  |  |  |
| Statutory Licenses, Consents, Agreements and Exemption Certificates required and Applicable conditions |  |  |  | Southern Water consent to the discharge of trade effluent (723611702). |  |  |  |  |
|  |  |  |  | EA Permit EPR/NP/3930KB |  |  |  |  |
| Legislative Reference(s) applicable: |  |  |  | Pollution Prevention and Control Act 1999 |  |  |  |  |
|  |  |  |  | Environmental Permitting (England and Wales) Regulations 2016 |  |  |  |  |
|  |  |  |  | Water Industry Act 1991 |  |  |  |  |
|  |  |  |  | Environmental Protection Act 1990 |  |  |  |  |
|  |  |  |  | Environment Act 1995 |  |  |  |  |
|  |  |  |  | Hazardous Waste Regulations 2005 |  |  |  |  |
|  |  |  |  | Control Of Substances Hazardous to Health Regulations 2002 |  |  |  |  |
|  |  |  |  | Health & Safety at Work Act 1974 |  |  |  |  |
| Serial Numbers of Associated Register Entries |  |  |  |  |  |  |  |  |
| Additional Information / Notes (Control measures in place) ((Separate) Additional control measures) |  |  |  | Clean Bay EPR 2016 schedule 1, 2.3 activity, surface treatment of metal parts. Engine parts are submerged within tanks containing various acid, alkaline and chromate solutions for the purpose of cleaning and temporary surface protection. Spent chemical solution is routed to the tank farm adjacent to the Effluent Treatment Plant, via double skinned pipes, and stored within double skinned tanks in preparation for off haul disposal as hazardous waste by a licenced waste contractor. All tanks within the cleaning bay are stored within secondary containment comprising a floor bund and segregated sumps. Post chemical treatment, the parts are submerged in hot or cold water tanks for the purpose of removing chemical residues and drying. Rinse water from these tanks is routed to a sump and then to the Effluent Treatment Plant by double skinned pipework. Pipework is routed within a concrete lined trench which is gravity fed back into a sump where practicable. All bulk chemical (IBC’s and 205l drums) is stored within area 99 within designated chem lockers, providing secondary containment greater than 110% of the largest container stored. Spill kits are provided within the cleaning bay area. The site has established an emergency response plan, that includes spill response in the event of a loss of containment. All employees are trained in the requirements of spill control and emergency procedures upon induction and periodically thereafter. Where practicable, bulk storage containers are stored in close proximity to chemical process areas to minimise transport distances and handling times. Bulk chemicals stored within the cleaning bay for production use (i.e. 25l containers) are sited on a bund which is greater than 110% Chemical vapour from the clean bay chemical tanks is removed from the workplace by LEV systems, the vapour is routed to one of three scrubbers at the rear of 110. The scrubber liquid reservoir contains concentrated chemical residues. A loss of containment from the liquid reservoir could lead to an unlawful discharge to foul and/or surface water drain. The scrubber liquid reservoirs are sited within bunds that are sufficient to hold greater than 110% of the liquid stored within the reservoir. Liquid within the bund is pumped to the sump containing effluent from the general line. |  |  |  |  |

| Opportunities to reduce Environmental Impact |  |
| --- | --- |
| Scale of environmental impact | To review the maintenance and inspection requirements for pollution prevention and control equipment. Review BAT Assessment for Cleaning Bay EPR 2016 schedule 1, 2.3 activity |
| Population growth |  |
| Source of raw material |  |
| Energy supplies |  |
| Emissions of CO2 |  |
| Air pollution & damage to ozone |  |
| Water resources |  |
| Land issues |  |
| Loss of bio-diversity |  |
| Sustainability |  |