	South Coast Waste Holdings Limited

	Fire Prevention Plan
January 2026
Version 2.0


	Ackworth Road

Hilsea

Portsmouth

PO3 5NS




Document Control Sheet

	Version Reference
	Date
	Reason for Change
	Issued by

	1.0
	29/09/25
	Initial Draft
	PD

	2.0
	24/02/26
	Not Duly Made
	PD

	Approved by 
	Nick Williams


CONTENTS
41
Introduction


41.1
Roles and Responsibilities


41.2
Purpose


41.3
Scope


41.4
Liaison with Fire Rescue Service (FRS)


41.5
General considerations


52
Causes of Fire


63
Fire Prevention Plan


63.1
Site Plan and Receptors


63.2
Material Receipt and Storage


83.3
Signage


83.4
Training, Awareness and Visitors


83.5
Security


93.6
Planned Preventative Maintenance


93.7
Self Combustion


93.8
Hot Works


103.9
Mechanical Treatment


103.10
Hot Exhausts


103.11
Additional Actions


114
Fire Detection and Management


114.1
Fire Detection


124.2
Fire Fighting Strategy


134.3
Managing Fire Water


155
Annex A: Site Layout


176
Annex B: Site Drainage


187
Annex C: Fire Fighting Access, Equipment & Water Supply Plan


198
Annex D: Key Receptors


209
Annex E: Waste Acceptance Procedures


2110
Annex F: Fire Risk Checks Form for Fire Prevention


2211
Annex G: Emergency Contacts


2312
Annex H: EMS Documents




1 Introduction 
1.1 Roles and Responsibilities

The Site Manager Nick Williams has responsibility for ensuring these procedures are adhered to.  The Site Manager is specifically responsible for:

· Ensuring the adequate training of staff and contractors working on site regarding the content of these procedures;

· Ensuring the adequate provision of resources such as personal protective equipment (PPE);
· Ensuring the provision and maintenance of hand-held fire extinguishers and other fire fighting equipment at the site is adequate.

1.2 Purpose
The primary purpose of this Fire Prevention Plan (FPP) is to guide staff and contractors in the prevention of fire for South Coast Waste Limited.  This FPP also confirms the actions to be taken in the event of fire in order to minimise any impact on the environment and to control the fire where appropriate.  This FPP is to support a bespoke environmental permit application at PO3 5NS.
This FPP will be issued to the Fire Brigade in the event of a fire to aid with fire fighting.
1.3 Scope 

This FPP has been prepared in accordance with Environment Agency guidance.
   
In addition, all fire prevention measures will meet the stringent insurance requirements for the business.
Annex A shows a site layout plan.
1.4 Liaison with Fire Rescue Service (FRS)

The FRS will be provided a copy of this FPP in advance of commencing operations.
1.5 General considerations

The site is located at Ackworth Road, Hilsea, Portsmouth,PO3 5NS.
The site is approximately 0.072 Ha and lies on an industrial estate approx. 2Km north east of Portsmouth Town Centre south of the A27. At the time of writing this FPP, the site currently consists of an enclosed warehouse unit where inert materials sorting & recycling is proposed to take place and a picking station with conveyor.
The surrounding land use is a mix of light industrial & commercial.
South Coast Waste Limited operate under an existing Environmental Management System [EMS] which identifies the potential sources of pollution from site activities and controls site operations to eradicate emissions or where that is not possible to minimise their effect on human and environmental health.

This Fire Prevention Plan [FPP] forms part of the EMS.

The individual fire emergency procedures for each part of the site form part of the FPP.
The site has sealed drainage and as the recycling operation is within a sealed drainage system. There is no runoff to foul or surface water from the process. See Annex B Site Drainage. There is no waste storage internally within the building. 
SC Waste Holdings Ltd wish to operate a waste treatment facility which predominantly sorts commercial & household non hazardous waste. The facility consists of a warehouse for tipping skip waste and a picking station for manual separation. Sorted waste is subsequently stored in concrete firebays externally. There is a trommel and picking station. No other treatment occurs at the site.
The site is bounded by 5m high walls and consists of a concrete impermeable surface. Sorting bays inside the warehouse are also concrete firebays. Treatment consisting only of sorting, & grading. 

Waste accepted per year will not exceed 75,000 tonnes.

Waste Codes Required on the permit.

20 01 01 
paper and cardboard 
20 01 02 
glass 
20 01 10 
clothes 
20 01 11 
textiles 
20 01 38 
wood other than that mentioned in 20 01 37 
20 01 39 
plastics 
20 01 40 
metals 
170407 
mixed metals  

191202 
ferrous metal 
191203 
non-ferrous metal 
15 01 06 
mixed packaging 
170407 
Mixed metals 
17 04 11 
Cables other than those mentioned in 17 04 10 
17 05 
soil 
17 05 04 
Soil and stones other than those mentioned in 17 05 03 
17 05 08 
Track ballast other than those mentioned in 17 05 07 
17 09 
Other construction and demolition wastes 
17 09 04 
Mixed construction and demolition wastes other than those mentioned in 17 09 01,17 09 02 and 17 09 03 
170101 
concrete 
170102 
bricks 
170103 
Tiles and ceramics 
17 01 07 
Mixtures of concrete,bricks,tilesand ceramics other than those mentioned in 17 01 06 
17 02 
Wood,glass,plastic
17 02 01 
wood 
2 Causes of Fire
The following have been identified as potential causes of fire and their relevance to this site, when operational, is given in Table 1 
	Table 1 Causes of Fire and Applicability to the South Coast Site

	Cause of Fire
	Applicability to the South Coast Waste Site

	· Arson or vandalism
	Yes – see section 3.5 Security

	· Self-combustion
	No  – see 3.7 Self Combustion

	· Naked lights
	No – none on site 

	· Plant or equipment failure
	Yes – see  3.6 Planned Preventative Maintenance

	· Electrical faults
	No – none on site - occasional

	· Discarded smoking materials
	No – on site smoking is prohibited

	· Hot works
	No – see 3.8 Hot works

	· Hot exhausts
	No  – see 3.10 Hot exhausts

	· Industrial heater
	No – none on site

	· Open burning (adjacent to site)
	No – no likely sources of burning adjacent to site 

	· Damaged or exposed electrical cables
	No – no live cables on the site or to be introduced

	· Reactions between incompatible materials
	Not relevant given the waste types

	· Neighbouring site activities
	No – no likely sources of risk from neighbouring land use

	· Sparks from loading buckets
	No – No loading buckets.

	· Hot loads deposited at the site
	No – not a risk given the types of materials and sources of materials.  


Mitigation measures in relation to these activities, where under control of South Coast Waste Limited, are set out in this FPP.
3 Fire Prevention Plan
South Coast Waste Limited recognises that the risk of fire cannot be eliminated.  However, the site will be operated in accordance with a robust management system.  Operational Procedures are listed in the site’s EMS Manual Section 1.6 ‘Operational Control’. 
In addition to Operational Procedures, the following reasonable actions will be taken to minimise the risk of fire, in accordance with Environment Agency guidelines. 

3.1 Site Plan and Receptors
A Site Plan is given in Annex A showing the key features of the site relevant to the Fire Prevention Plan including site access, security, vehicle parking, materials storage, drainage and buildings. Annex C is a Fire Fighting Equipment plan including the location of booms extinguishers etc.

A map showing key receptors within 1 km of the site is in Annex D.

3.2 Material Receipt and Storage
Waste will be collected using the company’s vehicles which will be removed from the customer’s site and returned to site. Raw material (mixed skip waste) are emptied into a sorting bay in the building. Sorted waste is then removed to the firebays in the yard.  
Waste acceptance procedures will be followed as set out in Annex E.  
Only the waste types and EWC codes named on the environmental permit will be accepted at the site. Wastes entering the site will be inspected and registered at the site. Non-compliant waste materials not allowed on the permit will be turned away from the site. A record will be made in the site diary.
 
3.2.1 Quarantine area
The site plan shows the Fire Quarantine Area.  The Fire Quarantine firebay will always be kept clear in case of emergency.  The area is located close to a water supply for quenching burning or smouldering material. 
The Fire Quarantine Area is a dedicated emergency or quarantine area with a clear area of 6m around it.   The rationale for this area is:
· The area is required to be kept clear, at all times, for access.

· Only small quantities of material would ever be put in this site i.e. those that can be dealt with safely by the staff on the site.  Larger fire would be dealt with by the FRS. 
· The quarantine area is 3.5m x3.5m x3.5m (42.8 CUMEC) and can accommodate at least 50% of the largest waste pile (Firebay 4- 60 CUMEC). See appendix A.
· In the event of a fire or observed self-combustion, burning waste, if safe to do so, will be moved to the Fire Quarantine Area.  

· The Fire Quarantine Area is signposted.
· Hot loads can be quarantined in this area until such times that they can be stored safely.  

· The quarantine area, when made safe, will be emptied immediately. Should it be necessary to moves wastes to an alternative site then a local permitted site will be used.
3.2.2 Waste storage times

Minimal volumes of wastes will be stored on site for a maximum of 2-3 weeks. No other waste is stored in this building overnight with regular collections of waste offsite. Consideration is given to the likely dry nature of the material and the implications this has for self-combustion.  See 3.2.3 (stock rotation and management).
South Coast Waste Limited has key customers for each material. In addition, contingency customers are in place in case of a need to move material off site when the regular customer is not able to receive it.  In this way, the stock will not build up to levels over the permitted limits.

3.2.3 Stock rotation and management

Given the limited storage time on site – max 2-3 weeks – stock rotation not deemed necessary, however;
The company will, if necessary, undertake monthly stock checks which will involve moving the waste within each pile.  The purpose of the stock check is:

· To turn wastes in order to ensure the waste is not at risk of self-combustion and any potential hotspots are dissipated;

· To ensure the waste volumes do not exceed those specified in the permit. 
· To ensure waste is not kept on site for longer than allowed by the permit
Records will be maintained in the site office of the physical monthly stock checks.
The site manager in charge of stock checking will be vigilant for signs of combustion or hotspots.  If any are found, these will immediately be quenched with water and reported to the management team. Stock rotation will be by mechanical means as necessary.
Waste will follow the first in/first out principle as detailed in Annex F points 10/11/12.
3.2.4 Waste storage 

Waste will be stored in the firebays internally or internally in the sorting bay whilst it is being sorted.  Waste is not stored in the building overnight. The main piles are (these are all indicated on the site plan)
Within Warehouse
Sorting bays 1& 2 – no waste stored in the bay overnight. 3mx3mx4m each.
Waste is tipped and sorted here manually before being stored in the external firebays. Some waste may go through the picking station.

Firebays 3-5 all 5m W x 3m D x 4m H = 60 Cubic M with 1m freeboard observed in each.
3= Wood

4= Plastics

5= Paper/cardboard
Firebays 6-9 all 3mx3mx4m = 36 Cubic M.

6=Mixed metals

7=Mixed C&D Waste
8=Glass
9=Cables
· Total volumes: No more than 1000t at any one time
Firebay construction.
[image: image1.emf]


   
   



 
 
 
 
 



 
 



 
 
 
 
 
 
 
 
 
 
 
 
 
 
 
 
 
 
 



1.  INTRODUCTION 
 
A. Jansen Beton BV supplies concrete blocks referred to as ‘Legioblock’. The Legioblocks 
are stacked to produce fire-resisting retaining walls when storing combustible materials such 
as timber and tyres in the open air. Since legislation and regulations in the area of fire safety 
must be met, an investigation was performed. This report provides details of said 
investigation.  
 



20110645.R01b 
 
Retaining walls with Legioblock concrete blocks 
Fire resistance investigation (situations without a roof construction) 
 
 Date: 16 February 2012 



 
T H E  E N V I R O N M E N T ,  N O I S E ,  B U I L D I N G  C O N S U L T A N C Y  S E R V I C E S ,  F I R E  S A F E T Y ,  S P A T I A L  P L A N N I N G ,              
P O L I C Y  C O N S U L T A N C Y  S E R V I C E S  
 











3.3 Signage

Signage will be positioned throughout the facility showing Fire Exits and the position of extinguishers and other relevant fire fighting equipment. 

All waste storage areas will be clearly marked to ensure waste throughput timescales are adhered to.

South Coast Waste Limited will reinforce fire prevention messages using signs with key messages for staff.

3.4 Training, Awareness and Visitors

All staff and contractors working on-site will be aware and understand the contents of this FPP and the site Fire Response Plan.  Through site inductions and on-going staff awareness and training, SC Waste will ensure that all relevant staff and contractors will:

· Understand what they must do during a fire.

· Know where the fire prevention plan is kept

· Participate in regular exercises to test how well this FPP plan works and to confirm staff understand what to do.

For visitors to the site:

· They will be escorted at all times and signed in.
· They will understand the No Smoking policy for the site.
· When signing in, information on the fire exits and muster point will be provided. 
Training records are maintained as required by the site EMS.
Staff will be required to undergo regular fire training as part of the WAMITAB competency requirements. In addition, regular drills (annually) will be undertaken where desktop scenarios are played out and staff will be required to become familiar with this FPP as part of their ongoing competence. Mr Nick Williams will be responsible for implementing this plan and detailing annual tests and drills.

3.5 Security

The following security features will reduce fire risks from vandalism and deliberate arson through preventing access to the site by unauthorised people:

· Warehouse & doors are closed and locked outside of office hours to block access further.

· Regular checks of the Perimeter fencing and gates to the premises.

·  Only one entrance/ exit point to the site to/ from the public highway is in place, which is secured by means of lockable doors to be locked shut at any time the site is left unattended.
· CCTV which can be viewed remotely by the management team covering the whole of the permitted area
· A CCTV system with 24 motion detection & heat detection is employed for nigh time security. This sends alerts to all staff of SC Waste and would notify the owner if a fire were to break out during out of hours. See Annex C for location of CCTV cameras.
3.6 Planned Preventative Maintenance

The site has a Planned Preventative Maintenance Programme to ensure all machinery and components continue to remain effective.

There is a programme of routine planned maintenance is for each item of plant and machinery to manufacturers specifications, as well as the processing equipment in order to prevent breakdown and faults which may pose a fire risk.
Limited Electrical equipment including CCTV, lights & rigs will be used at the site. A PAT certificate will be provided to demonstrate that this equipment has been checked by a qualified electrician. A PPM schedule and maintenance contract will be in place to ensure that electrical equipment & plant is fit for purpose and to minimise the risk of ignition sources.
All faults needing corrective action will be reported to the Site Manager to be implemented.

For contingency, SC Waste recognises that if needed to ensure a continued material throughput, machinery will be hired from specialists if a significant plant breakdown occurs.  This is to ensure continued effective operations and prevent excessive storage of materials which are likely to give rise to the exceeding of permitted waste quantities.
3.7 Self Combustion

Given the stock rotation throughput times and material type, there is a limited potential for self-combustion. EA Guidance states that the risk increases when wastes are stored over 3 months and that combustible materials must not be stored for more than 6 months.  Wastes on site are not likely to be stored for longer than 2 weeks. No waste is stored in the building overnight.
Daily checks are made on the site as part of the Fire Risk Daily Checks Form (Annex F) and this includes checking for signs of self-combustion and housekeeping issues which may impact on fire risk.  
The risk of combustion is low, as the materials which will be managed on site are not anticipated to be contaminated with oil, however they will be dry.  As a result, a regime of turning the waste materials monthly during a stock take will be in place only if required.  For details see 3.2.3 Stock Rotation and Management. 
Heat will be released from waste before storing in piles.
The company has considered the risk of self-combustion and consider that given the storage times, management procedures in place and materials stored, the waste is unlikely to generate hot spots.  However, during operation, if the site records show that hotspots do occur on site regularly, the Site Management will consider further measures such as temperature probes.
In warmer weather waste piles will be sheeted or dampened as required to minimise the effects of external heating. The site (being internal to the warehouse) benefits from cover which will be used where possible to keep waste piles cool. Regular (daily) checks on waste piles will be made and the results recorded in the site diary.
3.8 Hot Works
Hot works will not be undertaken at the site.
No other combustible gases, chemicals, aerosols or fuels are kept on site
3.9 Mechanical Treatment
Mechanical treatment means the use of mobile plant.  The plant used on site will be as follows:

· One fork lift truck.
· One 360.

· Picking Station

3.10 Hot Exhausts

· As above – kept away from waste piles.
3.11 Additional Actions
Further actions to mitigate fire risk on site include:

· Overnight parking of vehicles away from processing and storage areas.
· The access route into the site is always kept clear and will therefore provide access for emergency vehicles.
· Site walkovers taken each day will identify any accumulations of combustible dust, litter or material which may pose a fire risk in the areas used by vehicles.
· Litter will be restricted by the warehouse and building to some extent. Visible litter will be picked daily at the end of the shift. Litter off site will be checked and removed at shift start and finish.
· Good housekeeping will be maintained at all times to ensure dust and wastes are prevented from accumulating on site.
· Operational vehicles will be fitted with fire extinguishers 
· Any fuel/oil spills from plant or vehicles will be cleaned up immediately with absorbent material and disposed of correctly
· Sources of ignition including non-energy efficient (heat emitting) light bulbs, lit cigarettes, naked flames and storage heaters will not be allowed on site.
· All other sources of ignition will be kept at least 6m from flammable & combustible waste

· Cleaning – The site will be cleaned daily at the end of the operational shift in order to prevent build-up of dust, fluff and combustible waste. This will be focused on areas where dust may build up e.g. computer screens flat surfaces, mobile plant etc. Surfaces will be dusted, wiped and/or jet washed if appropriate.

· Regular inspections of vehicles and the main roads are made to ensure that no annoyance to other road users and neighbours is apparent.
· Activity location benefits from good sound attenuation provided by the internal industrial location & setting. All plant benefits from noise and dust suppression being inside a building.
Ensure operations are only conducted within working hours and where practical noise is minimised by using the minimal movements of vehicles and materials onto and from site
4 Fire Detection and Management
4.1 Fire Detection

South Coast Waste Limited will 

· provide portable extinguishers

· carry out regular inspections, including at the start and end of every working day
All staff are aware of this FPP and the risk of fire on site and are trained to remain vigilant. 

Security staff are trained in actions in case of fire detection..
Fire Suppression:
The Site Fire Fighting Equipment Plan (Annex C & J) shows the following items for fire suppression:

Automatic fire suppression is not required and is considered unecomonic due to the small scale operation. No waste is stored in a building overnight. SC Waste will however install fire blankets and extinguishers within the building and a manual suppression system will be employed as staff are available to be at the site within 20 minutes. Staff will be able to fight small fires by using the equipment listed above. Larger fires will be left to the FRS due to safety.
Heat sensitive CCTV will be installed in the x2.
https://www.axis.com/en-gb/products/axis-q29-series
4.1.1 Water Supplies

Table 2 shows the available water on site which can be delivered from the water hydrant within 100m of the site entrance at Ackworth Rd. See Annex C for water supply site plan.
	Table 2: Volume of Water Available

	Hydrant
	1

	Delivery (l/min)
	2000

	Number of hydrants
	1

	Total Hydrant Delivery (l/m)
	2000


Water supplies for fire fighting can come from the nearby hydrant. In addition to one or more FRS water supply trucks if the FRS deems it necessary.

The largest stockpile likely to require water for fire fighting is considered to be the paper/card waste pile - a maximum of 60m3. 
4.2 Fire Fighting Strategy
In the event of a fire being suspected or detected, the following steps will be taken:
[image: image2.png]~\
*Raise the alarm - contact Emergency Services on 999
eEvacuate affected area as denoted by the fire assembly point
J
N

*Contactsite Health and Safety officer or person nominated as fire protection officer
sConduct staff role call if required depending on size of incident

J
If safe to do so: the appropriate electrical and mechanical equipment are shut
down
*A suitable hand held fire extinguisher is used )
N
«If emergency services are required, direct them to the source of the fire and
support them with identifying potential sources of ignition such as fuel stores
J
~
«If safe to do so, ensure fire water escape measures are implemented (booms and
drain covers)
J
~
*When fire extinguished, ensure removal of contaminated materials, use PPE when
moving the materials to appropriate container/disposal site
J
N
sComplete Incident Report and follow up with improvement measures if necessary
J

€€




The Site Manager, will liaise with the Emergency Services on their arrival.  The Site Manager will clearly identify him/herself to the Emergency Services on their arrival on site and update the FRS on the situation ensuring they are made aware of the location any compressed gases or flammable liquids on site.
Prior to arrival of the FRS on-site there are several measures that SC Waste can take to help fight fire, assuming there is no risk to life.
· Hand held fire extinguishers can be deployed in order to contain fires where possible

· Fire blankets/sheets can be used to smother smaller isolated sources of fire.

· The quarantine area is 3.5m x3.5m x3.5m (42.8 cubic metres) and can accommodate at least 50% of the largest waste pile (60 cubic metres in the yard). See appendix A.

· In the event of a fire or observed self-combustion, burning waste, if safe to do so, will be moved to the Fire Quarantine Area or alternative designated site. 

· The Fire Quarantine Area is signposted.  

· The quarantine area, when made safe, will be emptied immediately. Should it be necessary to move or divert wastes to an alternative site then an alternative permitted location will be used. Vehicles will be directed to this site. (Note the only vehicles coming to site will be SC Waste own operated vehicles or suppliers and not the general public so all drivers will be notified to divert to this location).
· Neighbours and local businesses downwind will be notified of any potential fire incident by the site operator as soon as possible from the local contact list. This will be completed by telephone and will be completed as soon as it is safe to do so. Local receptors will be notified in order of proximity to the site and prevailing wind direction. Local receptors will be kept updated as to the progress of fire-fighting as new information comes to light and fully debriefed at the end of the event.
· Once the fire has been dealt with, post fire de-contamination arrangements will be agreed with the local EA officer

· The site is an impermeable surface and will be scraped clean

· Drains and runs will be gulped out and cleaned by tankers
· Waste will be removed from site if necessary

· If necessary, soil and groundwater monitoring will be undertaken as agreed with the EA

· Once the local EA officer has agreed that the site is ready to become operational again then operations will recommence.
4.3 Managing Fire Water
Table 3 shows the potential volume of fire water which may need to be managed on site should the largest waste pile require quenching. 

	Table 3:  Volume of Water Required

	l/min/1m3 of waste *
	                  6.6 

	Largest Combustible Pile (m3)
	                 60

	Water Required (l/min)
	396              

	Total Requirement for 3 hours (l)
	       71,280

	*Based on EA guidance: 2000l of water minute is required for a 300m3 stockpile for three hours


Table 4 shows the volume of fire water which can be contained within the site. The operation benefits from being inside a yard sealed around the perimeter which will contain firewater.  A permanent ramp will be deployed across the warehouse door entrance to retain water to a height of 12cm as per Annex C if required.
	Table 4:  Volume of Firewater Contained within Site 

	Average Site Length (m)
	26

	Average Site Width (m)
	26

	Water Depth (m)* 
	0.12

	Site Volume (m3)
	                         81.12

	Site Volume (l)
	      81,120

	*minimum height of curb or boom


These tables show that the site would be able to contain the volume of water needed in a worst-case scenario.  Therefore, the key receptors in Annex D which could be affected by firewater will be protected. A ramp (12cm) will be deployed across the warehouse entrance should firewater need to be contained during a fire.. It is likely that all water will be retained by the walls in the yard on the other 3 sides of the site and the ramp at the warehouse gate. Externally firewater is retained by kerbing (12cm) as shown in Annex C.
South Coast Waste Limited has a contact for emergency spillage response with a company which provides tankers to remove firewater.  The company would come to site to remove water from the warehouse contained by the walls.  Clean Surface Water from the yard is discharged via SW gulley to the blind sump. Contaminated water is caught in a blind sump and tankered away.  
Future Actions

This plan is based on current planned operations.  South Coast Waste Limited understand that it is important that this Fire Prevention Plan is maintained up to date and relevant to the business.  Therefore, it will be updated accordingly, in collaboration with the Environment Agency as required, should business operations change in the future.

5 Annex A: Site Layout

All site is impermeable concrete.                          (See section 3.2.4 for key to firebays.)
[image: image3.jpg]N
Address

SOUTH COAST WASTE LTD, ACKWORTH ROAD, PORTSMOUTH, CITY OF PORTSMOUTH,
Date Grid reference
03/09/2025 466498, 104129

Site

Picking
Entrance

Office \ EEny Station

e
Recycling Conveyor
Business

S60/grab Tipping/sorting
5 (o) CCTV  bays inside

building

4 8 12 16 20 24 28

32 36
Scale: 1:200 | Area: < 1ha | Paper size: A4





[image: image4.jpg]Address

SOUTH COAST WASTE LTD, ACKWORTH ROAD, PORTSMOUTH, CITY OF PORTSMOUTH,
Date Grid reference

03/09/2025 466466, 104094

20 40 60 80 100 120 140 160 180 200

Scale: 1:2500 | Area: 4ha | Paper size: A4



A2- Site Access
6 Annex B: Site Drainage
[image: image5.jpg]N
Address

SOUTH COAST WASTE LTD, ACKWORTH ROAD, PORTSMOUTH, CITY OF PORTSMOUTH,
Date Grid reference
03/09/2025 466498, 104129

___\ Impermeable concrete surface throughout
yard.

12 cm ramp at site entrance to prevent 4
egress of firewater

[]Begycung-ﬂ
=~ yBusiness

S

Conveyor

Gullies leading

\n 4= toblind sump

Perimeter of site kerbed/
ramped to prevent egress of

water \

I I I I I
4 8 12 16 20 24 28 32 36

Scale: 1:200 | Area: < 1ha | Paper size: A4





7 Annex C: Fire Fighting Access, Equipment & Water Supply Plan
[image: image6.jpg]Address
SOUTH COAST WASTE LTD, ACKWORTH ROAD, PORTSMOUTH, CITY OF PORTSMOUTH,

Date Grid reference
03/09/2025 466466, 104094
H;nd held extinguishers and

blankets held in office

Th

‘Water hydrant in
\Ackworth Rd

S *

— — — —
20 40 60 80 100 120 140 160 180 200

Scale: 1:2500 | Area: 4ha | Paper size: A4



C1
8 Annex D: Key Receptors
	[image: image7.jpg]7




	The receptors shown are within 1km of the site (black circle). Sensitive human receptors include areas containing residential properties to the north/east.  

The site is in on an industrial estate which is surrounded by light industry.  Langstone harbour SSSI is 500m East and there is priority habitat 30m North.
Key infrastructure includes the motorway to the North and railway to the East. The nearest Fire Response Service operation is Cosham fire station some 2Km NW.
Cosham Fire Station - 85 Northern Rd, Cosham, Portsmouth PO6 3AH

Wind Direction

According to the UK Met Office, the prevailing wind direction in the area is South-Westerly
. This means the prevailing winds blow over the site to the north east, which is away from the residential areas.


9 Annex E: Waste Acceptance Procedures
In order to identify non-compliant wastes including any hot loads, the following Waste Acceptance Procedure is implemented by SC Waste
Waste Acceptance

The procedure that shall be adopted at site is detailed below

 1. Waste arrives on site.

2. Documentation is checked at the office at the entrance to the site. See annex A2. 

3. All vehicles will have their contents examined during unloading and this shall be crosschecked with the documentation presented. 

4. Staff will check that the type of waste is acceptable in terms of the waste permit. 

5. If the waste is unacceptable the waste shall be isolated and arrangements put in place for the contractor to remove the waste from site or for the waste to be segregated in the quarantine area until such times that it can be removed.
6. If the person who is checking in the load is suspicious of its contents the driver shall be directed to the waste inspection area near the reception office, where the load shall be sampled and inspected to ensure that it corresponds to the accompanying documentation. In any event compliance testing will be carried out at regular intervals.

 7. Assuming the on-site verification at the office is satisfactory, the load is checked in and directed to the yard as appropriate. Here, the waste will be checked again to verify that the description is correct before tipping is allowed.

10 Annex F: Fire Risk Checks Form for Fire Prevention

The following regular check has been completed:

	Checks to be made

	1. Security – all security fencing and security equipment is intact (daily)

	2. Signs of Self Combustion – no smoke visible /potential hot spots identified (daily)

	3. Storage areas – housekeeping is suitable (daily)

	4. Storage areas – pile sizes within permitted limits (daily)

	5. Exhausts – exhausts are cool and located away from combustible materials(daily)

	6. Fire fighting water – all hose reels and hydrants if available are accessible(daily)

	7. Fire extinguishers – all fire extinguishers are in the correct place and intact(daily)

	8. Fire Quarantine area – clear from waste and signage intact(daily)

	9. Mobile plant parked remotely, secured and key out when site closed(daily)

	10. Waste turned when? – recorded on waste inventory in site office(monthly)

	11. Waste in (t) – recorded on waste inventory weekly in site office. Waste removed in date order

	12. Waste out (t) – recorded on waste inventory weekly in site office. Waste removed in date order.


	Date
	Morning check (initials)
	Evening Check (Initials)
	Issues to Report to Site Manager

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	


11 Annex G: Emergency Contacts
	Name & Address
	Telephone Number

	Environment Agency 
	General Enquiries:
Incident Hotline Reporting:
	03708 506 506

0800 80 70 60

	Electricity Supplier & mains switch location
	
	

	Gas supplier & shut off valve location
	
	

	Water supplier & shut off valve location
	
	

	Local Authority Emergency Services
	
	

	Insurance Company and policy number
	
	

	Nearest Hospital
	
	

	Emergency Spillage Response company
	
	


12 Annex H: EMS Documents
           Drainage & Bund Checks
· A current site drainage plan will be drawn up and displayed in the office areas for information. The standard colour coding of blue for surface water drainage that discharge to the environment and red for sealed or foul drainage systems will be employed.

· The integrity of impermeable surfaces, gulleys and storage areas will be visually inspected by the operator on a monthly basis. To achieve this, it will be necessary to sweep/ wash clean the impermeable surface that form licensed area and clear any debris that has collected in drain gulleys to the front of the building. Where any defects are found, remedial steps will be taken promptly to maintain the integrity of the structure. If, however the integrity of the structure is breached a temporary repair will be made by the end of the working day and a full repair will be made within 10 days.           

	Area
	When Checked 
	Date
	Comments

	Warehouse
	weekly
	20/01/24
	Clean 

	Firebays
	weekly
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	


          Site Vehicle and Machinery Maintenance.

· All machinery will be fitted with working exhaust silencing equipment.

· Staff will not continue to operate any piece of machinery or equipment that appears to be visibly or audibly failing.

· All vehicles and machinery operated within the site will undergo regular planned preventive maintenance/ servicing and inspections, at the frequency deemed appropriate by manufacturer or required by legislation. As a minimum, this will be a statutory annual inspection of lifting (LOLER) and work (PUWER) equipment. Maintenance/ Servicing and inspection records will be kept on site for reference.

· Where the necessary maintenance and repair skill do not exist within the company, a contract for these services will be in place, so that the repair of site vehicles and machinery will be undertaken promptly.

· If mobile plant maintenance/ repair will involve the removal/ loss of potentially polluting fluids from the vehicle, if possible, the vehicle should be moved to impermeable concrete area and worked on there, where any spills will land on an impermeable surface. All fluid leaks or drained oils will be collected in a container and removed.

· Where mobile plant must be repaired in the location that it breaks down, if this is on hard standing, drip trays and absorbent mats will be put in place under the vehicle before work begins, to capture any spills of potentially polluting substances and prevent contamination to the earth below.
Plant and Vehicles will be inspected and recorded below;

	Equipment
	When checked
	Date
	Comments
	signed

	Delivery vehicles
	weekly
	
	
	

	FLT
	Manufacturers Spec’
	
	
	

	360
	Manufacturers Spec’
	
	
	

	Picking Line
	Manufacturers Spec’
	
	
	


Dealing with Spills

Scope: To detail how spills during normal and abnormal operations are dealt with to minimize impact on the environment

Responsibility: Site owner

Background: Spillage of oils and chemicals can have an impact on the soil and groundwater beneath the site.

The site carries quantities of absorbent granules and absorbent booms to mop up small quantities of hydrocarbon and other liquids if spilt. If used these are stored in a hazardous waste container until removed from the site by specialist contractor within a reasonable period of time.

· During normal operations, all staff have been made aware of the requirement to minimise fuel and liquid spills on site

· All staff have had appropriate training on how to deal with a fuel spill in the event of an incident occurring

· Absorbent is used to clean up the spill at source. If it is a larger spill and it is safe to do so then the source of the spill is curtailed if possible.

· The location of spill kits and absorbent material is identified on the site plan

· Where possible all spills are directed to the sealed drainage system for containment

· A store of general absorbent material will be kept on site in an easily accessible central location known to all site staff. The absorbent material will be hydrocarbon (fuel, oil etc.) absorbent, as this is the most likely material to be spilt on site.
· Where leakage from any storage container (only diesel storage on-site) on site is found, actions to remedy the leak will be taken. Any such leakage and remedial action will be recorded in the site diary.

          In addition:

· The source of the leak or spill will be investigated, located and stopped.

· If any significant leaks or spills of substances occur, which have the potential to harm the environment or pose a risk to human health; the materials detailed under the section 'site provisions' will be utilized and disposed of appropriately.

· Any pooling leak or spill of a potentially polluting liquid will be soaked up with appropriate absorbent material, such as saw dust, sand or granules. The absorbent material will be cleared from the ground when it has soaked up all free polluting liquid. Where there is the potential to reuse absorbent material because it is not fully saturated, it will be stored in containers labeled 'absorbents for reuse' when fully saturated, absorbents will be placed in containers labeled 'absorbents for disposal'.

· In the event of a significant and/ or on-going leak or spill of a potentially polluting liquid, clay damit mats or suction covers will be applied to drain grills to seal them to prevent (further) liquid from entering the sealed drainage system. None in warehouse.
· If any leaks or spills of substances occur, which have the potential to harm the environment or pose a risk to human health escape the site boundary, the management will inform the Environment Agency immediately. Any remedial action specified by the Environment Agency will be undertaken, a record of which will be made in the site diary.

     Waste Acceptance, Storage and Inspection     

     To deal with the acceptance, storage & inspection of waste on-site.

     Introduction

The company will introduce a system of storage on-site to minimise the potential for cross contamination and potential run off from wastes whilst stored on site.

Waste Types

Only the waste types and EWC codes named on the environmental permit will be accepted at the site. Wastes entering the site will be inspected and registered at the site. Non-compliant waste materials not allowed on the permit will be turned away from the site. A record will be made in the site diary. 
     Working Hours

     Normal working hours will be 0800-1800  Monday - Saturday
    Sunday – closed

    Responsibility

    The Manager (Nick Williams) is responsible for identifying and      highlighting non-conforming   waste. The Environmental Manager is responsible   for inspecting, documenting and safe removal of any non-conforming waste.

Waste Storage

Containers will be nominated on-site for each waste type. These will be labelled and identified on the site plan. The site plan will be updated on a regular basis provide a record of what type of waste and quantity is stored where.
Waste Acceptance

The procedure that shall be adopted at site is detailed below

 1. Waste arrives on site.

2. Documentation is checked at the office. 

3. All vehicles will have their contents examined during unloading and this shall be crosschecked with the documentation presented. 

4. Staff will check that the type of waste is acceptable in terms of the waste licence. 

5. If the waste is unacceptable the waste shall be isolated and arrangements put in place for the contractor to remove the waste from site. 

6. If the person who is checking in the load is suspicious of its contents the driver shall be directed to the waste inspection area close to the reception office, where the load shall be sampled and inspected to ensure that it corresponds to the accompanying documentation. In any event compliance testing will be carried out at regular intervals if required
 7. Assuming the on-site verification at the office is satisfactory, the load is checked in and directed to the yard as appropriate. Here, the waste will be checked again to verify that the description is correct.
Waste Area Inspection

As part of the EMS waste areas are inspected routinely, deviations from normal operation conditions, result are logged and acted upon in the site log.

Records

SC Waste shall keep records of all waste loads rejected including; 

· Date

· Name of Carrier  

· Source of Waste  

· Vehicle Registration  

· Description of Waste

· EWC code 

· Quantity of Waste 

· Name of person carrying out inspection 

· Destination of Load prior to rejection
Car parking area











N








� Fire Prevention Plans, Version 2 January 2021.


� http://www.metoffice.gov.uk/climate/uk/regional-climates/





 PAGE 

