## Cover Page
Project Title |  | IED PERMIT COMPLIANCE DELIVERY - BLACKBURN
Project No: |  | 80064852
Document Title: |  | BLACKBURNWwTW
SECONDARY CONTAINMENT ESTIMATING SCOPE
|  | 80064852-MISCE-IE-C-000001 | REV
Document No: |  |  | P01
REVISION | DATE | REASON FOR REVISION | Author | Checker | Approver
P01 | 2022-06-17 | First Issue | Will Bartley
B | 2022-11-02 | First Revision, updated solution details | David Jowett

## OPTION A
RECOMMENDATIONS FROM STANTEC REPORT | ESTIMATING SCOPE
7.1 CONTAINMENT FOR GROUP 1, GROUP 3, GROUP 4 AND GROUP 5 ASSETS
Figure 15: Blackburn STC Predicted Flow Paths following Unscreened Sludge Buffer Tank Burst
|  |  |  | Section 6 | Section 7 | Total
|  | CONTAINMENT WALL | mm | 129982.7 | 250029.7
|  |  | m | 129.9827 | 250.0297 | 380.0124 | See sheet ' Containment Wall'
Figure 13: Blackburn STC Predicted Flow Paths following EEH Reactor No. 6 Tank Burst
Figure 11: Blackburn STC Predicted Flow Paths following Centrate Tank Burst
Figure 9: Blackburn STC Predicted Flow Paths following Post Digestion Tank no 2 Burst
Figure 7: Blackburn STC Predicted Flow Paths following Digestor No 4 Burst
Section 6
Section 7

## Containment Wall (Opt A)
CONTAINMENT WALL |  | 380.0124 | m
C30 strength RC
▲ESTIMATING SCOPE▲
▼ Jetting Calc ▼ | NOT USED
Jetting distance
Assumed values
Thermophillic Digesters
|  |  |  | H | 13.6 | m
|  |  |  | h | 1.5 | m
|  |  |  | Imax | 12.1 | m
Post Digestion Tank
|  |  |  | H | 7 | m
|  |  |  | h | 1.5 | m
|  |  |  | Imax | 5.5 | m

## SACRIFICIAL AREA DRAINAGE Opt A
ONLY REQUIRED FOR OPTION B1
Impermeable membrane area Strip existing surfacing (assume gravel), prep surface, lay membrane, reinstate surfacing | 13000 | m2
Length of French drains | 550 | m
No. of existing manhole connections | 8 | No.
https://uusp/engdel/Standards/engineering%20standards/Standard%20Details/STND_00%20Miscellaneous/Current%20Versions/STND-00-001_B.pdf
|  |  | ID | Area | Area | Connecting Manhole | CL | IL | EGL | Start IL | Gradient | DN | Length | End IL | Check
|  |  |  | mm2 | m2 | [10 empty] | https://www.uksuds.com/tools/members/surface-water-storage-volume-estimation-members
|  |  | A | 4205298221.6062 | 4205.2982 | MH071 | 49.83 | 47.44 | 49.83 | 49.13 | 0.5% | 150 | 100 | 48.63 | OK | Using this online tool to give inidcation of surface water capacity needed
[6 empty] | MH061 | 48.5 | 46.7 | 48.5 | 47.8 | 0.5% | 150 | 100 | 47.3 | OK |  | Notes for WwTW | Blackburn
|  |  | B | 3119060731.1 | 3119.0607 | MH077 | 49.99 | 47.52 | 49.99 | 49.29 | 0.5% | 150 | 135 | 48.615 | OK | Site latitude | Use map zoom and drop pin on location | 53.76077° N
|  |  | C | 637002755.7 | 637.0028 | MH096 | 53.07 | 48.87 | 53.07 | 52.37 | 0.5% | 150 | 85 | 51.945 | OK | Site longitude | Use map zoom and drop pin on location | 2.60252° W
|  |  | D | 600040385.3 | 600.0404 | MH096 | 53.07 | 48.87 | 53.07 | 52.37 | 0.5% | 150 | 55 | 52.095 | OK | Total site area (m2) | Total additional impermeable area created by option | 13000
|  |  | E | 3647153065.6901 | 3647.1531 | MH070 | 49.53 | 47.27 | 49.53 | 48.83 | 0.5% | 150 | 70 | 48.48 | OK | Total site area (ha) |  | 1.3
|  |  | F |  | 0 |  | 53 | 2.31 | 53 | 52.3 | 0.5% | 150 |  | 52.3 | OK | Significant public open space (ha) |  | 0
|  |  | G |  | 0 |  | 5.95 | 4.75 | 5.95 | 5.25 | 0.5% | 150 |  | 5.25 | OK | Area positively drained (ha) |  | 1.3
[5 empty] | 12208.5552 | [7 empty] | 545 |  |  | Impermeable area (ha) |  | 1.3
[16 empty] | Drained area that is impermeable (%) |  | 100%
[16 empty] | Impervious area drained via infiltration (ha) |  | 0
[16 empty] | Return period for infiltration system design (years) |  | 100
[16 empty] | Impervious area drained to rainwater harvesting systems (ha) | Assume zero | 0
[16 empty] | Return period for rainwater harvesting system design (years) | Default | 10
[16 empty] | Compliance factor for rainwater harvesting system design (%) | Default | 66%
[16 empty] | Net site area for storage volume design (ha) | Calculated | 1.3
[16 empty] | Net impermeable area for storage volume design (ha) | Calculated | 1.3
[16 empty] | Pervious area contribution (%) | Default | 30
[16 empty] | Rainfall 100yrs 6hrs (mm) | Results using the IH24 method | 70
[16 empty] | Rainfall 100yrs 12hrs (mm) | Results using the IH24 method | 97.44
[16 empty] | Qbar (l/s) |  | 10.02
[16 empty] | 1 in 1 year (l/s) |  | 8.7
[16 empty] | 1 in 30 year (l/s) |  | 17
[16 empty] | 1 in 100 years (l/s) |  | 20.8
[16 empty] | Attenuation storage (m3) |  | 1095
[16 empty] | Long term storage (m3) |  | 300
[16 empty] | Total storage (m3) |  | 1396
[16 empty] | 1 in 30 year area rate (l/s/m2) |  | 0.0013077
[16 empty] | DN150 Proposal capacity (@1 in 200 ks=1.5mm) | l/s | 10.9052
[16 empty] | AREA PER PIPE( DN150) | m2 | 8339.2899
Area D
Area E
Area C
Area B
Area A

## OPTION B1
RECOMMENDATIONS FROM STANTEC REPORT | ESTIMATING SCOPE
CONTAINMENT FOR GROUPS 1-7
Figure 16: Blackburn STC Predicted Flow Paths following Unscreened Sludge Buffer Tank Burst
|  |  |  | Section 1 | Section 2 | Section 3 | Total
|  | CONTAINMENT WALL | mm | 118000 | 194000 | 246000
|  |  | m | 118 | 194 | 246 | 558 | See sheet ' Containment Wall'
|  | SACRIFICIAL AREA | m2 | 17000 | See sheet 'SACRIFICIAL AREA DRAINAGE'
|  | SACRIFICIAL AREA DRAINAGE | m | 550
|  | MECHANICAL FLOOD GATE (2NO.) | m | 11
Figure 14: Blackburn STC Predicted Flow Paths following EEH Reactor No. 6 Tank Burst
Figure 12: Blackburn STC Predicted Flow Paths following Centrate Tank Burst
Figure 10: Blackburn STC Predicted Flow Paths following Post Digestion Tank no 2 Burst
Figure 8: Blackburn STC Predicted Flow Paths following Digestor No 4 Burst
Figure 18: Blackburn STC Predicted Flow Paths Following Centrate and Filtrate Tank Burst
Figure 20: Blackburn STC Predicted Flow Paths Following Drum Thickener Feed Tank No.1 Burst
Section 1
Section 2
Section 3

## Containment Wall (Opt B1)
CONTAINMENT WALL |  | 305 | m (1m above ground)
|  | 225 | m (1.5m above ground)
|  | 530 | total length of containment walls
C30 strength RC
Additional items to consider:
Vegetation removal | 200m x 3m
Compensatory planting (shrubbed area including allowance for small trees) | 400m2
▲ESTIMATING SCOPE▲
▼ Jetting Calc ▼ | NOT USED
Jetting distance
Assumed values
Thermophillic Digesters
|  |  |  | H | 13.6 | m
|  |  |  | h | 1.5 | m
|  |  |  | Imax | 12.1 | m
Post Digestion Tank
|  |  |  | H | 7 | m
|  |  |  | h | 1.5 | m
|  |  |  | Imax | 5.5 | m
Vegetation removal & compenstory planting

## SACRIFICIAL AREA DRAINAGE Opt B
ONLY REQUIRED FOR OPTION B1
| Impermeable membrane area Strip existing surfacing (assume gravel), prep surface, lay membrane, reinstate surfacing | 17000 | m2
| Length of French drains | 1250 | m
| No. of existing manhole connections | 11 | No.
1000000
https://uusp/engdel/Standards/engineering%20standards/Standard%20Details/STND_00%20Miscellaneous/Current%20Versions/STND-00-001_B.pdf
|  |  |  | ID | Area | Area | Connecting Manhole | CL | IL | EGL | Start IL | Gradient | DN | Length | End IL | Check
[5 empty] | mm2 | m2 | [10 empty] | https://www.uksuds.com/tools/members/surface-water-storage-volume-estimation-members
|  |  |  | A | 9322000000 | 9322 | MH071 | 49.83 | 47.44 | 49.83 | 49.13 | 0.5% | 150 | 120 | 48.53 | OK | Using this online tool to give inidcation of surface water capacity needed
[7 empty] | MH165 | 47.32 | TBC | 47.32 | 46.62 | 0.5% | 150 | 105 | 46.095 | Won't work!
[7 empty] | MH165 | 47.32 | TBC | 47.32 | 46.619 | 0.5% | 151 | 60 | 46.319 | Won't work!
[7 empty] | MH165 | 47.32 | TBC | 47.32 | 46.618 | 0.5% | 152 | 75 | 46.243 | Won't work!
[7 empty] | MH165 | 47.32 | TBC | 47.32 | 46.618 | 0.5% | 152 | 120 | 46.018 | Won't work!
[7 empty] | MH061 | 48.5 | 46.7 | 48.5 | 47.8 | 0.5% | 150 | 100 | 47.3 | OK |  | Notes for WwTW | Blackburn
|  |  |  | B | 70000000 | 70 | MH087 | 54.37 | 52.09 | 54.37 | 53.67 | 0.5% | 150 | 30 | 53.52 | OK | Site latitude | Use map zoom and drop pin on location | 53.76077° N
|  |  |  | C | 5323000000 | 5323 | MH070 | 49.53 | 47.27 | 49.53 | 48.83 | 0.5% | 150 | 70 | 48.48 | OK
[7 empty] | MH071 | 49.83 | 47.44 | 49.83 | 49.13 | 0.5% | 150 | 120 | 48.53 | OK
[7 empty] | MH071 | 49.83 | 47.44 | 49.83 | 49.13 | 0.5% | 150 | 150 | 48.38 | OK
[7 empty] | MHXXX | 50.22 | TBC | 50.22 | 49.52 | 0.5% | 150 | 100 | 49.02 | Won't work!
[7 empty] | MH087 | 54.37 | 52.09 | 54.37 | 53.67 | 0.5% | 150 | 30 | 53.52 | OK
|  |  |  | D | 494000000 | 494 | MHXXX | 54.14 | TBC | 54.14 | 53.44 | 0.5% | 150 | 65 | 53.115 | Won't work! | Total site area (m2) | Total additional impermeable area created by option | 17000
|  |  |  | E | 101000000 | 101 | MHXXX | 54.14 | TBC | 54.14 | 53.44 | 0.5% | 150 | 40 | 53.24 | Won't work! | Total site area (ha) |  | 1.7
|  |  |  | F | 763000000 | 763 | MH038 | 54.13 | 52.32 | 54.13 | 53.43 | 0.5% | 150 | 60 | 53.13 | OK | Significant public open space (ha) |  | 0
|  |  |  | G | 105000000 | 105 | [10 empty] | Area positively drained (ha) |  | 1.7
[6 empty] | 16178 | [7 empty] | 1245 |  |  | Impermeable area (ha) |  | 1.7
[17 empty] | Drained area that is impermeable (%) |  | 100%
[17 empty] | Impervious area drained via infiltration (ha) |  | 0
[17 empty] | Return period for infiltration system design (years) |  | 100
[17 empty] | Impervious area drained to rainwater harvesting systems (ha) | Assume zero | 0
[17 empty] | Return period for rainwater harvesting system design (years) | Default | 10
[17 empty] | Compliance factor for rainwater harvesting system design (%) | Default | 66%
[17 empty] | Net site area for storage volume design (ha) | Calculated | 1.7
[17 empty] | Net impermeable area for storage volume design (ha) | Calculated | 1.7
[17 empty] | Pervious area contribution (%) | Default | 30
[17 empty] | Rainfall 100yrs 6hrs (mm) | Results using the IH24 method | 70
[17 empty] | Rainfall 100yrs 12hrs (mm) | Results using the IH24 method | 97.44
[17 empty] | Qbar (l/s) |  | 10.02
[17 empty] | 1 in 1 year (l/s) |  | 8.7
[17 empty] | 1 in 30 year (l/s) |  | 17
[17 empty] | 1 in 100 years (l/s) |  | 20.8
[17 empty] | Attenuation storage (m3) |  | 1095
[17 empty] | Long term storage (m3) |  | 300
[17 empty] | Total storage (m3) |  | 1396
[17 empty] | 1 in 30 year area rate (l/s/m2) |  | 0.001
[17 empty] | DN150 Proposal capacity (@1 in 200 ks=1.5mm) | l/s | 10.9052
[17 empty] | AREA PER PIPE( DN150) | m2 | 10905.2252
As Received 02/11/2022
As measured on Mapinfo, sqm
[7 empty] | Area A | 9322
[7 empty] | Area B | 70
[7 empty] | Area C | 5323
[7 empty] | Area D | 494
[7 empty] | Area E | 101
[7 empty] | Area F | 763
(88sqmDeducted for Tanks)
[7 empty] | Area G | 105
[7 empty] | Total | 16178
Area D
Area C
Area E
Area B
Area A
Area D
Area F

## Risks and Oppportunities
NOTES
| OPTION A | OPTION B1
1 | Initial design to provide approporiate magnitude of cost. | Initial design to provide approporiate magnitude of cost.
2 | Retaing wall size and location assumes no allowance for jetting necessary (Cira C739 pg86). Risk of need for more scope. | Retaing wall size and location assumes no allowance for jetting necessary (Cira C739 pg86). Risk of need for more scope.
3 | No additional hardstanding and drainage provision assumed. Risk that this is required. | -
4 | - | Trief/Titan kerbing is designed to contain traffic not liquid. Risk is detail may not be acceptable on water retention basis. Opportunirty that use of smaller pre cast concrete units may be feasible.
5 | Indicative wall design. Boundary is at the crest of some steep slopes and ther may be issues around slope stability as a result of the loading regime the wall introduces.Assumed it's possible to set the wall an appropriate distance away from the top of the slopes to avoid any need for slope stability works/ more significant foundations. | Wall design indicative. Detail design would need confirmation of ground conditions and topography.
6 | Wall alignment assumes reduction in existing track adjacent to western section of wall can be reduced to c. 3m width with no need for additional works (surfacing, drainage, etc) | Indicative wall design. Boundary is at the crest of some steep slopes and ther may be issues around slope stability as a result of the loading regime the wall introduces.Assumed it's possible to set the wall an appropriate distance away from the top of the slopes to avoid any need for slope stability works/ more significant foundations.
7 | - | -
8 | - | -
9 | Level of detail for extent is a coarse first pass. Detailed interrogation of topo data and on site confirmation needed to confirm exact extent and transition details. | Level of detail for extent is a coarse first pass. Detailed interrogation of topo data and on site confirmation needed to confirm exact extent and transition details.
10 | - | -
11 | - | Possible planning risk in relation to site appearance and habitat loss/compensation
12 | In-situ concrete walls conservative assumption - there will be DFMA opportunities | In-situ concrete walls conservative assumption - there will be DFMA opportunities
13 | - | Assumption that existing drainage system can accommodate additional drainage. Risk that addional pumping stations required.
14 | - | Proposed land drainage scoped to provide indication of magnitude of cost. Risk that lengths and sizing may be optimistic
15 | - | Assumption that existing ground does not provide an impermeable layer beneath proposed sacrificial areas.Opportunity that need for membrane may not be required.