## Containment Areas
RECOMMENDATIONS FROM STANTEC REPORT | ESTIMATING SCOPE
Figure 14 : Proposed Mitigation Measures for Group 1 – Import Break Tank
|  |  |  | Section 1 | Section 2 | Section 3 | Section 4 | Section 6 | Total
|  | CONTAINMENT KERB | mm | 70000 | 110000 | 84000 | 52000 | 20000
|  |  | m | 73 | 122 | 100 | 52 | 52 | 399 | See sheet 'Kerbing Detail'
|  |  |  | Section 5 | Section 7 | Total
|  | CONTAINMENT WALL | mm | 273000 | 92000
|  |  | m | 273 | 92 | 365 | See sheet ' Containment Wall'
Section 1
Section 5
Section 2
Section 3
Section 4
Section 1
Section 6
Section 5
Section 7

## Kerbing Detail
| Total length on kerbing required (m) | 399
| Allowance for 0.5m wide strip of bitmac resurfacing (m2) | 199.5
(Trief Cadet or Titan Compact)

## Containment Wall
|  |  |  | CONTAINMENT WALL 1500mm(h) from ground level | 365 | m
|  |  |  | TRIEF KERB 300mm(h) | 399 | m
|  |  |  | 150mm(h) SPEED BUMP | 32 | m
|  |  |  | PROPOSED 450mm(w) x 300mm(d) CULVERT, EXCAVATION AND | 11 | m
BREAK INTO EXISTING CONCRETE CHAMBER AND REPURPOSE
|  |  |  | 1200mm dia manhole sump, with puddle pump intergral float - static lift circa 5m | 1 | no.
C30 strength RC
Additional items to consider:
|  | Vegetation removal | 400m x 2.5M
|  | Compensatory planting (shrubbed area including allowance for small trees) | 1900m2
|  | Existing fence removal & replacement | 369M
▲ESTIMATING SCOPE▲
▼ Jetting Calc ▼ | NOT USED
Jetting distance
Assumed values
Secondary Digesters
|  |  |  | H | 12.8 | m
|  |  |  | h | 1.5 | m
|  |  |  | Imax | 11.3 | m
Primary Digesters
|  |  |  | H | 16 | m
|  |  |  | h | 1.5 | m
|  |  |  | Imax | 14.5 | m
Typical Section A (Proposed)
Containment wall
1500
2000
1800

## SACRIFICIAL AREA DRAINAGE
Impermeable membrane area Strip existing surfacing (assume gravel), prep surface, lay membrane, reinstate surfacing | 12000 | m2
Length of French drains | 718 | m
No. of existing manhole connections (within permit boundary) | 16 | No.
https://uusp/engdel/Standards/engineering%20standards/Standard%20Details/STND_00%20Miscellaneous/Current%20Versions/STND-00-001_B.pdf
|  |  | ID | Area | Area | Connecting Manhole | CL | IL | EGL | Start IL | Gradient | DN | Length | End IL | Check
|  |  |  | mm2 | m2 | [10 empty] | https://www.uksuds.com/tools/members/surface-water-storage-volume-estimation-members
|  |  | A | 140000000 | 1400 | MH46 | 4.93 | Not available | 4.93 | 4.23 | 0.5% | 150 | 42 | 4.02 | Won't work! | Using this online tool to give inidcation of surface water capacity needed
[17 empty] | Notes for WwTW | Southport
|  |  | B | 184921000 | 1849.21 | MH52 | 5.04 | 3.44 | 5.04 | 4.34 | 0.5% | 150 | 51 | 4.085 | OK | Site latitude | Use map zoom and drop pin on location | 53°40'42'' N
|  |  | C | 177388000 | 1773.88 | MH34 | 5.01 | 2.36 | 5.01 | 4.31 | 0.5% | 150 | 42 | 4.1 | OK | Site longitude | Use map zoom and drop pin on location | 002°57'24'' W
|  |  | D | 278285000 | 2782.85 | MH41 | 4.75 | 2.43 | 4.75 | 4.05 | 0.5% | 150 | 104 | 3.53 | OK | Total site area (m2) | Total additional impermeable area created by option | 12000
|  |  | E | 141296000 | 1412.96 | MH39 | 5.11 | 1.11 | 5.11 | 4.41 | 0.5% | 150 | 57 | 4.125 | OK | Total site area (ha) |  | 1.2
|  |  | F | 10000000 | 100 | TBC | TBC | #VALUE! | TBC | #VALUE! | 0.5% | 150 | 40 | #VALUE! | #VALUE! | Significant public open space (ha) |  | 0
|  |  | G | 49500000 | 495 | TBC | TBC | #VALUE! | TBC | #VALUE! | 0.5% | 150 | 57 | #VALUE! | #VALUE! | Area positively drained (ha) |  | 1.2
|  |  | H | 44500000 | 445 | TBC | TBC | #VALUE! | TBC | #VALUE! | 0.5% | 150 | 57 | #VALUE! | #VALUE! | Impermeable area (ha) (of spill modelled area) |  | 0.96
|  |  | J | 31900000 | 319 | TBC | TBC | #VALUE! | TBC | #VALUE! | 0.5% | 150 | 57 | #VALUE! | #VALUE! | Drained area that is impermeable (%) |  | 80%
|  |  | K | 29860000 | 298.6 | TBC | TBC | #VALUE! | TBC | #VALUE! | 0.5% | 150 | 57 | #VALUE! | #VALUE! | Impervious area drained via infiltration (ha) |  | 0
|  |  | L | 13800000 | 138 | TBC | TBC | #VALUE! | TBC | #VALUE! | 0.5% | 150 | 57 | #VALUE! | #VALUE! | Return period for infiltration system design (years) |  | 100
|  |  | M | 18000000 | 180 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Impervious area drained to rainwater harvesting systems (ha) | Assume zero | 0
[16 empty] | Return period for rainwater harvesting system design (years) | Default | 10
[16 empty] | Compliance factor for rainwater harvesting system design (%) | Default | 66%
|  |  | Total |  | 11194.5 | [7 empty] | 621 |  |  | Net site area for storage volume design (ha) | Calculated | 0.96
[16 empty] | Net impermeable area for storage volume design (ha) | Calculated | 0.96
|  |  | Note: Manhole locations and cover levels taken from Utility Survey Report 6279_U3_A, 20/08/13 | [12 empty] | Pervious area contribution (%) | Default | 30
[16 empty] | Rainfall 100yrs 6hrs (mm) | Results using the IH24 method | 63
[16 empty] | Rainfall 100yrs 12hrs (mm) | Results using the IH24 method | 81.62
[16 empty] | Qbar (l/s) |  | 5.83
[16 empty] | 1 in 1 year (l/s) |  | 5.1
[16 empty] | 1 in 30 year (l/s) |  | 9.9
[16 empty] | 1 in 100 years (l/s) |  | 12.1
[16 empty] | Attenuation storage (m3) |  | 792
[16 empty] | Long term storage (m3) |  | 249
[16 empty] | Total storage (m3) |  | 1042
[16 empty] | 1 in 30 year area rate (l/s/m2) |  | 0.000825
[16 empty] | DN150 Proposal capacity (@1 in 200 ks=1.5mm) | l/s | 10.9052
[16 empty] | AREA PER PIPE( DN150) | m2 | 13218.4548