## Sheet1
Redhill LGW10 & LGW11 Data Centre 2021 diesel consumption
LGW10 Data extracted from Redhill 2021 EU ETS Annual Emissions Report calculation sheet
LGW10 | [5 empty] | LGW11
Suite | Fuel Use at 100% Capacity (L/h) | 2020-12-01 | 2021-12-01 | Total | Litres consumed using run hours and flow rates | Suite | Fuel Use at 100% Capacity (L/h) | 2020-12-01 | 2021-12-01 | Total | Litres consumed using run hours and flow rates
LL Gen | 58.9 | 171.6 | 174.3 | 2.7 | 159.03 | S110 Gen A1 | 394 | 93.2 | 103 | 9.8 | 3861.2
S110 Gen 1 | 331.5 | 135.8 | 140.4 | 4.6 | 1524.9 | S110 Gen A2 | 394 | 123 | 132 | 9 | 3546
S110 Gen 2 | 331.5 | 139.6 | 143.6 | 4 | 1326 | S110 Gen B1 | 394 | 61.2 | 70.7 | 9.5 | 3743
S110 Gen 3 | 331.5 | 162.6 | 167.4 | 4.8 | 1591.2 | S110 Gen B2 | 394 | 50.4 | 90 | 39.6 | 15602.4
S120 Gen 1 | 331.5 | 108.7 | 112.5 | 3.8 | 1259.7 | Landlord | 46 | 26.5 | 32.3 | 5.8 | 266.8
S120 Gen 2 | 331.5 | 122.7 | 127.4 | 4.7 | 1558.05
S130 Gen 1 | 331.5 | 103.6 | 107.3 | 3.7 | 1226.55
S130 & S150 Swing | 371 | 61 | 64 | 3 | 1113
S140 Gen 1 | 371 | 124 | 129 | 5 | 1855
S140 Gen 2 | 371 | 118 | 125 | 7 | 2597
S140 Gen 3 | 371 | 130 | 136 | 6 | 2226
S140 Gen 4 | 371 | 64 | 66 | 2 | 742
S150 Gen 1 | 371 | 79.5 | 82.4 | 2.9 | 1075.9
S160 Gen 1 | 371 | 101 | 105 | 4 | 1484
S160 Gen 2 | 371 | 89.2 | 93.2 | 4 | 1484
S160 Gen 3 | 371 | 48.3 | 50.3 | 2 | 742
Total litres | 48983.73
Tonnes | 41.3714
Max litres available | 229225
Max Tonnes | 193.6022
Note on A7: Soiza, Jade: Olympian GEH275-2
Note on K7: Skinner, Rachel: Cummins QSK60-G3 2020 kva
Note on A8: Soiza, Jade: CAT 3512B-1600
Note on K8: Skinner, Rachel: Cummins QSK60-G3 2020 kva
Note on A9: Soiza, Jade: CAT 3512B-1600
Note on K9: Skinner, Rachel: Cummins QSK60-G3 2020 kva
Note on A10: Soiza, Jade: CAT 3512B-1600
Note on K10: Skinner, Rachel: Cummins QSK60-G3 2020 kva
Note on A11: Soiza, Jade: CAT 3512B-1600
Note on K11: Skinner, Rachel: Cummins 6CTAA8.3G2
Note on A12: Soiza, Jade: CAT 3512B-1600
Note on A13: Soiza, Jade: CAT 3512B-1600
Note on A14: Soiza, Jade: QSK60-G3. Called 'S 130 Gen 2 on permit'
Note on A15: Soiza, Jade: QSK60-G3
Note on A16: Soiza, Jade: QSK60-G3
Note on A17: Soiza, Jade: QSK60-G3
Note on A18: Soiza, Jade: QSK60-G3
Note on A19: Soiza, Jade: QSK60-G3
Note on A20: Soiza, Jade: QSK60-G3
Note on A21: Soiza, Jade: QSK60-G3
Note on A22: Soiza, Jade: QSK60-G3

## Sheet2
LGW10 & LGW11 Tank capacities
LGW10
Site | Suite | Tank Size (Lts)
LGW10 | LL Gen | 1485
LGW10 | S110 Gen1 | 8000
LGW10 | S110 Gen2 | 8000
LGW10 | S110 Gen 3 | 8000
LGW10 | S120 Gen 1 | 8000
LGW10 | S120 Gen 2 | 8000
LGW10 | S110 & S120 Bulktank | 48000
LGW10 | S130 Gen 1 | 8000
LGW10 | S130 & S150 Swing | 10000
LGW10 | S140 Gen 1 | 10000
LGW10 | S140 Gen 2 | 10000
LGW10 | S140 Gen 3 | 10000
LGW10 | S140 Gen 4 | 10000
LGW10 | S150 Gen 1 | 10000
LGW10 | S160 Gen 1 | 10000
LGW10 | S160 Gen 2 | 10000
LGW10 | S160 Gen 3 | 10000
LGW11
Site | Suite | Tank Size (Lts)
LGW11 | S110 Gen A1 | 10000
LGW11 | S110 Gen A2 | 10000
LGW11 | S110 Gen B1 | 10000
LGW11 | S110 Gen B2 | 10000
LGW11 | Landlord | 1740
Total capacity | 229225