## Unit 3 - DR
Generator list and tank sizes extracted from Digital Realty's monthly diesel fuel level and run hour spreadsheet
Redhill Generator Information for Air Quality Risk Assessment | [17 empty] | Emission Rates
Site | Suite | Tank Size (Lts) | Make of Engine | Model | Engine Type & Number | Standby KW Output | Thermal input MWth | Sulphur content from Crown Oil fuel polishing report once polished (mg/kg) | Approx stack heights on generator (m) | Stack diameter (mm) | Approx total stack height from ground (m) | Nearest building elevation (height) e.g south 13m | Emission point 12-digit grid reference - Easting, Northing | 2020 run hours from generator (used in EU ETS) | 2021 run hours from generator (used in UK ETS) | 2022 run hours from generator (used in UK ETS) | Notes | NOX (mg/Nm3) | CO (mg/Nm3) | PM (mg/Nm3) | HC (mg/Nm3) | SO2 | Emission rate notes
Redhill, UK
Redhill, UK | LL Gen | 1485 | CAT | GFH275-2 | GCB 330A WS5348N1539582 | 220 | 0.59 |  |  | ~400 | 6.5 | West 13m | 528664 , 151432 | 3.6 | 2.7 | 6 | [6 empty] | No emissions data available
Redhill, UK | S110 Gen1 | 8000 | CAT | CAT 3512 GD | 3512 GD 1GZ05137 | 1280 | 3.34 | 3433 | ~3 | ~400 | 8 | West 13m | 528670 , 151444 | 2.8 | 4.6 | 33.5 | Emissions data measurement procedures are consistent with those described in EPA CFR 40 Part 89, Subpart D &E and ISO8178-1 for measuring HC, CO, PM, NOx. Data shown is based on steady state operating conditions of 77° F, 28.42 in HG and number 2 diesel fuel with 35° API and LHV of 18,390 btu/lb. The nominal emissions data shown is subject to instrumentation, measurement, facility and engine to engine variations. Emissions data is based on 100% load and thus cannot be used to compare to EPA regulations which use values based on a weighted cycle. | 1830.3 | 134.2 | 35.3 | 68.8 |  | Please note - emission level in (mg/Nm3) corrected to 5% oxygen in the exhaust
Redhill, UK | S110 Gen2 | 8000 | CAT | CAT 3512 GD | 3512 GD 1GZ05123 | 1280 | 3.34 | 3611 | ~3 | ~400 | 8 | West 13m | 528665 , 151442 | 11.6 | 4 | 3.8 |  | 1830.3 | 134.2 | 35.3 | 68.8 |  | Please note - emission level in (mg/Nm3) corrected to 5% oxygen in the exhaust
Redhill, UK | S110 Gen 3 | 8000 | CAT | CAT 3512 GD | 3512 GD 1GZ05129 | 1280 | 3.34 | 3417 | ~3 | ~400 | 8 | West 13m | 528660 , 151441 | 20.6 | 4.8 | 22.5 |  | 1830.3 | 134.2 | 35.3 | 68.8 |  | Please note - emission level in (mg/Nm3) corrected to 5% oxygen in the exhaust
Redhill, UK | S120 Gen 1 | 8000 | CAT | CAT 3512 GD | 3512 GD 1GZ05135 | 1280 | 3.34 | 3555 | ~3 | ~400 | 8 | West 13m | 528643 , 151504 | 2.7 | 3.8 | 4.2 |  | 1830.3 | 134.2 | 35.3 | 68.8 |  | Please note - emission level in (mg/Nm3) corrected to 5% oxygen in the exhaust
Redhill, UK | S120 Gen 2 | 8000 | CAT | CAT 3512 GD | 3512 GD 1GZ05133 | 1280 | 3.34 | 3460 | ~3 | ~400 | 8 | West 13m | 528648 , 151505 | 7.7 | 4.7 | 7.7 |  | 1830.3 | 134.2 | 35.3 | 68.8 |  | Please note - emission level in (mg/Nm3) corrected to 5% oxygen in the exhaust
Redhill, UK | S130 Gen 1 | 8000 | CAT | CAT 3512 GD | 3512 GD 1GZ05119 | 1280 | 3.34 | 5470 | ~3 | ~400 | 8 | West 13m | 528653 , 151506 | 3.6 | 3.7 | 3.9 |  | 1830.3 | 134.2 | 35.3 | 68.8 |  | Please note - emission level in (mg/Nm3) corrected to 5% oxygen in the exhaust
[18 empty] | NOX (mg/m3) | CO (mg/m3) | PM (mg/m3) | HC (mg/m3)
Redhill, UK | S130 & S150 Swing | 10000 | Cummins | QSK60-G3 | C2000 D5 H09KBAP500 | 1600 | 3.74 | 6624 | ~3 | ~400 | 8.5 | East 13m | 528769 , 151475 | 1 | 3 | 2 |  | 4359 | 454 | 65 |  |  | mg/m³ and PPM numbers are measured dry and corrected to 5% 02 content.
Redhill, UK | S140 Gen 1 | 10000 | Cummins | QSK60-G3 | C2000 D5 E10KBGB260 | 1600 | 3.74 | 4342 | ~3 | ~400 | 8.5 | East 13m | 528749 , 151537 | 5 | 5 | 10 |  | 4359 | 454 | 65 |  |  | mg/m³ and PPM numbers are measured dry and corrected to 5% 02 content.
Redhill, UK | S140 Gen 2 | 10000 | Cummins | QSK60-G3 | C2000 D5 C1OKBDK270 | 1600 | 3.74 | 5104 | ~3 | ~400 | 8.5 | East 13m | 528751 , 151534 | 3 | 7 | 8 |  | 4359 | 454 | 65 |  |  | mg/m³ and PPM numbers are measured dry and corrected to 5% 02 content.
Redhill, UK | S140 Gen 3 | 10000 | Cummins | QSK60-G3 | C2000 D5 E10KBGB260 | 1600 | 3.74 | 5618 | ~3 | ~400 | 8.5 | East 13m | 528752 , 151528 | 3 | 6 | 12 |  | 4359 | 454 | 65 |  |  | mg/m³ and PPM numbers are measured dry and corrected to 5% 02 content.
Redhill, UK | S140 Gen 4 | 10000 | Cummins | QSK60-G3 | C2000 D5 H09KBAR130 | 1600 | 3.74 |  | ~3 | ~400 | 8.5 | East 13m | 528753 , 151525 | 2 | 2 | 1 |  | 4359 | 454 | 65 |  |  | mg/m³ and PPM numbers are measured dry and corrected to 5% 02 content.
Redhill, UK | S150 Gen 1 | 10000 | Cummins | QSK60-G3 | C2000 D5 A11KBR860 | 1600 | 3.74 | 4424 | ~3 | ~400 | 8.5 | East 13m | 528770 , 151469 | 2.5 | 2.9 | 3.2 |  | 4359 | 454 | 65 |  |  | mg/m³ and PPM numbers are measured dry and corrected to 5% 02 content.
Redhill, UK | S160 Gen 1 | 10000 | Cummins | QSK60-G3 | C2000 D5 ALLKBMR870 | 1600 | 3.74 |  | ~3 | ~400 | 8.5 | East 13m | 528772 , 151466 | 6 | 4 | 8 |  | 4359 | 454 | 65 |  |  | mg/m³ and PPM numbers are measured dry and corrected to 5% 02 content.
Redhill, UK | S160 Gen 2 | 10000 | Cummins | QSK60-G3 | C2000 D5 B114BMX790 | 1600 | 3.74 | 5105 | ~3 | ~400 | 8.5 | East 13m | 528774 , 151457 | 6.2 | 4 | 7.5 |  | 4359 | 454 | 65 |  |  | mg/m³ and PPM numbers are measured dry and corrected to 5% 02 content.
Redhill, UK | S160 Gen 3 | 10000 | Cummins | QSK60-G3 | C2000 D5 B11KBMX780 | 1600 | 3.74 | 4844 | ~3 | ~400 | 8.5 | East 13m | 528773 , 151460 | 1.3 | 2 | 1.3 |  | 4359 | 454 | 65 |  |  | mg/m³ and PPM numbers are measured dry and corrected to 5% 02 content.
Total |  | 139485
Testing scenario
Monthly off load testing, individual generator tested at at time (10mins).
Quarterly - On load testing - each suite tested at a time, maximum 3 generators running at a time. One can be running and then another one is brought on (15-20mins). Generators average loaded to around 50%
Annual loadbank testing - each generator is run at (100-110% of load) for 1 hour. Each generator is run individually
Emergency/worst case scenario - all gens fire and 12 generators (2 in each datahall suite, plus S150 generator and landlord) keep running - 24 hours for 5 days
Note on S3: Rachel Skinner: Data provided by Perkins 4000 Series Diesel Engine Emissions table and Cummins datasheet (see attached)

## Unit 2
Generator list and tank sizes extracted from Digital Realty's monthly diesel fuel level and run hour spreadsheet
Redhill Generator Information for Air Quality Risk Assessment | [18 empty] | Emission Rates
Site | Suite | Tank Size (Lts) | Make of Engine | Model | Engine Type & Number | Standby KW Output | Thermal input MWth | Sulphur content from Crown Oil fuel polishing report once polished (mg/kg) | Approx stack heights on generator (m) | Stack diameter (mm) | Approx total stack height from ground (m) | Nearest building elevation (m) | Emission point 12-digit grid reference - Easting, Northing | 2018 run hours from generator | 2019 run hours from generator | 2021 run hours from generator | 2022 run hours from generator | Notes | NOX (mg/m3) | CO (mg/m3) | PM (mg/m3) | HC (mg/m3) | SO2 | Emission rate notes
Redhill, UK
Redhill, UK | S110 Gen1 (B01) | 10000 | Cummins | QSK60-G3 2020 kva | C2250 D5 D10KBFB980 | 1600 | 4.4 | unknown |  | ~400 | 8.5 | South ~13m | 528620 , 151495 | 6.3 | 2.7 | 9.8 | 3.9 |  | 4359 | 454 | 65 |  |  | mg/m³ and PPM numbers are measured dry and corrected to 5% 02 content.
Redhill, UK | S110 Gen2 (B02) | 10000 | Cummins | QSK60-G3 2020 kva | C2250 D5 L10KBMA550 | 1600 | 4.4 | unknown |  | ~400 | 8.5 | South ~13m | 528624 , 151496 | 6 | 3 | 9 | 3 |  | 4359 | 454 | 65 |  |  | mg/m³ and PPM numbers are measured dry and corrected to 5% 02 content.
Redhill, UK | S110 Gen3 (A02) | 10000 | Cummins | QSK60-G3 2020 kva | C2250 D5 B09KAXX840 | 1600 | 4.4 | unknown |  | ~400 | 8.5 | South ~13m | 528589 , 151484 | 5.2 | 2.8 | 9.5 | 4.2 |  | 4359 | 454 | 65 |  |  | mg/m³ and PPM numbers are measured dry and corrected to 5% 02 content.
Redhill, UK | S110 Gen4 (A01) | 10000 | Cummins | QSK60-G3 2020 kva | C2250 D5 H10KBHZ370 | 1600 | 4.4 | unknown |  | ~400 | 8.5 | South ~13m | 528585 , 151483 | 5.7 | 2.3 | 39.6 | 0 |  | 4359 | 454 | 65 |  |  | mg/m³ and PPM numbers are measured dry and corrected to 5% 02 content.
Redhill, UK | LL Gen | 1740 | Cummins | 6CTAA8.3G2 | C250 D5 C09KAYQ990 | 200 | 0.5 | unknown | 2.3 | ~100-150 |  | East ~13m | 528586 , 151432 | 2.7 | 0.7 | 5.8 | 2.7 | Horizontal exhaust stack
Total |  | 41740
Testing scenario
Monthly off load testing, two generators tested at at time (10mins) and landlord tested on its own (10mins)
Quarterly - On load testing - all 2 generators tested at a time for (20mins) and landlord tested on its own (20mins)
Annual loadbank testing - 2 generators at a time are tested to (100-110% of load) for 1 hour. Landlord tested on its own (1 hour)
Emergency/worst case scenario - all 4 generators fire and then ramp down to 2 generators running to meet the site load - 24 hours for 5 days
Note on T3: Rachel Skinner: Data provided by Perkins 4000 Series Diesel Engine Emissions table and Cummins datasheet (see attached)

## Unit 2- Run hours
Unit 2 | 2017-12-01 | 2018-12-01 | 2018 run hours | 2019-12-01 | 2019 run hours | 2020-12-01 | 2020 run hours | 2021-12-01 | 2021 run hours | 2022-12-01 | 2022 run hours
S110 Gen1 | 81 | 87.3 | 6.3 | 90 | 2.7 | 93.2 | 3.2 | 103 | 9.8 | 106.9 | 3.9
S110 Gen2 | 111 | 117 | 6 | 120 | 3 | 123 | 3 | 132 | 9 | 135 | 3
S110 Gen3 | 50 | 55.2 | 5.2 | 58 | 2.8 | 61.2 | 3.2 | 70.7 | 9.5 | 74.9 | 4.2
S110 Gen4 | 69 | 74.7 | 5.7 | 77 | 2.3 | 50.4 | -26.6 | 90 | 39.6 | 90 | 0
LL Gen | 20.8 | 23.5 | 2.7 | 24.2 | 0.7 | 26.5 | 2.3 | 32.3 | 5.8 | 35 | 2.7

## Sheet1
E and ISO8178-1 for measuring HC, CO, PM, NOx. Data shown is based on steady state operating conditions of
77° F, 28.42 in HG and number 2 diesel fuel with 35° API and LHV of 18,390 btu/lb. The nominal emissions data
on 100% load and thus cannot be used to compare to EPA regulations which use values based on a weighted cycle.