## Sheet1
Crawley LGW15 & LGW16 Data Centre 2023 diesel consumption
LGW16 & LGW15 Data extracted from Crawley 2023 UK ETS Annual Emissions Report calculation sheet
LGW16 | [5 empty] | LGW15
Suite | Fuel Use at 100% Capacity (L/h) | 2022-12-01 | 2023-12-01 | Total | Litres consumed using run hours and flow rates | Suite | Fuel Use at 100% Capacity (L/h) | 2020-12-01 | 2021-12-01 | Total | Litres consumed using run hours and flow rates
Generator 1 | 544 | 62.8 | 64.9 | 2.1 | 1142.4 | Shell and Core Generator A | 123 | 152.8 | 166.4 | 13.6 | 1672.8
Generator 2 | 544 | 32.3 | 34.7 | 2.4 | 1305.6 | Shell and Core Generator B | 123 | 127.5 | 140 | 12.5 | 1537.5
Generator 3 | 544 | 61.1 | 63.5 | 2.4 | 1305.6 | Data Hall 1 Generator A | 355 | 158.6 | 177.2 | 18.6 | 6603
Generator 4 | 544 | 30.8 | 33.2 | 2.4 | 1305.6 | Data Hall 1 Generator B | 355 | 122.1 | 137.4 | 15.3 | 5431.5
Generator 5 | 544 | 64.8 | 67.3 | 2.5 | 1360 | Data Hall 1 Generator C | 355 | 142.5 | 162.1 | 19.6 | 6958
Generator 6 | 544 | 33.4 | 35.8 | 2.4 | 1305.6 | Data Hall 1 Generator D | 355 | 155.5 | 170.1 | 14.6 | 5183
Generator 7 | 544 | 29.8 | 32.2 | 2.4 | 1305.6 | Data Hall 2 Generator A | 355 | 142.1 | 156.8 | 14.7 | 5218.5
| 3808 | 315 | 331.6 | 16.6 | 9030.4 | Data Hall 2 Generator B | 355 | 169.3 | 186.1 | 16.8 | 5964
[6 empty] | Data Hall 2 Generator C | 355 | 128 | 144 | 16 | 5680
[6 empty] | Data Hall 2 Generator D | 355 | 124.9 | 141.1 | 16.2 | 5751
[6 empty] | Fire Sprinkler Diesel Pump | 41.6 | 179.6 | 202.5 | 22.9 | 952.64
[7 empty] | 3127.6 | 1602.9 | 1783.7 | 180.8 | 50951.94
Total litres | 59982.34
Tonnes | 50.2786 |  | 1193
Max litres available | 71050
Max Tonnes | 59.5557 |  | 1193
Note on A14: Soiza, Jade: QSK60-G3. Called 'S 130 Gen 2 on permit'
Note on A15: Soiza, Jade: QSK60-G3
Note on A16: Soiza, Jade: QSK60-G3
Note on A17: Soiza, Jade: QSK60-G3
Note on A18: Soiza, Jade: QSK60-G3
Note on P18: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Augusta McGuinness please update formula to include all lines
Note on A19: Soiza, Jade: QSK60-G3
Note on A20: Soiza, Jade: QSK60-G3
Note on A21: Soiza, Jade: QSK60-G3
Note on A22: Soiza, Jade: QSK60-G3

## Sheet2
LGW15 & LGW16 Tank capacities
LGW15
Site | Suite | Tank Size (Lts)
LGW15 | Shell and Core Generator A | 3050
LGW15 | Shell and Core Generator B
LGW15 | Data Hall 1 Generator A | 13500
LGW15 | Data Hall 1 Generator B | 13500
LGW15 | Data Hall 1 Generator C
LGW15 | Data Hall 1 Generator D
LGW15 | Data Hall 2 Generator A | 13500
LGW15 | Data Hall 2 Generator B | 13500
LGW15 | Data Hall 2 Generator C
LGW15 | Data Hall 2 Generator D
LGW15 | Fire Sprinkler Diesel Pump
LGW11
Site | Suite | Tank Size (Lts)
LGW16 | Generator 1 | 2000
LGW16 | Generator 2 | 2000
LGW16 | Generator 3 | 2000
LGW16 | Generator 4 | 2000
LGW16 | Generator 5 | 2000
LGW16 | Generator 6 | 2000
LGW16 | Generator 7 | 2000
Total capacity | 71050
Note on A1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Augusta McGuinness please update title
Note on A17: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Augusta McGuinness please update title