## Crawley campus summary
Digital Realty Crawley Campus
Site | Site code | Total no of generators | Total thermal input MWth
Crawley 1 | LGW15 | 10 | 33.8561
Crawley 2 (North) | LGW16 | 7 | 38.0307
Crawley 3 - new in construction
Total |  |  | 71.8868

## LGW15 Crawley 1
Crawley LGW15 Generator thermal input calculations
| QSX15-G8 |  | C2000 D5 |  | Total
[5 empty] | Number of QSX15-G8 | 2
| Engine Fuel Rate (From Gen Set Performance Data) |  | Engine Fuel Rate (From Gen Set Performance Data) |  | Number of C2000 D5 | 8
| 123 | litres/hr (at 440 kWe) | 393 | litres/hr (at 1650 kWe)
[5 empty] | Total Net MW | 33.8561
| Conversion factor for Diesel Oil |  | Conversion factor for Diesel Oil
| 1184 | litres/ton (from DUKES 2020 Annex A) | 1184 | litres/ton (from DUKES 2020 Annex A)
| Net calorific value for Diesel Oil |  | Net calorific value for Diesel Oil
| 42.5688 | GJ/tonne (from GHG inventory 2020) | 42.5688 | GJ/tonne (from GHG inventory 2020)
| Thermal Input Calculation |  | Thermal Input Calculation
| Net Calorific Value |  | Net Calorific Value
| 123 | litres/hr | 393 | litres/hr
| 0.034167 | litres/s | 0.10917 | litres/s
| 2.8857e-05 | tonnes/s | 9.2202e-05 | tonnes/s
| 0.0012284 | GJ/s (GW) | 0.0039249 | GJ/s (GW)
| 1.2284 | MW | 3.9249 | MW

## LGW16 Crawley 2
Crawley 2 LGW16 Generator thermal input calculations
MODEL 1 - Cummins C2750 D5B |  | MODEL 2 - |  | MODEL 3 |  | Total |  | Estimated emissions
| 2200kW, 2750 Kva - QSK60-G22 |  |  |  |  | Number of model 1 | 7 | 15 min monthly test then 1 hour per quarter
Engine Fuel Rate (From Gen Set Performance Data) |  | Engine Fuel Rate (From Gen Set Performance Data) |  | Engine Fuel Rate (From Gen Set Performance Data) |  | Number of model 2 |  | 120 | 2 | hours
544 | litres/HR - highest stated fuel load |  | litres/hr |  | litres/hr | Number of model 3 |  | 240 | 4 | hours
[6 empty] | Total Net MW | 38.0307 | total | 6 | hours testing per generator
Conversion factor for Diesel Oil |  | Conversion factor for Diesel Oil |  | Conversion factor for Diesel Oil |  |  |  |  | 42 | hours for the site
1184 | litres/ton (from DUKES 2020 Annex A) | 1184 | litres/ton (from DUKES 2020 Annex A) | 1184 | litres/ton (from DUKES 2020 Annex A)
[9 empty] | 544 | litres/ hr
Net calorific value for Diesel Oil |  | Net calorific value for Diesel Oil |  | Net calorific value for Diesel Oil |  |  |  |  | 22848 | annual litres
42.5688 | GJ/tonne (from GHG inventory 2020) | 42.5688 | GJ/tonne (from GHG inventory 2020) | 42.5688 | GJ/tonne (from GHG inventory 2020) |  |  |  | 19.2973 | tonnes
Thermal Input Calculation |  | Thermal Input Calculation |  | Thermal Input Calculation |  |  |  |  | Emission factor (tCO2/TJ)(net) | Calorific Value (GJ/Tonne) | Calorific Value (TJ/Tonne) | Oxidation Factor | Emissions (tCO2)
Net Calorific Value |  | Net Calorific Value |  | Net Calorific Value |  |  |  |  | 74.9375 | 42.5688 | 0.042569 | 1 | 61.5584
544 | litres/hr | 0 | litres/hr | 0 | litres/hr
0.15111 | litres/s | 0 | litres/s | 0 | litres/s
0.00012763 | tonnes/s | 0 | tonnes/s | 0 | tonnes/s |  |  |  | not accounted for annual fail test so assume 100 tonnes
0.005433 | GJ/s (GW) | 0 | GJ/s (GW) | 0 | GJ/s (GW)
5.433 | MW | 0 | MW | 0 | MW
*